## Slide 1
5/14/01
1
S. Motzko
BAAQMD Generator Proposal
April 2001
What Is It?
Notes: 1

## Slide 2
5/14/01
2
S. Motzko
With the current energy crisis in California, many people are looking toward emergency generators to help their businesses cope with the potential of rolling blackouts.
A clean diesel emergency generator emits more than 20 times as much NOx as a new well-controlled power plant.
Diesel particulate has been identified as a toxic air contaminant with a potency that results in cancer risks from engines operated for as little as 30 hours per year.
BAAQMD Rule Management Summary
Notes: 3

## Slide 3
5/14/01
3
S. Motzko
Emergency standby engines have been exempt from permitting as an emissions source only if used for 100 hours or less testing and 200 hours or less of emergency use per year.
There is a proposed BAAQMD regulation (April 2001) where the exemption will be eliminated and the ability to grant permits will be eased.
Mobile sources are not addressed by BAAQMD, provided they are <1 year, but fall under the state of California rules (CARB).
Background - Diesel Standby Generators
BAAQMD Generator Proposal
Notes: 2

## Slide 4
5/14/01
4
S. Motzko
Proposed Regulation was published on the BAAQMD website on Monday, April 30, 2001.
Workshop on the Proposed Regulation was held May 11, 2001 at the BAAQMD.
Proposed Final Draft Regulation scheduled to be published on the BAAQMD website on May 20, 2001.
The final regulation will be voted on by the BAAQMD Board of Directors (tentatively) on June 20, 2001.
The regulation would be effective July 1, 2001 and the permitting process will be announced in a letter to those thought to possibly have generators.
BAAQMD Generator Proposal Timing
Notes: 3

## Slide 5
5/14/01
5
S. Motzko
Permit required for existing and new engines > 50hp
A limit of 100 hours/year for testing, maintenance and “reliability” (which could include bridging time between announced stage 3 and actual blackout)
Unlimited run time during actual power outage “emergencies”
  Involuntary curtailment & power provider has shed firm load (blackouts).
Existing sources would be exempt from New Source Review
  To meet existing criteria, they must be on-site before 7/1/01.
  New and replacement engines subject to risk management criteria based on characteristics of engine and installation analysis (BAAQMD).
Sources installed on or after May 17, 2000 would be subject to existing risk management policies.
BAAQMD Generator Proposal
Notes: 4

## Slide 6
5/14/01
6
S. Motzko
BAAQMD to send out letters notifying the need for permits within three months of adoption of the amendments.
Loss of exemption (existing generators) permits will be processed and issued automatically.
New source review permits (including replacement generators) will be reviewed by a team of permit engineers.
  Must meet BACT combustion control (NOx & Particulate Emmissions)
The cost of the permits:
  $120/year annual fee for small engine
  ~$550 for replacement or new engine permit/application
Standby Generator Application Instructions Online
<http://www.baaqmd.gov/permit/standby.htm>
BAAQMD Generator Permit Process
Notes: 3

## Slide 7
5/14/01
7
S. Motzko
Non-resettable totalizing meter that measures hours of operation required.
Records must be kept for at least 2 years.
Monthly log of usage shall include:
  Hours of operation (total)
  Hours of operation (emergency)
  For each emergency, the nature of the emergency condition
BAAQMD Monitoring Requirements
Notes: 3

## Slide 8
5/14/01
8
S. Motzko
An emergency standby generator may be temporarily converted to discretionary use (this section expires January 1, 2003), provided the following criteria are met:
The engine is an internal combustion engine.
  The increased emissions from the modified engine do not trigger federal new source review.
  The timing of the engine is adjusted to minimize NOx emissions (without adversely affecting particulate emissions).
  After conversion, the engine will meet the BAAQMD Risk Management Policy for Diesel Engines (subject to permit conditions).
BAAQMD Generator Conversion
Notes: 3