## Slide 1: PCB Roving Training 2000
The Gas Company
Sempra Energy

## Slide 2: History
Discovered in pipelines in 1981
Long Island Lighting employee exposure
CPUC required us to check our pipelines
Found in “gasoline” like portions (Drips)
Found in two-thirds of the system

## Slide 3: History
Transwestern used PCBs as compressor oil
Compressor failure introduced into pipeline
Cost recovery through binding arbitration
$7.3 million 1981 - 1988
Ongoing 86% recovery

## Slide 4: History
GWO 99300 for Labor. 300097138 for Non-Labor.
25% labor for PCB drip collection is charged to PCB
Quarterly reimbursement
Periodic audits

## Slide 5: Regulations
Toxic Substances Control Act
  regulates manufacture, use, storage, disposal
  30 day storage
  PCB label
  Spill Prevention Plan

## Slide 6: Regulations
Compliance Agreement Eliminated
  storage non-compliance
  presumed condensates greater than 50 ppm
  established temporary storage facilities
  treated as product from the drip location

## Slide 7: PCB-Suspect Locations
California Hazardous Waste PCBs
  - Adelanto - Newberry Springs
  - Devore - North Needles
Federal PCBs
  - Fontana
  - Kelso
  - Yorba

## Slide 8: PCB Megarule - Abandonment
Sampling required
  Liquids or “wipe”
Abandonment
  Less than 500 ppm - drain and seal ends
  Greater than 500 ppm - drain, grout/ cap or decon
Policy
  Grout 2” or less, but Test greater than 2”

## Slide 9: PCB Megarule Removal
Less than 500 ppm - reuse, sell, scrap
500 ppm or more - decontaminate or landfill (less than 1%)
Less than 3.5 mi - sample ends + 5 other locations
3.5 miles or more - sample every 1/2 mi

## Slide 10: Field Handling
Handle liquids from contaminated areas as PCB-suspect
Meters and regulators with liquids from contaminated areas are considered PCB contaminated
Rags, etc. into trash

## Slide 11: Field Handling
Protective clothing for drip blowing
  gloves
  goggles
  disposable coveralls with hood and boot covers
  S.I. 104.0080

## Slide 12: Field Handling
Approved Containers
  UN 1A1/X or 1A1/Y drums - liquids
  UN 1A2/X or 1A2/Y drums - solids
  Labeling and Marking
  Examples
  Transport to Temporary Storage Facility

## Slide 13: Field Handling
Transportation Documents from field to temporary storage
  Remotely Generated Hazardous Waste Form - solids from 10 to 2500 pounds
  Straight Bill of Lading - liquids (more than one drum)

## Slide 14: Spills
Remove visible traces
1 foot buffer
Drum or roll-off bin
Remove within 48 hours
Solid surfaces - double rinse
Document clean up Keep records

## Slide 15: Reportable Quantities (RQ)
The one pound PCB RQ refers to the amount of pure PCB, not the amount of liquid that contains some level of PCB. A manifest should only use “RQ” when there is one pound or more of PCB.

## Slide 16: Temporary Storage
Verify hours of acceptance
Additional Labeling
Additional Marking on drum
Storage - 30 days for federal. 90 days for State.
Weekly Inspections

## Slide 17: Temporary Storage Locations
Brea
Goleta
Industry
North Needles
Playa del Rey
Taft
Ventura
Victorville
Pico Rivera*

## Slide 18: Pico Rivera Temporary Storage Facility
  Commerce
  Downey
  Industry
  Montebello
  Pico Rivera
  Santa Fe Springs
  Whittier
  Unincorporated LA*
*Immediately east between Santa Fe Springs and Whittier, northeast between Whittier and Industry, and north between Industry & Montebello.

## Slide 19: Temporary Storage Requirements
No smoking, Caution PCBs, and Hazardous Waste signs
Cover drums
Spill equipment
Norm - Flammables 50 ft. from property line
SPCC Plan

## Slide 20: Shipping to Long Term Storage
Coordinate w/ shipping
Hazardous Waste Manifest
Land Ban Forms
Registered Haulers

## Slide 21: Long-Term Storage
Olympic base permit
Manifested shipments
Sampling of drums
Detectable PCB (2 ppm) to incinerator
Solids to Landfill