## Slide 1: Transmission Losses
Physical System Operations

## Slide 2: Transmission Losses
NERC’s definition(s):
  Electric System Losses
  Total electric energy losses in the electric system. The losses consist of transmission, transformation, and distribution losses between supply sources and delivery points. Electric energy is lost primarily due to heating of transmission and distribution elements.
  Scheduled Losses
  The scheduled power transfer to a transmission provider for compensation of losses incurred on that provider's transmission system due to a transfer of power between purchasing and selling entities.
PJM:
  “Real Power Losses: Real Power Losses are associated with all transmission service. The Transmission Provider is not obligated to provide Real Power Losses. The Transmission Customer is responsible for replacing losses associated with all transmission service as calculated by the Transmission Provider. The applicable Real Power Loss factors are as follows: 3 percent for on-peak hours and 2.5 percent for off-peak hours, as on-peak and off-peak are defined by NERC, which shall be supplied as set forth in Attachment K.”

## Slide 3: What “Causes” Losses and how are they determined?
PLosses= I²R (a.k.a. heating - resistance)
Metal(s) contained within cable, Equipment type, lengths (distances)
Location of Generation (source) relative to the location of the Load (sink)
Simply a measure of resistance/impedance from one point on the grid to another
  From calculations the TO develops a “Matrix” from which they can determine the losses in the system.

## Slide 4: Ohm’s Law
Battery supplies energy to a load.
Current flows in only one direction.
Power flow primarily a function of load size.
Rotating generator energy to a load.
Current reverses 60 times per second.
Power flow a function of load size and the power line’s magnetic properties.
Simple DC Circuit
+
-
  V
R
I
V
R
I =
  V 
Simple AC Circuit
P
P =

X
X

## Slide 5: Losses (Example is single phase for simplicity)
PInput= PLoss+ POutput
POutput = V * I
PLoss = I2 * R
Doubling operating voltage quarters losses
PInput
R
X
I
  V 
Load

## Slide 6: Power Flow in Transmission Lines
X1 = .10
X2 = .05
300 MW
Input
P1 = 100 MW
P2 = 200 MW
300 MW
Output
Power flow is inversely proportional to transmission line impedance.
There are no control valves to reroute flow from one line to another.

## Slide 7: Why do Transmission Providers charge for losses and how are losses applied in today’s markets?
Losses = Real Energy = Real $$$
  Financial – TC pays the “going rate” for energy
  Physical – TC “pays” by supplying compensating energy
The loss distribution assures the CAO will maintain the balance between generation and load, and assure the parties utilizing the system are paying their fair share.
Notes: 3.4.2 Transmission Losses.
(b) Transmission Customers shall be charged for transmission losses in an
amount equal to the product of (i) the Transmission Customer’s megawatt-hours of deliveries using Point-to-Point Transmission Service, times (ii) the appropriate loss factor for deliveries using Point-to-Point Transmission Service, times (iii) the weighted average Day-ahead or Real-time Price, as applicable, for all load busses in the PJM Control Area. The foregoing average hourly loss factor shall be: (i) determined by the Office of the Interconnection from time to time as conditions affecting losses shall warrant; and (ii) calculated separately for on-peak and off-peak hours on the basis of the average ratio of losses to load served in each such period.
A Transmission Customer may elect to pay for losses in kind, rounded off to the nearest whole megawatt, rather than as specified above if its total deliveries in an hour using Point-to-Point Transmission Service are greater than 200 megawatts. If it so elects, the Transmission Customer’s specified source for the energy to be delivered using Point-to-Point Transmission Service may be scheduled to supply to the PJM Control Area boundary an amount of energy equal to the delivery schedule plus the amount of losses determined by applying the appropriate hourly loss factor as specified above to the delivered amount.

## Slide 8
Questions and Answers