## Slide 1
7EA DLN 1.0 Emissions Compliance Corrective Actions

## Slide 2
Data Was Analyzed Using DFSS Gen III Tools
Generate Effects Plots from Which Curve/Fit Corrections can be Generated
RCA Team Performed Evaluation of Fleet Data and Lab Test Data

## Slide 3
Resized Dilution Hole Patch
Secondary Peg Hole Dia.
Effective Area (Nozzle Area)
7EA Secondary Nozzle
Secondary Nozzle Area Drawing
Group Numbers
Secondary Nozzle Area Drawing
Group Numbers
Changing Wilton Lincoln Center from the current Group 4 to Group 9 effective area will provide
an overall reduction in NOx and CO.
Secondary Nozzle Effective Area

## Slide 4
Emissions Multiplier
Manufacturing issues found during 2000 fleet implementation for the secondary nozzles resulted in excessive internal leakages.
% Secondary Flow Leakage into Transfer Passage
Secondary Nozzle Internal Leakage

## Slide 5
Primary Nozzle Area Drawing Group Numbers
Primary Nozzle Area Drawing Group Numbers
GRP13 GRP11 GRP5 GRP 2
GRP13 GRP11 GRP5 GRP 2
Changing Wilton Lincoln Center from the current Group 2 to Group 13 effective area will provide
an overall reduction in NOx and CO.
Primary Nozzle Nozzle Tip
Endcover With All 6 Primary Nozzles
Primary Nozzle Effective Area

## Slide 6
Decreasing Liner Dilution Hole Size
Secondary nozzle leakage's, varying degrees of leakage's across combustor cans, and non-optimum secondary and primary nozzle effective areas resulted in higher than expected NOx and CO. The resulting higher NOx lead to overtuning (ie. smaller liner dilution hole). Control curve adjustments were made to temporarily help mitigate CO emissions.
CO
NOx
9 ppm
Combined Effective Area and Leakage’s Effects On Liner Tuning

## Slide 7
7EA DLN 1 Liner
Resize Liner Dilution Holes To Optimize Unit Emissions to a Targeted NOx value of 7.5 - 8.5 and CO value of <10:
Resized Dilution Hole
Corrective Actions

## Slide 8
Adjust
Control
Curve, If
Needed
Collect data for analysis at Base Load
(Attachment A data -
MK-5 View 2 &
Emissions Data)
Data
Review
Complete Hardware Changeout and Install Nominal Control Constants *
Run Unit, Heat Soak,
Perform Fuel Gas
Splitter Valve
Optimization at Base
Load
Completed With
Emissions
Compliance
* Seed set hardware/consumables will be on site for 1st unit. Follow units will use hardware from previous units
Obtain latest reliable emissions data, if required.
Corrective Action Process Flow Diagram