## Slide 1: Information Needed By All Market Participants To Facilitate Transmission Congestion Studies In ERCOT
Presented to the ERCOT ROS
by Shannon Caraway, P.E. - TXU Energy Trading
5/8/2001
Draft Copy

## Slide 2: Presentation Outline
Overview of market issues.
Request for five types of power flow support files.
Request for planned system expansion information details and timing.
Concluding issues.

## Slide 3: Market Issues
Section 7 of the ERCOT Protocols addresses how the issue of congestion management will be addressed.
It provides the framework by which Transmission Congestion Rights (TCRs) will be defined, valued & implemented in the market.
According to section 7.3.3 - “ERCOT will convert to a direct assignment of cost methodology of CSC Congestion at the earlier of May 1, 2004 or within six months after the cost of clearing CSC Congestion during a rolling twelve month period reaches $20,000,000.”

## Slide 4: Market Issues
All Market Participants (MPs), including ERCOT itself, have the need of being able to perform meaningful market simulations that predict the expected amount of future transmission congestion.
Many of the pieces of the puzzle required to perform these market simulations (SSTF power flow cases, CSC congestion zones, etc…) are already available to all market participants.
However, some specific contingency data required to accurately forecast congestion in an automated fashion is still not publicly available to all market participants.

## Slide 5: Power Flow Support Files
The following requests (#1 - #5), represent information that is needed by all market participants to perform meaningful transmission studies for ERCOT as a whole.
The information sought in these requests in conjunction with the dataset A & B power flow models should provide all market participants the information necessary to study future congestion issues.

## Slide 6: Request #1
Publish a listing of single element contingencies, by SSTF bus numbers, that power flow programs perform that are historically known to be invalid (or phantom) contingencies from a physical perspective due to modeling limitations.
This listing of phantom contingencies should be developed and stored in spreadsheet format (or some other agreed upon method) that easily allows users to import it into the power flow software that they use.
A separate file should be developed, maintained and posted on the ERCOT website by the SSTF for each of the dataset A & B cases that are prepared annually.

## Slide 7: Illustration #1
Switching Station B
Bus 1
Bus 2
Bus 3
Switching Station E
138 kV
69 kV
To Station A
To Station C
To Station F
To Station D
PSS/E outages branch 1 - 2 with function ACCC.
This incorrectly leaves the 21 MW load on the 138 kV system at bus 2 as being back fed from the 69 kV system.
As a result, PSS/E reports a 168% overload of the 69 kV feed from Station F.
If branch 1 - 2 were on an exception list, any user would know that this overload could be ignored and the outage of concern (2 - 3) would still be monitored.
21 MW
69 kV
69 kV
138 kV
138 kV

## Slide 8: Request #2
Publish a listing of the normal and emergency voltage limits that ERCOT Operations personnel will utilize to make voltage related congestion decisions.
The intent of this request is to inform all market participants of the low voltage thresholds that will be utilized when determining transfer capability between the CSC congestion zones and for identifying local area voltage related congestion issues.
This listing should be published on the ERCOT website and updated periodically to keep in sync with the ERCOT Operations EMS system.

## Slide 9: Request #3
Publish a listing of all the Special Protection Schemes (SPSs) and Remedial Action Plans (RAPs) that are being used, or are planned to be used, in ERCOT and post it on the ERCOT website.
Sufficient information such that the implementation date and deactivation date of each SPS and RAP should be specified so that it will be possible for the user to determine in which future year cases that the schemes are applicable.
The overall detailing of the scheme should be descriptive enough (i.e. one-line diagrams where necessary) that any user can use it and the SSTF power flow cases alone to interpret how to implement it in a power flow simulation.

## Slide 10: Request #4
Provide a listing of all double-circuit lines, by SSTF bus numbers, that are greater than 0.5 miles (as defined by the ERCOT planning criteria) that will be used during planning studies. The list need only include the most limiting sections of a double-circuit line outages and not all of the intermediate sections.
Provide an official “good weather” and “bad weather” contingency file that will be used for all operational studies.
A separate file should be developed, maintained and posted on the ERCOT website by the SSTF for each of the dataset A & B cases that are prepared annually.

## Slide 11: Illustration #4
The entire 138 kV line shown is a double-circuit line.
However, for power flow contingency studies related to this example, it is only necessary to study outages of the end sections in order to observe the most severe scenarios.
Only branch pairs 1 - 2 / 1 - 3 and 9 - 11 / 10 - 12 need to be studied for contingency analysis purposes.
The TDSPs via the SSTF should provide a comprehensive list of all double-circuit outages that need to be studied for planning studies and both a “good weather” and a “bad weather” list for operational studies.
138kV
Bus 1
Bus 2
Bus 3
Bus 5
Bus 4
Bus 8
Bus 7
Bus 9
Bus 10
Bus 6
Bus 12
Bus 11
Switching Station A
Substation B
Substation C
Substation D
Substation E
Substation F
Switching Station G

## Slide 12: Request #5
Provide a listing by load flow bus number of all special contingencies that should be included in power flow contingency studies to reflect the actual response of relay protection and sectionalizing facilities in place that constitute a single element outage.
This is necessary since relay operations and sectionalizing often require the removal of multiple power flow branches simultaneously to simulate a single NERC contingency outage in power flow programs.
A separate file should be developed, maintained and posted on the ERCOT website by the SSTF for each of the dataset A & B cases that are prepared annually.

## Slide 13: Illustration #5
The relay protection in place opens both breakers at Switching Station A and the breakers at Switching Stations A & C for a fault at the point shown.
To simulate the conditions immediately after this single element fault, it is necessary to open branches 1 - 2, 7 - 8, 6 - 7, & 3 - 4.
To simulate the conditions after all possible sectionalizing has occurred, it is necessary to open branches 2 - 3, 3 - 5, & 3 - 4.
The intent of this item isn’t to create a list of all single element contingencies that have to be studied, only those that aren’t picked up by the automatic contingency functions in power flow packages.
Bus 4
Bus 1
Bus 2
155MW
84MW
66MW
Bus 6
Bus 5
Bus 3
345kV
138kV
Bus 7
Bus 8
Switching Station C
Substation B
Switching Station A
Substation D
Switching Station E
345kV
345kV
There are no sectionalizing switches at this tap point
To Switching Station F
Fault
Location

## Slide 14: Planned System Expansion
The following requests (#6 - #7), represent information that is needed by all market participants to better understand the planned expansion of the transmission system as detailed in the dataset A & B cases.
The same legal disclaimers that apply to the dataset A & B power flow cases should apply to the following requested documents as well.

## Slide 15: Request #6
Publish an annual transmission plan document that is posted on the ERCOT website which graphically and verbally illustrates the electrical connectivity (i.e. one-line representation) and proposed in-service date of all projects.
The projects proposed and described in this expansion plan document should be of the same scope and timing as the ones modeled in the SSTF dataset A & B cases.
This document would be posted annually on the website at the same time as the dataset A & B cases.
As an example, the California ISO currently provides this type of information on their website at the following address: http://www.caiso.com/thegrid/planning/transassessments/.

## Slide 16: Request #7
Provide a project status report that is updated periodically and documents timing and scope changes to the transmission plan document that is posted annually.
Projects that are scheduled to be placed in service within the next twelve months should have their status updated monthly.
Projects that are scheduled to be placed in service outside of the next twelve months should have their status updated quarterly.

## Slide 17: Conclusions
Section 7 of the ERCOT Protocols provides for the creation of TCRs to hedge against transmission congestion.
The only way for market participants to objectively determine the value of future TCRs, is to utilize exactly the same study criteria that ERCOT and the TDSPs will be using to study system conditions.
This series of requests seeks to make comparable studies possible for all market participants.

## Slide 18: Conclusions
They will provide information related to the regulated aspects of TCR valuation studies to all market participants in a non-discriminatory manner.
It is in the best interest of future system reliability for the specifics of how the grid will be studied, to be broadly known.
Currently, all market participants must speculate on how ERCOT and the TDSPs will interpret the NERC planning and operating criteria.