## Slide 1: Winter 2001-02 Power Supply Adequacy/Reliability Analysis
Power Committee Briefing
October 17, 2001

## Slide 2: Results of May analysis
Goal

## Slide 3: Current analysis bottom line
Situation much improved – LOLP<< 5%
Largely due to:
  Additional load reduction
  Hydro conditions

## Slide 4: What’s changed
Aggressive actions to reduce loads – loads further reduced from May analysis
Hydro
  Succeeded in storing addition energy in Canada (3700 MW-Mo vs 1500 MW-Mo, increased withdrawal rate
  Different distribution of water conditions
  Different Canadian operation
Improved analytics
  Treatment of forced outages
  Transmission

## Slide 5: What hasn’t changed but might
New thermal generation
  About the same as May analysis
Import availability –
  Using same assumptions as May analysis
  If anything, availability should be improved.
Contracts in/out of region
  Unable to get updated information from most utilities
  Using same assumptions as May
  Continuing to pursue additional information
  Will update analysis if necessary

## Slide 6: Short to Mid-Term Load Forecast

## Slide 7: Monthly load change from previous year
Notes: This figure shows what has happened to electricity loads (temperature adjusted) in the region since 1999. The figure shows percent change in loads for a month compared to the same month in the previous year.
Significant declines began showing up in the summer and fall of 2000.
By this past summer loads were down by near 20 percent from the same month in 2000.
This magnitude of load reduction in unprecedented in the region. Far greater than the declines experienced in 1982 for example. Mainly due to complete shutdown of the regional aluminum industry and several other large industrial plants.

## Slide 8: Composition of July 2001 load reduction
Notes: 70 percent of the load reduction in July 2001 compared to July 2000 is due to large industrial and some irrigation load reduction. The remaining 30 percent reflects responses of smaller consumers to a number of factors.
About a nine percent retail price increase
Heavily publicized electricity shortages and extremely high wholesale prices
Pleas by the region’s governors to conserve
Bonneville and regional utilities’ conservation efforts
Clearly, loads have deviated substantially from the Council’s long term trend forecast for 2001 in the last power plan.

## Slide 9: Factors to consider
Effect of recent retail price increases
Economic recession
Lower wholesale prices
Status of load buyout agreements
Potential for reduced retail prices
Persistence of voluntary load reductions after end of crisis atmosphere
Notes: Cumulative electricity price increase through August was about 9%. By November is might be around 25%.
Since the terrorist attacks of Sept. 11, the economic outlook was worsened. Many forecasters are expecting a recession that lasts into the middle of next year. The depth and duration of recession are unknown. (15% drop in aluminum prices since June)
Meanwhile, wholesale electricity prices have retreated from high levels down to the low 20s on peak and the teens off peak.
Most industrial buyouts run through next summer, but many are renegotiable. In addition, plants could potentially buy from the spot market.
At some point in the future, lower wholesale prices are likely to find their way into reduced retail prices.
How lasting will the recent reductions in consumption be as the electricity problems fade from the headlines.

## Slide 10: Forecast compared to long-term trend
Average Megawatts
Notes: The red (upper) line is the long-term trend forecast from the Council’s 4th power plan. The blue (lower) line is the proposed short-term forecast. In the shaded area, you can see how far loads have dropped below the trend.
I have assumed that loads will return to the long-term trend over the next couple of years.
Forecasts remain depressed throughout this winter. I have assumed that none of the bought out loads will begin to return until at least April 2002.

## Slide 11: Monthly Load Patterns
Notes: It is easier to see the load drop and recovery patterns in this diagram which compared the four years 1999-2002.

## Slide 12: Comparison of loads – May and Oct Studies

## Slide 13: Hydro Conditions for Fall and Winter

## Slide 14: What we did in May
Examined historic record, observed greater likelihood of continued lower fall and winter runoff following a dry year
Analysis used only lower 2/3 of the runoffs in the record – sampled with equal weights

## Slide 15: Oct-Dec Runoff vs. Preceding Jan-Jul Runoff Volume
58.2 MAF Jan-Jul runoff yields about 15 MAF average Oct-Dec with large variability

## Slide 16: Estimating Runoff Volumes for Jan-Jul 2002
Climate Prediction Center Forecast:
  No indication for dry or wet conditions
  More variability in weather
Very dry soil and low aquifer levels
  Will absorb about 10% of precipitation
Assume average runoff volume minus 10% or 94 Maf
Result very close to Bonneville estimates reached via different approaches

## Slide 17: Runoff Volumes Putting it All Together
Assume a “normal” distribution for Jan-Jul runoff volume
Mean is 94 maf with standard error 14 maf
Fit all historical data into curve to get weights
Expected fall runoff is 14.8 Maf (15.7 in May study)
Expected Jan-Jul runoff is 94.4 Maf (93.6 in May study)

## Slide 18: Changes in Hydro (from the May Study)
Average about the same but different distributions
  May study somewhat higher likelihood of very dry years
More water stored in Canada
  Yields about 2,200 MW-mo more energy
  Constraints on using the water relaxed – can more effectively address periods of high demand

## Slide 19: Non-hydro generation prospects

## Slide 20: Generating Resource Prospects for Winter 2001 - 02
On net, about 2180 MW of new generation is expected to have entered service during 2001.
  About 1650 MW of this is permanent.
  About 530 MW of this operates under temporary permits.
Some additional temporary projects may be removed from service, but some unverified capacity may be available for service.

## Slide 21: Of the 1650 MW of permanent generation…
About 1340 megawatts of energy:
  7% increase in average Northwest energy capability.
Composition:
  46% natural gas combined-cycle.
  23% natural gas simple-cycle.
  17% wind.
Winter availability reasonably certain:
  About 70 % of the 1650 MW is now in service
  Much of the remaining is wind, currently under construction.

## Slide 22: Of the 530 MW of temporary generation…
About 890 MW placed in service during 2001.
  Mostly oil-fired reciprocating engine-generator sets.
360 MW expected to be removed by EOY 2001.
  Variable costs are $90 – 140/MWh
  Price cap mechanism creates uncertainty regarding ability to dispatch speculative capacity.
  Some replaced by permanent capacity.
The winter availability of the remaining 530 MW moderately certain.
  Assuming available to dispatch if necessary

## Slide 23: New resource expectations

## Slide 24: October vs May new resource expectations
Period
of
analysis
3000 MW –Feb 2000 estimate of new resources need by winter 2003

## Slide 25: Other Issues
Import availability –
  Assumed up to 1000 MW on-peak, additional 3000 MW off-peak
  If anything, availability should be improved
    3500 MW new generation
    3500 MW of existing generation that couldn’t run last year now fitted with NOx controls
Contract obligations a question mark
  We’re somewhat conservative in relation to utility reports to PNUCC, continuing to work the issue

## Slide 26: Results
5% Target
Insufficiencies are possible but very unlikely
Requires combinations of extreme weather, bad water and forced outages

## Slide 27: Major Contributing factors
Reduced loads across the winter
Differences in Hydro
  Availability of additional energy in storage and relaxed constraints on use
  Distribution
  Canadian operation

## Slide 28: What if loads hadn’t been reduced
*
*Same hydro conditions, thermal generation
and import availability