## Slide 1
ProcessA
ProcessB
14 bars
4 bars/156 C
ST1
ST2
CBC
CR
GTV
41 bars/420 C
85 bars/480 C
Black liquor
Fuel oil 3A
GNC-Conc.
Biomass
Fuel oil 3A
Methanol
GNC-DI
GNC-Conc.
94
98
81-94
94
98
25,3 MW
38,6 MW
Fuel oil 3A
NG
Nat. Gas
Conversion
240 t/h
80 t/h
227,229 t/h
153,060 t/h
68,168 t/h
Energia = EBE SE 88 kV
Consumo Fábrica = 48 - 49 MWh
Energia Comprada = 11 - 15 MWh (Agosto / 2000)
Demanda Ponta = 16,5 MW
Demanda For a Ponta = 17 MW
Pot . Inst = 63 MW
Carga Gerada = 38 MW
To the boilers
60/70 t/h
VCP - Votorantim Celulose e Papel

## Slide 2: VCP - Votorantim Celulose e Papel
According to the available figures 2.6% of the steam produced is lost in the processes.
There is a spare steam capacity of approximately 152 ton/hour
We can fit in another steam turbine aiming the production of extra power
The conversion to Natural Gas could be made with the inclusion of gas turbine perhaps in a combined cycle.
We can leave as it is now and try to classify the installation as one of biomass power production and be entitled to sell power for the respective VN number (R$ 81)
Study the processes in depth, with aim of streamlining the energy use and, consequently, the production of excess power.