## 032102Bu
PLANNED AND UNPLANNED OUTAGES AFFECTING THE BUSHTON UNIVERSE.
2002-03-21
The information provided is tentative and may be changed without further notice. Northern Natural Gas Transwestern and Florida Gas Transmission are not responsible for any reliance on this information.
# | Region | Location | Units | Title | EstStart | EstComp | Dur (Days) | Est Flow Affected | Est Thru Affected | DescOfWork | ActStart | ActComp | Act Flow Affected | Planned Unplanned
17698 | LIB | FINNEY 4 | 1 | BEARING SENSOR | 2001-10-05 14:00 | 2002-06-30 16:30 | 268.1 | 0 | 0 | Lost main bearing sensor. Pulled doors off to check sensor and found metal in crankcase. Drained oil and located problem. Unit will have to be re-worked. | 2001-10-05 14:00 |  | 0 | U
18461 | AMA | BEAVER 12 | 1 | SUCTION SCRUBBER | 2001-12-29 12:00 | 2002-03-25 16:00 | 86.2 | 0 | 0 | Have suction scrubber rebuilt. | 2001-12-29 12:00 |  | 0 | U
18353 | LIB | HUGOTON | 10 | CHECK MAIN BEARING | 2002-01-07 08:00 | 2002-04-15 14:00 | 98.3 | 0 | 0 | Check Main Bearing and replace if needed. Other maintenance has been completed. | 2002-01-07 08:00 |  | 0 | P
18466 | LIB | BEAVER 1 | 3 | BORESCOPE | 2002-03-01 08:00 | 2002-03-22 16:00 | 21.3 | 0 | 0 | Borescope power cylinder. Change heads clean ports. | 2002-03-01 08:00 |  | 0 | P
18547 | LIB | STEVENS 2 | 3 | CRANKSHAFT | 2002-03-01 21:44 | 2002-03-29 16:00 | 27.8 | 4 | 111.2 | Cooper Energy is pulling the crankshaft. Reynolds-French will determine the necessity of a line bore. Estimated completion depends on the findings from Reynolds - French. | 2002-03-01 21:44 |  | 0 | U
17154 | BEA | CUNNINGHAM | 5 | OVERHAUL & CRACKED MANIFOLD | 2002-03-04 07:00 | 2002-03-25 15:30 | 21.3 | 50 | 1066.7 | Major overhaul MEP 12 cylinder power and compressor ends based on analysis and run hours. Unit will be disassembled and inspected and returned to OEM standards. Repair Manifold. (Flow affect is about 50 mmcfd depending on the needs on the pipeline). | 2002-03-04 07:00 |  | 0 | P
18563 | LIB | SUBLETTE | 20 | OIL COUPLIER | 2002-03-04 15:00 | 2002-03-22 12:00 | 17.9 | 0 | 0 | Replace the float oil couplier on oil pump. (Parts are on order). | 2002-03-04 15:00 |  | 0 | P
18062 | LIB | STEVENS 7 | 1 | MP2 | 2002-03-05 09:00 | 2002-03-07 16:00 | 2.3 | 4 | 9.2 | MP2 Tasks. |  |  | 0 | P
18589 | AMA | BEAVER 7 | 2 | COMPRESSOR CYLINDER | 2002-03-10 07:00 | 2002-03-22 16:00 | 12.4 | 2 | 24.8 | Unit down with a knock in the #1 compressor. Not sure what they have unitl they tear into it. | 2002-03-10 07:00 |  | 0 | U
18446 | LIB | STEVENS 4 | 2 | SERVICE | 2002-03-13 08:00 | 2002-03-14 16:00 | 1.3 | 3.5 | 4.7 | Service and MP2 tasks. |  |  | 0 | P
18601 | LIB | STEVENS 2 | 7 | COMPRESSOR CYLINDER & PISTON | 2002-03-14 08:00 | 2002-03-22 16:00 | 8.3 | 0 | 0 | Specialty Compressor is re-doing the compressor cylinder and piston. | 2002-03-14 08:00 |  | 0 | U
18436 | LIB | STEVENS 4 | 1 | MP2 | 2002-03-20 08:00 | 2002-03-20 20:00 | 0.5 | 3.5 | 1.8 | MP2 tasks. |  |  | 0 | P
17964 | LIB | SUBLETTE | 22 | MP2 | 2002-03-22 08:00 | 2002-03-23 08:00 | 1 | 0 | 0 | MP 2 Tasks. 2000 HP |  |  | 0 | P
18610 | LIB | SUBLETTE | 24 | COUPLING ALIGNMENT | 2002-03-25 08:00 | 2002-03-25 18:00 | 0.4 | 3 | 1.3 | Perform coupling alignment and base deflection. |  |  | 0 | U
17946 | LIB | SUBLETTE | 19 | MP2 | 2002-03-25 08:00 | 2002-03-26 08:00 | 1 | 0 | 0 | MP 2 Tasks. 2000 HP |  |  | 0 | P
17982 | LIB | SUBLETTE | 26 | MP2 | 2002-03-25 08:00 | 2002-03-26 08:00 | 1 | 0 | 0 | MP 2 Tasks. 6000 HP |  |  | 0 | P
17970 | LIB | SUBLETTE | 23 | MP2 | 2002-03-26 08:00 | 2002-03-27 08:00 | 1 | 9 | 9 | MP 2 Tasks. 1400 HP |  |  | 0 | P
18019 | LIB | FINNEY 2 | 8 | MAINTENANCE | 2002-03-26 08:00 | 2002-03-27 16:00 | 1.3 | 0 | 0 | Scheduled maintenance: work orders & DET list. |  |  | 0 | P
17846 | LIB | STEVENS 3 | 3 | SERVICE | 2002-03-26 08:00 | 2002-03-27 16:00 | 1.3 | 0 | 0 | Service unit plus panel S/D & PM MP2 Tasks. 1100 HP |  |  | 0 | P
18362 | AMA | BEAVER 12 | 3 | OVERHAUL (ON HOLD) | 2002-03-26 13:00 | 2002-04-26 16:00 | 31.1 | 0 | 0 | Overhaul Engine & Compressors. |  |  | 0 | P
17988 | LIB | SUBLETTE | 13 | MP2 | 2002-03-27 08:00 | 2002-03-28 08:00 | 1 | 0 | 0 | MP 2 Tasks. 2000 HP |  |  | 0 | P
17958 | LIB | SUBLETTE | 21 | MP2 | 2002-03-28 08:00 | 2002-03-29 08:00 | 1 | 0 | 0 | MP 2 Tasks. 2000 HP |  |  | 0 | P
18020 | LIB | FINNEY 2 | 9 | MAINTENANCE | 2002-03-28 08:00 | 2002-03-29 16:00 | 1.3 | 0 | 0 | Scheduled maintenance: work orders & DET list. |  |  | 0 | P
17952 | LIB | SUBLETTE | 20 | MP2 | 2002-03-29 08:00 | 2002-03-30 08:00 | 1 | 0 | 0 | MP 2 Tasks. 2000 HP |  |  | 0 | P
17934 | LIB | SUBLETTE | 27 | MP2 | 2002-03-29 08:00 | 2002-03-30 08:00 | 1 | 0 | 0 | MP 2 Tasks. 6000 HP |  |  | 0 | P
18364 | LIB | FINNEY 3 | 1 | INFRAME OVERHAUL | 2002-04-01 08:00 | 2002-04-15 16:00 | 14.3 | 0 | 0 | Engine inframe overhaul. |  |  | 0 | P
18367 | AMA | BEAVER PLANT | 12 | OVERHAUL (ON HOLD) | 2002-04-01 08:00 | 2002-04-30 16:00 | 29.3 | 0 | 0 | Major enigne & compressors. (Subject to Dynegy approval). |  |  | 0 | P
18608 | LIB | FINNEY 4 | 3 | COMPRESSOR PISTON | 2002-04-02 08:00 | 2002-04-11 16:30 | 9.3 | 4.5 | 42 | Need to pull #1 compressor piston. Pull valves packing and repair. (Unit 2 will also be down because of unit 3). |  |  | 0 | P
18588 | AMA | ELLIS 3 | 6 | 1500 HR. INSPECTION | 2002-04-07 09:00 | 2002-04-07 12:00 | 0.1 | 0 | 0 | 1500 hour inspection. |  |  | 0 | P
17620 | LIB | TEXAS 1 | 2 | CONTROLS PM | 2002-04-08 07:30 | 2002-04-08 16:00 | 0.4 | 0 | 0 | Controls PM. |  |  | 0 | P
17621 | LIB | TEXAS 1 | 6 | CONTROLS PM | 2002-04-15 07:30 | 2002-04-17 16:00 | 2.4 | 0 | 0 | Controls PM. |  |  | 0 | P
18368 | LIB | FINNEY 2 | 1 | OVERHAUL (ON HOLD) | 2002-04-15 08:00 | 2002-04-30 16:00 | 15.3 | 0 | 0 | Inframe engine & compressor OH. |  |  | 0 | P
18363 | LIB | FINNEY 4 | 4 | OVERHAUL (ON HOLD) | 2002-04-15 08:00 | 2002-05-10 16:30 | 25.3 | 3 | 76 | Unit will be pulled out and overhauled. (Unit Exchange if possible). |  |  | 0 | P
18554 | AMA | ELLIS 1 | 1 | 1500 HR. INSPECTION | 2002-04-15 09:00 | 2002-04-15 11:00 | 0.1 | 2 | 0.2 | 1500 hr. Inspection. |  |  | 0 | U
18437 | LIB | STEVENS 4 | 1 | MP2 | 2002-04-17 08:00 | 2002-04-17 20:00 | 0.5 | 3.5 | 1.8 | MP2 tasks. |  |  | 0 | P
18553 | AMA | ELLIS 1 | 4 | 1500 HR. INSPECTON | 2002-04-17 09:00 | 2002-04-17 12:00 | 0.1 | 5 | 0.6 | 1500 hr. Inspection. |  |  | 0 | U
17676 | LIB | TEXAS 2 | 6 | ENGINE SERVICE | 2002-04-18 08:00 | 2002-04-18 16:00 | 0.3 | 0 | 0 | Engine service. |  |  | 0 | P
18447 | LIB | STEVENS 4 | 2 | MP2 | 2002-04-18 08:00 | 2002-04-18 20:00 | 0.5 | 3.5 | 1.8 | MP2 tasks. |  |  | 0 | P
18552 | AMA | ELLIS 1 | 3 | 1500 HR. INSPECTION | 2002-04-19 09:00 | 2002-04-19 11:00 | 0.1 | 2 | 0.2 | 1500 hr. inspection. |  |  | 0 | U
18401 | LIB | BURDETT | 1 | BORESCOPE & MINOR MAINTENANCE | 2002-04-29 07:30 | 2002-05-10 16:00 | 11.4 | 0 | 0 | Borescope and minor maintenance. |  |  | 0 | P
17151 | BEA | BUSHTON | 26 | OVERHAUL (ON HOLD) | 2002-04-29 08:00 | 2002-05-31 16:00 | 32.3 | 0 | 0 | Major overhaul on the power and compressor ends of an Ingersoll Rand KVS412 based on analysis and run hours. Unit will be disassembled and inspected and returned to OEM standards. |  |  | 0 | P
18569 | BEA | CUNNINGHAM | ALL | MAIN PLANT DRIPS | 2002-04-30 07:00 | 2002-04-30 16:00 | 0.4 | 0 | 0 | Repair/replace 1" line on Main Plant Drips. This is a consolidated audit action item. (It will affect max Inj. and Wdl). |  |  | 0 | P
18370 | LIB | MULLINVILLE | 8 AUX. | OVERHAUL | 2002-05-01 08:00 | 2002-05-03 16:00 | 2.3 | 0 | 0 | TEO |  |  | 0 | P
17836 | LIB | HOLCOMB | 10 | REPLACE PISTONS & RINGS (ON HOLD) | 2002-05-01 08:00 | 2002-05-31 16:00 | 30.3 | 0 | 0 | Replace pistons and rings overhaul 2 & 3 compressors. |  |  | 0 | P
18369 | AMA | BEAVER PLANT | 14 | OVERHAUL | 2002-05-01 08:00 | 2002-06-01 16:00 | 31.3 | 0 | 0 | Major engine and compressors. |  |  | 0 | P
18528 | AMA | BEAVER 2 | ALL | ESD | 2002-05-02 08:00 | 2002-05-02 12:00 | 0.2 | 5 | 0.8 | Annual ESD. |  |  | 0 | P
18465 | LIB | BEAVER 1 | ALL | ESD | 2002-05-02 08:00 | 2002-05-02 12:00 | 0.2 | 14 | 2.3 | Annual ESD. |  |  | 0 | P
18522 | AMA | BEAVER PLANT | ESD | ESD | 2002-05-02 08:00 | 2002-05-02 16:00 | 0.3 | 350 | 116.7 | Annual ESD. (7 to 8 hours). |  |  | 0 | P
18524 | AMA | NORTHRUP | ALL | ESD | 2002-05-02 08:00 | 2002-05-02 20:00 | 0.5 | 10 | 5 | Annual ESD. |  |  | 0 | P
18525 | AMA | PERRYTON BARLOW | ALL | ESD | 2002-05-02 08:00 | 2002-05-02 20:00 | 0.5 | 7 | 3.5 | Annual ESD. |  |  | 0 | P
18467 | LIB | CLARK 1 | ALL | ESD | 2002-05-02 08:00 | 2002-05-02 20:00 | 0.5 | 6.5 | 3.3 | Annual ESD. |  |  | 0 | P
18469 | LIB | CLARK 2 | ALL | ESD | 2002-05-02 08:00 | 2002-05-02 20:00 | 0.5 | 6 | 3 | Annual ESD. |  |  | 0 | P
18494 | LIB | MULLINVILLE | ALL | ESD | 2002-05-02 08:00 | 2002-05-02 20:00 | 0.5 | 300 | 150 | Annual ESD. Will by-pass Rich gas thru the station. Will affect about 150 mmcfd Lean gas due to some of the other outages south of Beaver. |  |  | 0 | P
18583 | AMA | BEAVER PLANT | B LINE ORIFICE | REMOVE ORIFICE PLATE | 2002-05-02 08:00 | 2002-05-03 16:00 | 1.3 | 0 | 0 | They believe the orifice plate is bent on the B line measurement at Beaver. They need to remove it when Beaver has their ESD. Actual time table for the work is estimated. It could be more or less. Flow affect is Spearman volumes. Estimated(68 mmfcd). |  |  | 0 | P
18523 | AMA | SPEARMAN | ESD & A LINE | ESD & A LINE LEAKS | 2002-05-02 08:00 | 2002-05-03 16:00 | 1.3 | 68 | 90.7 | Annual ESD. Need to repair several A Line leaks. |  |  | 0 | P
18073 | LIB | STEVENS 1 | ALL | ANNUAL ESD | 2002-05-07 07:30 | 2002-05-07 10:30 | 0.1 | 30 | 3.8 | Annual ESD. |  |  | 0 | P
18493 | LIB | STEVENS 3 | ALL | ESD | 2002-05-07 07:30 | 2002-05-07 10:30 | 0.1 | 6 | 0.8 | Annual ESD. |  |  | 0 | P
17622 | LIB | MORTON 1 | ALL | ANNUAL ESD | 2002-05-07 07:30 | 2002-05-07 13:00 | 0.3 | 18 | 4.5 | Annual ESD. |  |  | 0 | P
17623 | LIB | MORTON 6 | ALL | ANNUAL ESD | 2002-05-07 07:30 | 2002-05-07 13:00 | 0.3 | 8 | 2 | Annual ESD. |  |  | 0 | P
18527 | BEA | BUSHTON | ALL | ESD | 2002-05-07 07:30 | 2002-05-07 20:00 | 0.5 | 300 | 162.5 | Annual ESD. We should be able to bypass some volumes through the station using Clifton H.P. |  |  | 0 | P
18089 | LIB | HUGOTON | ALL | ESD | 2002-05-07 07:30 | 2002-05-08 13:00 | 1.3 | 130 | 162.5 | Planned ESD. (Actual completion time depends on final scope of work). |  |  | 0 | P
17624 | LIB | TEXAS 1 | ALL | ANNUAL ESD | 2002-05-07 07:30 | 2002-05-08 14:00 | 1.3 | 10 | 12.9 | Annual ESD. |  |  | 0 | P
17625 | LIB | TEXAS 2 | ALL | ANNUAL ESD | 2002-05-07 07:30 | 2002-05-08 14:00 | 1.3 | 15 | 19.4 | Annual ESD. |  |  | 0 | P
17842 | LIB | STEVENS 2 | ALL | ANNUAL ESD | 2002-05-07 08:00 | 2002-05-07 10:30 | 0.1 | 19 | 1.6 | Annual ESD |  |  | 0 | P
18472 | LIB | STEVENS 7 | ALL | ESD | 2002-05-07 08:00 | 2002-05-07 10:30 | 0.1 | 0 | 0 | Annual ESD. The flow affect is captured in the Stevens 1 ESD. |  |  | 0 | P
18473 | LIB | SUBLETTE | ALL | ESD | 2002-05-07 08:00 | 2002-05-07 13:00 | 0.2 | 0 | 0 | Annual ESD. (Flow affects are in Hugoton's outage). |  |  | 0 | P
17895 | LIB | STEVENS 4 | ALL | ANNUAL ESD | 2002-05-07 08:00 | 2002-05-08 16:00 | 1.3 | 20 | 26.7 | Annual ESD. (Station will be back up when Hugoton comes back on). |  |  | 0 | P
18471 | LIB | STEVENS 6 | ALL | ESD | 2002-05-07 08:00 | 2002-05-08 16:00 | 1.3 | 18 | 24 | Annual ESD. (The station will be back on line when the Hugoton plant comes back on). |  |  | 0 | P
18459 | AMA | ELLIS 1 | ALL | ANNUAL ESD | 2002-05-07 09:00 | 2002-05-07 11:00 | 0.1 | 0 | 0 | Annual ESD. Will blind flange and not blow the station down. |  |  | 0 | P
18460 | AMA | BEAVER 6 | ALL | ANNUAL ESD | 2002-05-08 10:00 | 2002-05-08 12:00 | 0.1 | 0 | 0 | Annual ESD. Will blind flange and not blow the station down. |  |  | 0 | P
18438 | LIB | STEVENS 4 | 1 | SERVICE | 2002-05-09 08:00 | 2002-05-10 20:00 | 1.5 | 3.5 | 5.3 | Service and MP2 tasks. |  |  | 0 | P
17626 | LIB | MORTON 6 | 1 | MP 2 | 2002-05-13 07:30 | 2002-05-15 16:00 | 2.4 | 4 | 9.5 | MP2 8 000 hour inspect. |  |  | 0 | P
18511 | LIB | FINNEY 2 3 4 | ALL | ANNUAL ESD | 2002-05-14 07:30 | 2002-05-14 16:00 | 0.4 | 0 | 0 | Annual ESD's for the Finney Co. Stations. 2 3 and 4. |  |  | 0 | P
18570 | LIB | FINNEY 1 | ALL | ESD | 2002-05-14 07:30 | 2002-05-15 16:00 | 1.4 | 10 | 13.8 | Annual ESD. Finney 1 will need to be down 2 days for Holcomb south's outage. Cleaning their VTECH. |  |  | 0 | P
17627 | LIB | TEXAS 1 | 3 | CONTROLS PM | 2002-05-14 07:30 | 2002-05-16 16:00 | 2.4 | 0 | 0 | Controls PM |  |  | 0 | P
18408 | LIB | BURDETT | ALL | ANNUAL ESD | 2002-05-14 08:00 | 2002-05-14 12:00 | 0.2 | 0 | 0 | Annual ESD will shut down during the same time as Holcomb's ESD. |  |  | 0 | P
17839 | LIB | HOLCOMB | ESD | ANNUAL ESD | 2002-05-14 08:00 | 2002-05-14 12:00 | 0.2 | 135 | 22.5 | Annual ESD and maintenance. |  |  | 0 | P
17757 | LIB | TATE | ALL | ESD | 2002-05-14 08:00 | 2002-05-14 12:00 | 0.2 | 14 | 2.3 | Annual ESD test. |  |  | 0 | P
17840 | LIB | HOLCOMB | HOLCOMB SOUTH | ESD & CLEAN BETEX | 2002-05-14 08:00 | 2002-05-15 12:00 | 1.2 | 6 | 7 | Outage coordinated with Holcomb's Annual ESD. And also to clean their BETEX. Finney co. 1 will need to be down through this outage. |  |  | 0 | P
18513 | AMA | ELLIS 2 | ALL | ESD | 2002-05-15 09:00 | 2002-05-15 11:00 | 0.1 | 0 | 0 | Annual ESD. |  |  | 0 | P
18402 | LIB | BURDETT | 2 | BORESCOPE & MAINTENANCE | 2002-05-20 07:30 | 2002-05-31 16:00 | 11.4 | 0 | 0 | Borescope and minor maintenance. |  |  | 0 | P
18448 | LIB | STEVENS 4 | 2 | MP2 | 2002-05-23 08:00 | 2002-05-23 20:00 | 0.5 | 3.5 | 1.8 | MP2 tasks. |  |  | 0 | P
17628 | LIB | MORTON 6 | 2 | MP2 | 2002-05-28 07:30 | 2002-05-30 16:00 | 2.4 | 4 | 9.5 | MP2 8 000 hr inspection |  |  | 0 | P
17892 | LIB | STEVENS 4 | 4 | OVERHAUL | 2002-06-01 08:00 | 2002-07-01 16:00 | 30.3 | 0 | 0 | Comp. & engine overhaul. |  |  | 0 | P
17152 | BEA | BUSHTON | 27 | OVERHAUL | 2002-06-03 08:00 | 2002-07-03 16:00 | 30.3 | 0 | 0 | Major overhaul on the power and compressor ends of an Ingersoll Rand KVS412 based on analysis and run hours. Unit will be disassembled and inspected and returned to OEM standards. |  |  | 0 | P
18568 | BEA | CUNNINGHAM | ALL | ESD | 2002-06-04 07:00 | 2002-06-04 16:00 | 0.4 | 0 | 0 | Annual ESD test. (This will affect the injection by 150 mmcfd from 450 mmcfd to 300 mcfd and withdrawal by 60-80 mmcfd from 220 mmcfd to 150 mmcfd). |  |  | 0 | P
17672 | LIB | TEXAS 1 | 3 | ENGINE SERVICE | 2002-06-05 08:00 | 2002-06-05 16:00 | 0.3 | 0 | 0 | Engine service |  |  | 0 | P
17629 | LIB | TEXAS 2 | 1 | CONTROLS PM | 2002-06-10 07:30 | 2002-06-10 16:00 | 0.4 | 0 | 0 | Controls PM |  |  | 0 | P
18403 | LIB | BURDETT | 3 | BORESCOPE & MAINTENANCE | 2002-06-10 07:30 | 2002-06-21 16:00 | 11.4 | 0 | 0 | Borescope and minor maintenance. |  |  | 0 | P
18514 | AMA | WOODWARD 1 | ALL | ESD | 2002-06-12 09:00 | 2002-06-12 11:00 | 0.1 | 0 | 0 | Annual ESD. |  |  | 0 | P
18374 | AMA | BEAVER 7 | 1 | OVERHAUL (ON HOLD) | 2002-06-15 08:00 | 2002-06-30 16:00 | 15.3 | 0 | 0 | Major overhaul. |  |  | 0 | P
18375 | LIB | STEVENS 1 | 4 | OVERHAUL | 2002-06-15 08:00 | 2002-06-30 16:00 | 15.3 | 0 | 0 | Major compressor and all five cylinders. |  |  | 0 | P
18407 | LIB | BURDETT | ALL | RELIEF VALVE TESTING | 2002-06-17 07:30 | 2002-06-21 16:00 | 4.4 | 0 | 0 | Will take one unit down at a time to do the testing. |  |  | 0 | P
17631 | LIB | TEXAS 2 | 2 | CONTROLS PM | 2002-06-18 07:30 | 2002-06-18 16:00 | 0.4 | 0 | 0 | Controls PM |  |  | 0 | P
18439 | LIB | STEVENS 4 | 1 | MP2 | 2002-06-19 08:00 | 2002-06-19 20:00 | 0.5 | 3.5 | 1.8 | MP2 tasks. |  |  | 0 | P
18516 | AMA | WOODWARD 3 | ALL | ESD | 2002-06-19 09:00 | 2002-06-19 11:00 | 0.1 | 0 | 0 | Annual ESD. |  |  | 0 | P
18430 | LIB | STEVENS 4 | 2 | MP2 | 2002-06-20 08:00 | 2002-06-20 20:00 | 0.5 | 3 | 1.5 | MP2 tasks. |  |  | 0 | P
17674 | LIB | TEXAS 2 | 7 | INSPECTION | 2002-06-24 08:00 | 2002-06-24 16:00 | 0.3 | 0 | 0 | 8 000 hr. inspection |  |  | 0 | P
18404 | LIB | BURDETT | 4 | BORESCOPE & MAINTENANCE | 2002-07-01 07:30 | 2002-07-12 16:00 | 11.4 | 0 | 0 | Borescope and minor maintenance. |  |  | 0 | P
18409 | LIB | BURDETT | ALL | JACKET WATER PROJECT | 2002-07-01 08:00 | 2002-07-01 16:00 | 0.3 | 0 | 0 | There is no firm date for this outage yet if at all. |  |  | 0 | P
17633 | LIB | TEXAS 2 | 3 | CONTROLS PM | 2002-07-08 07:30 | 2002-07-08 16:00 | 0.4 | 0 | 0 | Controls PM |  |  | 0 | P
17634 | LIB | MORTON 1 | 3 | MP2 | 2002-07-08 07:30 | 2002-07-26 16:00 | 18.4 | 0 | 0 | MP2 8 000 hour inspection. |  |  | 0 | P
18376 | AMA | BEAVER 2 | 5 | OVERHAUL | 2002-07-08 08:00 | 2002-08-09 16:00 | 32.3 | 0 | 0 | Major engine (Mike White OH). |  |  | 0 | P
18431 | LIB | STEVENS 4 | 2 | SERVICE | 2002-07-10 08:00 | 2002-07-11 16:00 | 1.3 | 3 | 4 | Service & MP2. |  |  | 0 | P
17635 | LIB | TEXAS 2 | 4 | CONTROLS PM | 2002-07-15 07:30 | 2002-07-15 16:00 | 0.4 | 0 | 0 | Controls PM |  |  | 0 | P
18377 | AMA | ELLIS 2 | 2 | OVERHAUL | 2002-07-15 08:00 | 2002-07-30 16:00 | 15.3 | 0 | 0 | Major compressor. |  |  | 0 | P
18440 | LIB | STEVENS 4 | 1 | MP2 | 2002-07-17 08:00 | 2002-07-17 20:00 | 0.5 | 3.5 | 1.8 | MP2 tasks. |  |  | 0 | P
18515 | AMA | WOODWARD 2 | ALL | ESD | 2002-07-17 09:00 | 2002-07-17 11:00 | 0.1 | 0 | 0 | Annual ESD. |  |  | 0 | P
18405 | LIB | BURDETT | 5 | BORESCOPE & MAINTENANCE | 2002-07-22 07:30 | 2002-08-02 16:00 | 11.4 | 0 | 0 | Borescope and minor maintenance. |  |  | 0 | P
17677 | LIB | TEXAS 2 | 6 | INSPECTION | 2002-07-22 08:00 | 2002-07-22 16:00 | 0.3 | 0 | 0 | 8 000 hr. inspection |  |  | 0 | P
17780 | LIB | STEVENS 2 | 7 | SERVICE | 2002-07-23 08:00 | 2002-07-23 16:00 | 0.3 | 0 | 0 | Service unit plus panel board S/D & PM. 1234 HP |  |  | 0 | P
18365 | AMA | BEAVER PLANT | 9 | OVERHAUL | 2002-07-29 08:00 | 2002-08-30 16:00 | 32.3 | 0 | 0 | Major engine & compressors. |  |  | 0 | P
17675 | LIB | TEXAS 2 | 7 | ENGINE SERVICE | 2002-07-30 08:00 | 2002-07-30 16:00 | 0.3 | 0 | 0 | Engine service. |  |  | 0 | P
18378 | AMA | WOODWARD 1 | 3 | OVERHAUL | 2002-08-01 08:00 | 2002-08-30 16:00 | 29.3 | 0 | 0 | Major Engine. |  |  | 0 | P
17636 | LIB | TEXAS 2 | 5 | CONTROLS PM | 2002-08-05 07:30 | 2002-08-05 16:00 | 0.4 | 0 | 0 | Controls PM |  |  | 0 | P
18379 | LIB | STEVENS 2 | 8 | OVERHAUL | 2002-08-10 08:00 | 2002-08-30 16:00 | 20.3 | 0 | 0 | Compressor overhaul. |  |  | 0 | P
18406 | LIB | BURDETT | 6 | BORESCOPE & MAINTENANCE | 2002-08-12 07:30 | 2002-08-30 16:00 | 18.4 | 0 | 0 | Possible overhaul- ECS other wise Borescope & minor maintenance. |  |  | 0 | P
18441 | LIB | STEVENS 4 | 1 | MP2 | 2002-08-14 08:00 | 2002-08-14 20:00 | 0.5 | 3.5 | 1.8 | MP2 tasks. |  |  | 0 | P
18432 | LIB | STEVENS 4 | 2 | MP2 | 2002-08-15 08:00 | 2002-08-15 20:00 | 0.5 | 3 | 1.5 | MP2 tasks. |  |  | 0 | P
17669 | LIB | TEXAS 1 | 2 | ENGINE SERVICE | 2002-08-27 08:00 | 2002-08-27 16:00 | 0.3 | 0 | 0 | Engine service. |  |  | 0 | P
18380 | AMA | BEAVER 6 | 1 | OVERHAUL | 2002-09-01 08:00 | 2002-09-30 16:00 | 29.3 | 0 | 0 | Major Engine & compressor. |  |  | 0 | P
18381 | AMA | WOODWARD 2 | 4 | OVERHAUL | 2002-09-01 08:00 | 2002-09-30 16:00 | 29.3 | 0 | 0 | Major Engine. |  |  | 0 | P
18442 | LIB | STEVENS 4 | 1 | SERVICE | 2002-09-11 08:00 | 2002-09-12 16:00 | 1.3 | 3.5 | 4.7 | Service and MP2 tasks. |  |  | 0 | P
18382 | AMA | WOODWARD 3 | 4 | OVERHAUL | 2002-09-15 08:00 | 2002-09-30 16:00 | 15.3 | 0 | 0 | Major Compressor. |  |  | 0 | P
17678 | LIB | TEXAS 2 | 6 | ENGINE SERVICE | 2002-09-18 08:00 | 2002-09-18 16:00 | 0.3 | 0 | 0 | Engine service. |  |  | 0 | P
18433 | LIB | STEVENS 4 | 2 | MP2 | 2002-09-26 08:00 | 2002-09-26 20:00 | 0.5 | 3 | 1.5 | MP2 tasks. |  |  | 0 | P
18314 | LIB | HUGOTON | 16 | SERVICE & MAINTENANCE | 2002-10-08 08:00 | 2002-10-08 16:00 | 0.3 | 0 | 0 | Service and maintenance. |  |  | 0 | P
17817 | LIB | STEVENS 2 | 6 | MP2 | 2002-10-09 08:00 | 2002-10-09 16:00 | 0.3 | 0 | 0 | MP2 Tasks. 1234 HP |  |  | 0 | P
17643 | LIB | MORTON 6 | 2 | CONTROLS PM | 2002-10-14 07:30 | 2002-10-16 16:00 | 2.4 | 0 | 0 | Controls PM |  |  | 0 | P
18102 | LIB | HUGOTON | 17 | SERVICE | 2002-10-15 08:00 | 2002-10-15 14:00 | 0.3 | 0 | 0 | Service and maintenance. 1800 HP |  |  | 0 | P
18384 | AMA | BEAVER 7 | 4 | OVERHAUL | 2002-10-15 08:00 | 2002-10-30 16:00 | 15.3 | 0 | 0 | Major Engine. |  |  | 0 | P
18385 | AMA | ELLIS 1 | 1 | OVERHAUL | 2002-10-15 08:00 | 2002-11-15 16:00 | 31.3 | 0 | 0 | Major Engine. |  |  | 0 | P
18443 | LIB | STEVENS 4 | 1 | MP2 | 2002-10-16 08:00 | 2002-10-16 20:00 | 0.5 | 3.5 | 1.8 | MP2 tasks. |  |  | 0 | P
18434 | LIB | STEVENS 4 | 2 | MP2 | 2002-10-17 08:00 | 2002-10-17 20:00 | 0.5 | 3 | 1.5 | MP2 tasks. |  |  | 0 | P
17670 | LIB | TEXAS 1 | 2 | INSPEC TION | 2002-10-21 08:00 | 2002-10-25 16:00 | 4.3 | 0 | 0 | 8 000 hr. inspection |  |  | 0 | P
18386 | AMA | BEAVER 7 | 4 | OVERHAUL | 2002-11-01 08:00 | 2002-11-30 16:00 | 29.3 | 0 | 0 | Major Compressor. |  |  | 0 | P
17882 | LIB | STEVENS 4 | 1 | SERVICE | 2002-11-05 08:00 | 2002-11-06 16:00 | 1.3 | 0 | 0 | Panel S/D & PM MP 2. |  |  | 0 | P
17889 | LIB | STEVENS 4 | 3 | SERVICE | 2002-11-06 08:00 | 2002-11-06 20:00 | 0.5 | 0 | 0 | Panel S/D & MP 2. |  |  | 0 | P
17885 | LIB | STEVENS 4 | 2 | SERVICE | 2002-11-13 08:00 | 2002-11-14 16:00 | 1.3 | 0 | 0 | Service unit panel S/D & MP 2. |  |  | 0 | P
17644 | LIB | MORTON 1 | 3 | CONTROLS PM | 2002-12-02 07:30 | 2002-12-06 16:00 | 4.4 | 0 | 0 | Controls PM |  |  | 0 | P
17754 | LIB | TATE | 10 | INSPECTION | 2002-12-02 08:00 | 2002-12-13 16:00 | 11.3 | 0 | 0 | Unit inspection. |  |  | 0 | P
17773 | LIB | STEVENS 2 | 3 | SERVICE | 2002-12-04 08:00 | 2002-12-04 16:00 | 0.3 | 0 | 0 | Service unit plus panel board S/D & PM. 1324 HP |  |  | 0 | P
17788 | LIB | STEVENS 2 | 8 | SERVICE | 2002-12-05 08:00 | 2002-12-05 16:00 | 0.3 | 0 | 0 | Service unit plus panel board S/D & PM. 764 HP |  |  | 0 | P
18047 | LIB | FINNEY 3 | 1 | MAINTENANCE | 2002-12-06 08:00 | 2002-12-06 16:00 | 0.3 | 0 | 0 | Scheduled maintenance - work orders & DET list. |  |  | 0 | P
18444 | LIB | STEVENS 4 | 1 | MP2 | 2002-12-11 08:00 | 2002-12-11 20:00 | 0.5 | 3.5 | 1.8 | MP2 tasks. |  |  | 0 | P
18435 | LIB | STEVENS 4 | 2 | MP2 | 2002-12-12 08:00 | 2002-12-12 20:00 | 0.5 | 3 | 1.5 | MP2 tasks. |  |  | 0 | P
17755 | LIB | TATE | 11 | INSPECTION | 2002-12-16 08:00 | 2002-12-20 16:00 | 4.3 | 0 | 0 | Unit inspection. |  |  | 0 | P