## 12-20
SYSTEM OPERATIONS AND RELIABILITY SUMMARY FOR 12/20/2000
Time of Conference Call 12/20/00 10:00 | All Time | 2000-12-19 |  | 2000-12-20 |  | 2000-12-21 |  |  |  | Monday
Load Forecasts/Actual | Record | Load | Temp | Load | Temp | Load | Temp | Load
PG&E | 23128 |  |  | 16300
SCE | 19935 |  |  | 13700
SDG&E |  |  |  | 2980
CAISO | 45884 | 33782 |  | 33720
Scheduling Coordinator Forecast |  |  |  | 27711 |  |  |  | 6000 delta
SMUD | 2759
LADWP |  |  |  | 3725
Ties |  | 1820 |  | 1869 |  |  |  |  | 3812
Out of Market Purchases OOM
Interruptible Load shed
Firm Load shed |  | 0
CAISO % reserves |  | 6.2% |  | 5.2%
CA Generation out |  |  |  | 2339
CA Generation out for other reasons |  |  |  | 4782
CA Generation limited
Total CA generation out of service |  |  |  | 7123
| All Time | 2000-12-20 |  | 10:00 | 13:00 | 15:30 | 16:30
Peak Load Forecasts/Actual | Record | Load | Temp | Load | Load | Load | Load
PG&E | 23128 | 16300 | 0
SCE | 19935 | 13700 | 0
SDG&E |  | 2980 | 0
CAISO | 45884 | 33720 |  |  | 33720
Scheduling Coordinator Forecast |  | 27711
SMUD | 2759 | 0 | 0
LADWP |  | 3725 | 0
Ties |  | 1869
Out of Market Purchases OOM |  | 0
Interruptible Load shed |  | 0 |  |  | 0
Firm Load shed |  | 0
CAISO % reserves |  | 5.2% |  |  | 5.5%
CA Generation out |  | 2339
CA Generation limited |  | 0
Total CA generation out of service |  | 7123
10:00
yesterday Stage 2 path 15 mitigation
Stage 1 presently
700 MW of interruptable loads off if 700 MW of ties show up 18 or 19
1 helm unit generation available for 12 hours
1000 BPA
Very little response from Richardsons Order
The order will be extended for a week
Midway Vincent back in service with normal relaying back in service Loose bond wire and damage conductor repaired
Every two hours report any excess generation
BPA has 500 MW available of emergency water
1330 next call
1330 call
1000 MW additional energy. Some is due to the DOE order
Stage 2 for path 15 possible
Approximate 5 hours of Helms left full load

## 12-21
SYSTEM OPERATIONS AND RELIABILITY SUMMARY FOR 12/21/2000
Time of Conference Call 12/21/00 10:00 | All Time | 2000-12-20 |  | 2000-12-21 |  | 2000-12-22
Load Forecasts/Actual | Record | Load | Temp | Load | Temp | Load | Temp
PG&E | 23128 |  |  | 15900
SCE | 19935 |  |  | 13600
SDG&E |  |  |  | 2960 |  |  |  | 32460
CAISO | 45884 | 32834 |  | 33695
Scheduling Coordinator Forecast |  |  |  | 26901 |  |  |  | 6794
SMUD | 2759
LADWP |  |  |  | 3670
Ties |  | 3352 |  | 3149
Out of Market Purchases OOM
Interruptible Load shed
Firm Load shed |  | 0
CAISO % reserves |  | 7.1% |  | 11.6%
CA Generation out |  |  |  | 2080 |  |  |  | 3702 | np15
CA Generation out for other reasons |  |  |  | 4522 |  |  |  | 2900 | sp15
CA Generation limited
Total CA generation out of service |  |  |  | 6602
| All Time | 2000-12-21 |  | 10:00 | 13:30 | 15:30 | 16:30
Peak Load Forecasts/Actual | Record | Load | Temp | Load | Load | Load | Load
PG&E | 23128 | 15900 | 0
SCE | 19935 | 13600 | 0
SDG&E |  | 2960 | 0
CAISO | 45884 | 33695
Scheduling Coordinator Forecast |  | 26901
SMUD | 2759 | 0 | 0
LADWP |  | 3670 | 0
Ties |  | 3149
Out of Market Purchases OOM |  | 0
Interruptible Load shed |  | 0
Firm Load shed |  | 0
CAISO % reserves |  | 11.6%
CA Generation out |  | 2080
CA Generation limited |  | 0
Total CA generation out of service |  | 6602
10:00
Scenario 2 hour of full load at helms 11.6% reserves
Mitigating Path 15 resources in the north will aggrevate
Stage 2 for 2200 weather and holiday cooperating
Next call 1330
CDWR energy limited today
Non-firm and pumps possible and over the peak hours
Slight response to DOE order MPC and QF around path 15
Lack of

## 12-22
SYSTEM OPERATIONS AND RELIABILITY SUMMARY FOR 12/22/2000
Time of Conference Call 12/22/00 10:00 | All Time | 2000-12-21 |  | 2000-12-22 |  | 2000-12-23
Load Forecasts/Actual | Record | Load | Temp | Load | Temp | Load | Temp
PG&E | 23128 |  |  | 15500
SCE | 19935 |  |  | 13100
SDG&E |  |  |  | 2950 |  |  |  | 31550
CAISO | 45884 | 32937 |  | 32167 |  |  |  |  | 32167 | 31677
Scheduling Coordinator Forecast |  |  |  | 29249
SMUD | 2759
LADWP |  |  |  | 3450
Ties |  | 3352 |  | 4100
Out of Market Purchases OOM
Interruptible Load shed
Firm Load shed |  | 0
CAISO % reserves |  | 7% |  | 7%
CA Generation out |  |  |  | 2091
CA Generation out for other reasons |  |  |  | 4327
CA Generation limited
Total CA generation out of service |  |  |  | 6418
| All Time | 2000-12-22 |  | 10:00 | 13:30 | 15:30 | 16:30
Peak Load Forecasts/Actual | Record | Load | Temp | Load | Load | Load | Load
PG&E | 23128 | 15500 | 0
SCE | 19935 | 13100 | 0
SDG&E |  | 2950 | 0
CAISO | 45884 | 32167
Scheduling Coordinator Forecast |  | 29249
SMUD | 2759 | 0 | 0
LADWP |  | 3450 | 0
Ties |  | 4100
Out of Market Purchases OOM |  | 0
Interruptible Load shed |  | 0
Firm Load shed |  | 0
CAISO % reserves |  | 7%
CA Generation out |  | 2091
CA Generation limited |  | 0
Total CA generation out of service |  | 6418
10:00
Diablo reduce to half load for short duration for back at 1800
No stage 2 today
1000 1100 MW below yesterday's curve and 800 MW for the day ahead forecast
weekend
units will stay on to pay back to BPA and pump at helms
fill helms over the week end
five hours of helms of water left for today
Path 15 right on the limit at this time
DOE certification order in effect
The financial situation is sensitive because of insolvency threat ISO says it is real.
Two authorities to maintain flow of electricity. FERC tarrrif for must run
DOE federal power act must follow order once certification is in place
Annoucements made not until next week
Conditions to remain
New FERC rules Jan 1 soft caps and etc
how much help outside of state? Few hundred MW was arranged. BPA mostly

## 1-8
SYSTEM OPERATIONS AND RELIABILITY SUMMARY FOR 1/8/2001
Time of Conference Call 1/8/01 10:00 | All Time | 2001-01-07 |  | 2001-01-08 |  | 2001-01-09
Load Forecasts/Actual | Record | Load | Temp | Load | Temp | Load | Temp
PG&E | 23128 |  |  | 15800
SCE | 19935 |  |  | 13200
SDG&E |  |  |  | 2900
CAISO | 45884 | 28809 |  | 32386
Scheduling Coordinator Forecast |  |  |  | 28083 |  |  |  | 4303
SMUD | 2759
LADWP |  |  |  | 3610
Ties |  |  |  | 4162
Out of Market Purchases OOM
Interruptible Load shed
Firm Load shed
CAISO % reserves |  | 11.7% | [5 empty] | np | sp
CA Generation Planned out |  |  |  | 4682 |  |  |  | 2082 | 2600
CA Generation Forced out |  |  |  | 5338 |  |  |  | 1810 | 3528
CA Generation out for other reasons
Total CA generation out of service |  |  |  | 10020
| All Time | 2001-01-08 |  | 10:00 | 13:30 | 15:30 | 16:30
Peak Load Forecasts/Actual | Record | Load | Temp | Load | Load | Load | Load
PG&E | 23128 | 15800 | 0
SCE | 19935 | 13200 | 0
SDG&E |  | 2900 | 0
CAISO | 45884 | 32386
Scheduling Coordinator Forecast |  | 28083
SMUD | 2759 | 0 | 0
LADWP |  | 3610 | 0
Ties |  | 4162
Out of Market Purchases OOM |  | 0
Interruptible Load shed |  | 0
Firm Load shed |  | 0
CAISO % reserves |  | 0%
CA Generation out |  | 4682
CA Generation limited |  | 0
Total CA generation out of service |  | 10020
10:00
Raining and loads down
NP15 gen at full load NW import Down
Stage 1 Muni generation Highly probable but no commitment
Outages up
DOE extention out till Wednesday
NW not selling tomorrow due to politics and river situation
Path 15 an issue for today
Need MWh due to unit outages
General shortage for Muni reserves
next call tomorrow

## 1-11
SYSTEM OPERATIONS AND RELIABILITY SUMMARY FOR 1/11/2001
Time of Conference Call 1/11/01 10:00 | All Time | 2001-01-10 |  | 2001-01-11 |  | 2001-01-12
Load Forecasts/Actual | Record | Load | Temp | Load | Temp | Load | Temp
PG&E | 23128 |  |  | 16100
SCE | 19935 |  |  | 13350
SDG&E |  |  |  | 2950
CAISO | 45884 | 32623 |  | 32589
Scheduling Coordinator Forecast |  |  |  | 24424 |  |  |  | 8165
SMUD | 2759
LADWP |  | 3775 |  | 3700
Ties
Out of Market Purchases OOM
Interruptible Load shed |  | 400 |  | 800
Firm Load shed |  |  |  | 400
CAISO % reserves |  | 5.2% |  | 1.5% |  |  |  | np | sp
CA Generation Planned out |  |  |  | 4905 |  |  |  | 2237 | 2668
CA Generation Forced out |  |  |  | 9741 |  |  |  | 2355 | 7386
CA Generation out for other reasons | [8 empty] | 800
Total CA generation out of service |  |  |  | 14646
| All Time | 2001-01-11 |  | 10:00 | 13:30 | 15:30 | 16:30
Peak Load Forecasts/Actual | Record | Load | Temp | Load | Load | Load | Load
PG&E | 23128 | 16100 | 0 | 16100
SCE | 19935 | 13350 | 0 | 13350
SDG&E |  | 2950 | 0 | 3000
CAISO | 45884 | 32589 |  | 32488
Scheduling Coordinator Forecast |  | 24424
SMUD | 2759 | 0 | 0
LADWP |  | 3700 | 0 | 3700
Ties |  | 0 |  | 5063
Out of Market Purchases OOM |  | 0
Interruptible Load shed |  | 800 | [5 empty] | 1700 | 1800 | 1900 | 2000
Firm Load shed |  | 400 |  | 2000 |  |  |  | 500 | 2000 | 1400 | 1200
CAISO % reserves |  | 1.5% |  | 2.2%
CA Generation out |  | 4905
CA Generation limited |  | 0
Total CA generation out of service |  | 14646
7:30
Stage 2 called 5:01
6:45 shed interruptables
Stage 1 319
400 MW of CDWR pump load
400 MW of PG&E load
Tube leaks turbine vibration
No Diablo until 2100 tonight
Stage 3 staged for today
All interruptable loads 17 18 19
All time peak for LADWP
No DOE order due to lack of 5% load reduction program
Possibility of Stage 3 tonight
5.5 % reserves currently
Next call 1000
10:00
Stage 3 0850
all interruptable off in SCE PG&E and SDG&E in next half hour
Half SCE interruptagle now and all later (yes twice same day)
2100 hours stage
1000 tommorrow for diablo
unit with tube leak to come back today
Credit problem in getting energy
Could not pick up energy as usual
1901-02-06

## 1-17
SYSTEM OPERATIONS AND RELIABILITY SUMMARY FOR 1/17/2001
Time of Conference Call 1/17/01 10:00 | All Time | 2001-01-16 |  | 2001-01-17 |  | 2001-01-18
Load Forecasts/Actual | Record | Load | Temp | Load | Temp | Load | Temp
PG&E | 23128 |  |  | 15600
SCE | 19935 |  |  | 13000
SDG&E |  |  |  | 2950
CAISO | 45884 | 30979 |  | 32279 |  | 31856 |  | 31376
Scheduling Coordinator Forecast |  |  |  | 23205 |  |  |  | 9100 | 0.72
SMUD | 2759
LADWP |  |  |  | 3600
Ties |  |  |  | 691
Out of Market Purchases OOM
Interruptible Load shed |  | 1440 |  | 1600
Firm Load shed |  |  |  | 500
CAISO % reserves |  | 4.4% |  | 3%
CA Generation Planned out |  |  |  | 4251
North Path 15 |  |  |  | 1901
South Path 15 |  |  |  | 1572
CA Generation Forced out |  |  |  | 6883
North Path 15 |  |  |  | 2350
South Path 15 |  |  |  | 5311
CA Generation out for other reasons |  |  |  | 11134
Total CA generation out of service | 14646
| All Time | 2001-01-17 |  | 10:00 | 13:00 | 16:00 | 16:30
Peak Load Forecasts/Actual | Record | Load | Temp | Load | Load | Load | Load
PG&E | 23128 | 15600 | 0
SCE | 19935 | 13000 | 0
SDG&E |  | 2950 | 0
CAISO | 45884 | 32279 |  | 32279 | 32279
Scheduling Coordinator Forecast |  | 23205
SMUD | 2759 | 0 | 0
LADWP |  | 3600 | 0 |  |  |  |  | HE | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000
Ties |  | 691 |  | 2247 | 2247 |  |  |  | 2247 | 1515 | 1480 | 1497 | 1474 | 1362 | 1268 | 1339 | 1445 | 1326
Out of Market Purchases OOM |  | 0
Interruptible Load shed |  | 1600 |  | 1250 | 1600 |  |  |  | 7:30 |  | 10:00 |  | 13:00
Firm Load shed |  | 500 |  |  | 2000 |  |  | hour | CA wide | SMUD |  | SMUD
CAISO % reserves |  | 3% |  | 2.7% | 3.2% | 6% |  | HE 10 | 500 | 30
CA Generation Planned out |  | 4251 | [5 empty] | HE 11 | 500 | 30 | 500 | 30
North Path 15 |  | 1901 | [5 empty] | HE 12 | 1000 | 59 | 2000 | 119
South Path 15 |  | 1572 | [5 empty] | HE 13 | 500 | 30 | 1500 | 89
CA Generation Forced out |  | 6883 | [5 empty] | HE 14 | 0 | 0 | 1000 | 59
North Path 15 |  | 2350 |  |  | 175 |  |  | HE 15 | 0 | 0 | 800
South Path 15 |  | 5311 |  |  | 300 |  |  | HE 16 | 0 | 0 | 0
CA Generation out for other reasons |  | 11134 | [5 empty] | HE 17 | 0 | 0 | 0
Total CA generation out of service | 14646 | 0 | [5 empty] | HE 18 | 2000 | 119 | 2000 | 119 | 2000
[8 empty] | HE 19 | 1500 | 89 | 1500 | 89 | 1500
7:30 | [7 empty] | HE 20 | 1000 | 59 | 1000 | 59 | 1000
Stage 3 all day | [7 empty] | HE 21 | 0 |  | 0
Imports during the Peak 691MW
Interruptibles off for all 6 hours
Cogeneration 300MW hours less than yesterday
Wind generation is down
DGS to do everything | [8 empty] | CA Wide | SMUD share
Grocerers to do the same | [7 empty] | 1700-1800 | 2000 | 119
CDWR pumps off starting to impact | [7 empty] | 1800-1900 | 1500 | 89
550 pumps off yesterday all of non firm | [7 empty] | 1900-2000 | 1000 | 59
42 % of SCE interruptible load | [7 empty] | 2000-2001 | 0
1600 MW off at this time
1000 call
Asking SDG&E to extend nonfirm load shed
presently 2.5% reserves
all nonfirm and pump loads
may cycle pumps
Next call 1330
do not diseminate to others
notice going out to OES
Do not do anything until formal notice
1330 call
Currently 500 MW firm load interrupted
Second 500 MW blockoff but
Will restore shortly but not stand down
interruptible load off through 2100 tonight
Projecting
Large unit in SDG&E tripped back in an hour
State wide tonight
175 MW tripped initiated the trip
running helms is out of water saving for evening peak
Path 15 at the limit and increase path 15 limit
lower kings river generation level
Mitigate path 15 with load shed
lost Morro Bay
1630 hours next call
1630 call
Powerex and ladwp provided 1200 MW
one hour at a time
0 to 500 MW off in case this stuff goes away
CDWR sleaving
additional units coming on line in SDG&E
need to get stand down orders to get folks ready for tommorrow

## 1-18
SYSTEM OPERATIONS AND RELIABILITY SUMMARY FOR 1/18/2001
Time of Conference Call 1/18/01 10:00 | All Time | 2001-01-17 |  | 2001-01-18 |  | 2001-01-19
Load Forecasts/Actual | Record | Load | Temp | Load | Temp | Load | Temp
PG&E | 23128 |  |  | 15000
SCE | 19935 |  |  | 12600
SDG&E |  |  |  | 2850
CAISO | 45884 | 29724 |  | 31856 |  | 30758
Scheduling Coordinator Forecast |  |  |  | 23451 |  |  |  | 8405 | 2500
SMUD | 2759
LADWP |  |  |  | 3600
Ties |  |  |  | 1138
Out of Market Purchases OOM
Interruptible Load shed |  | 1400 | [5 empty] | 500 | pump
Firm Load shed |  |  |  | 1800
CAISO % reserves |  | 4.1% |  | 4.3%
CA Generation Planned out |  |  |  | 3243
North Path 15 |  |  |  | 902
South Path 15 |  |  |  | 2341
CA Generation Forced out |  |  |  | 7850
North Path 15 |  |  |  | 3273
South Path 15 |  |  |  | 4577
CA Generation out for other reasons
Total CA generation out of service | 14646 |  |  | 11093
| All Time | 2001-01-18 |  | 10:00 | 13:30 | 16:00 | 16:30
Peak Load Forecasts/Actual | Record | Load | Temp | Load | Load | Load | Load
PG&E | 23128 | 15000 | 0
SCE | 19935 | 12600 | 0
SDG&E |  | 2850 | 0
CAISO | 45884 | 31856 |  | 31856 | 31856
Scheduling Coordinator Forecast |  | 23451
SMUD | 2759 | 0 | 0
LADWP |  | 3600 | 0 |  |  |  |  | HE | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000
Ties |  | 1138 |  |  | 3802 | 3942 |  | 1507 | preschedule
Out of Market Purchases OOM |  | 0
Interruptible Load shed |  | 0 | [6 empty] | 7:30 |  | 10:00 |  | 13:00
Firm Load shed |  | 1800 | [5 empty] | hour | CA wide | SMUD |  | SMUD
CAISO % reserves |  | 4.3% |  | 4.9% |  | 6.3% |  | HE 10
CA Generation Planned out |  | 3243 | [5 empty] | HE 11
North Path 15 |  | 902 | [5 empty] | HE 12
South Path 15 |  | 2341 | [5 empty] | HE 13
CA Generation Forced out |  | 7850 | [5 empty] | HE 14
North Path 15 |  | 3273 | [5 empty] | HE 15
South Path 15 |  | 4577 | [5 empty] | HE 16
CA Generation out for other reasons |  | 0 | [5 empty] | HE 17
Total CA generation out of service | 14646 | 11093 | [5 empty] | HE 18 | 1800
[8 empty] | HE 19 | 1100
7:30 | [7 empty] | HE 20 | 700
All interruptible load is off at this time | [7 empty] | HE 21
9 hours at helms single unit
two units at helms running currently
interruption of load scheduled same as yesterday
1000 MW from BPA currently and will run out at 1000 hours
Nothing from NW | [8 empty] | CA Wide | SMUD share
1000 hours | [7 empty] | 1700-1800 | 1800 | 107
HE 18 Interruptible off again | [7 empty] | 1800-1900 | 1100 | 65
Restore interruptable 1100 | [7 empty] | 1900-2000 | 700 | 42
1800 MW firm load is off | [7 empty] | 2000-2001 | 0
Northern CA shed 500 to 1000 due to path 15 this morning
official notification for stand down from firm load
Gas issue for Roseville turbine
SDG&E curtailment for gas rotating curtailment
232 MW unit in the south trying to come back
Next call 1000
Waiting letter of credit
Checked with CDWR will sleave within the state
1000 hours
1000 MW off of NP15
600 MW curtailment on southern part of the state
any more loss of resources will trigger more load shed
no letter of credit
Helm down to 5 hours of single unit operation saving some for peak hours
duration of firm load shed 10:45 decision
Two worse day in a row
1330 call
Restored all firm customer load 1200
5 hours of helmss single unit
, all interruptable pump off 800 firm off 2.5 % reserves
if able to procure 2000 MW more 5.6 % reserve and just pump off
not standing down
hour to hour call to see if firm load shed is needed
Schedules are not firm yet but making progress
AB 1X is on the governor
Scenario two 15 to 24 is clear
1600 next call
1600 call
800 MW may need shed if schedules does not show up
needing 2000 MW of ties for 18 19 20
May be able to recover non firm load if tie flow show up
HE 21 all non firm restored regardless
Sellers are not commiting more than hourly
SCE to call all interruptible off
IPP resource is back on line
LADWP may be able to provide something with IPP back
2013 MW below yesterdays peak
tomorrow
need only 2500 MW to have no nonfirm load off
need to find 500 to 1800 MW in the morning hours to avoid nonfirm load shed
HE10 need 1800 MW, 1400 MW nonfirm then need 400 MW interrupted
Assuming no helms and no kings river
If kings river runs, No water for Helms to pump back
Generation back only one unit in the south
Next call 0730

## 1-19
SYSTEM OPERATIONS AND RELIABILITY SUMMARY FOR 1/19/2001
Time of Conference Call 1/19/01 10:00 | All Time | 2001-01-18 |  | 2001-01-19 |  | 2001-01-20
Load Forecasts/Actual | Record | Load | Temp | Load | Temp | Load | Temp
PG&E | 23128 |  |  | 14900
SCE | 19935 |  |  | 12300
SDG&E |  |  |  | 2800
CAISO | 45884 | 29537 |  | 30798
Scheduling Coordinator Forecast |  |  |  | 22618 |  |  |  | 8180
SMUD | 2759
LADWP |  |  |  | 3500
Ties |  |  |  | 3000
Out of Market Purchases OOM
Interruptible Load shed |  | 1204 |  | 1200
Firm Load shed |  |  |  | ?
CAISO % reserves |  | 4.1% |  | 4.1%
CA Generation Planned out |  |  |  | 2347
North Path 15
South Path 15 |  |  |  | 753
CA Generation Forced out |  |  |  | 7850
North Path 15 |  |  |  | 1508
South Path 15 |  |  |  | 6300
CA Generation out for other reasons
Total CA generation out of service | 14646 |  |  | 10197
| All Time | 2001-01-19 |  | 10:00 | 13:30 | 16:00 | 16:30
Peak Load Forecasts/Actual | Record | Load | Temp | Load | Load | Load | Load
PG&E | 23128 | 14900 | 0
SCE | 19935 | 12300 | 0
SDG&E |  | 2800 | 0
CAISO | 45884 | 30798
Scheduling Coordinator Forecast |  | 22618
SMUD | 2759 | 0 | 0
LADWP |  | 3500 | 0 |  |  |  |  | HE | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000
Ties |  | 3000 | [5 empty] | 1507 | preschedule
Out of Market Purchases OOM |  | 0
Interruptible Load shed |  | 1200 | [6 empty] | 7:30 |  | 10:00 |  | 13:00 | need MW
Firm Load shed |  | ? | [5 empty] | hour | CA wide | SMUD |  | SMUD
CAISO % reserves |  | 4.1% | [5 empty] | HE 10 | [5 empty] | 500
CA Generation Planned out |  | 2347 | [5 empty] | HE 11 | [5 empty] | 1200
North Path 15 |  | 0 | [5 empty] | HE 12 | [5 empty] | 1000
South Path 15 |  | 753 | [5 empty] | HE 13 | [5 empty] | 700
CA Generation Forced out |  | 7850 | [5 empty] | HE 14 | [5 empty] | 400
North Path 15 |  | 1508 | [5 empty] | HE 15
South Path 15 |  | 6300 | [5 empty] | HE 16
CA Generation out for other reasons |  | 0 | [5 empty] | HE 17
Total CA generation out of service | 14646 | 10197 | [5 empty] | HE 18 | 1800 |  |  |  |  | 1200
[8 empty] | HE 19 | 1100 |  |  |  |  | 500
7:30 | [7 empty] | HE 20 | 700 |  |  |  |  | 600
no pump load shed during the peak | [7 empty] | HE 21
expecting units back coal south and gas in norht
diablo rampin down over the weekend
interupptible off all peak hours
0600 lost a coal fired unit out in NW
[9 empty] | CA Wide | SMUD share
19 hours of single unit helms operation | [7 empty] | 1700-1800
State wide load shed | [7 empty] | 1800-1900
path 15 is 300 MW below its limit | [7 empty] | 1900-2000
3.4% operating reserves | [7 empty] | 2000-2001
no credit or financial problems today
CDWR $400,000
suppliers only hour at a time
helms 1 is back in service
next call 1000

## 1-22
SYSTEM OPERATIONS AND RELIABILITY SUMMARY FOR 1/22/2001
Time of Conference Call 1/22/01 10:00 | All Time | 2001-01-21 |  | 2001-01-22 |  | 2001-01-23 |  | 2001-01-24 |  | 2001-01-25
Load Forecasts/Actual | Record | Load | Temp | Load | Temp | Load | Temp
PG&E | 23128 |  |  | 15000
SCE | 19935 |  |  | 12700
SDG&E |  |  |  | 2800
CAISO | 45884 | 27657 |  | 32187
Scheduling Coordinator Forecast |  |  |  | 26988 |  |  |  | 5200
SMUD | 2759
LADWP |  |  |  | 3525
Ties |  |  |  | 3670
Out of Market Purchases OOM
Interruptible Load shed |  | 250 |  | 0 |  |  |  |  | np15
Firm Load shed
CAISO % reserves |  | 6.9% |  | 5.6%
CA Generation Planned out |  |  |  | 2604
North Path 15 |  |  |  | 764
South Path 15 |  |  |  | 1840
CA Generation Forced out |  |  |  | 4464
North Path 15 |  |  |  | 1622
South Path 15 |  |  |  | 2842
CA Generation out for other reasons
Total CA generation out of service | 14646 |  |  | 7068
| All Time | 2001-01-22 |  | 10:00 | 13:30 | 16:00 | 16:30
Peak Load Forecasts/Actual | Record | Load | Temp | Load | Load | Load | Load
PG&E | 23128 | 15000 | 0 |  | 14900
SCE | 19935 | 12700 | 0 |  | 12700
SDG&E |  | 2800 | 0 |  | 2700
CAISO | 45884 | 32187
Scheduling Coordinator Forecast |  | 26988
SMUD | 2759 | 0 | 0
LADWP |  | 3525 | 0 |  | 3525 |  |  | HE | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000
Ties |  | 3670 | [5 empty] | 1507 | preschedule
Out of Market Purchases OOM |  | 0
Interruptible Load shed |  | 0 |  | 250 |  |  |  |  | 7:30 |  | 10:00 |  | 13:00 | need MW
Firm Load shed |  | 0 | [5 empty] | hour | CA wide | SMUD |  | SMUD
CAISO % reserves |  | 5.6% | [5 empty] | HE 10
CA Generation Planned out |  | 2604 | [5 empty] | HE 11
North Path 15 |  | 764 | [5 empty] | HE 12
South Path 15 |  | 1840 | [5 empty] | HE 13
CA Generation Forced out |  | 4464 | [5 empty] | HE 14
North Path 15 |  | 1622 | [5 empty] | HE 15
South Path 15 |  | 2842 | [5 empty] | HE 16
CA Generation out for other reasons |  | 0 | [5 empty] | HE 17
Total CA generation out of service | 14646 | 7068 | [5 empty] | HE 18
HE 19
7:30 | [7 empty] | HE 20
dropped firm load 101 MW dropped 1410 requested 25 minutes | [7 empty] | HE 21
No interruptable load shed planned
one unit 13 hours operation at Helms 3 units available
Remain Stage 3 all day
Still dry
[9 empty] | CA Wide | SMUD share
next call 1000 | [7 empty] | 1700-1800
1000 call
PG&E Interruptible load is done for the rest of the year | [7 empty] | 1800-1900
Rain on Tuesday for north | [7 empty] | 1900-2000
Rain statewide Wednesday and Thursday possible on the weekend | [7 empty] | 2000-2001
Firm load shed from hear on out.
Some munis were selling outside of CA
next call 1330
1330 call
stuff has not changed
Path 15 still a problem or at its limit.
Evening peak with out
Next morning firm load interruption
See if CDWR can bring on energy from NW
Remain hydro is very limited
2 hours of helms may be left to get to
1200 and 1800 MW from CDWR
1500 MW of energy for the rest of the day
Next call 1600
1600 call
finish non firm program
2100 2400 hours resources run out and need to secure energy
No resources returning from this morning
Enough for day break tomorrow and then firm load shed
HE 0800 start firm load shed
Helms is limited and may not be enough to mitigate as northern CA hydro runs out
Can we use interruptible in So Cal? No because of Path 15
Restore Interruptable when 4.5 hour runs out, 1920 hours is the end
Next 0730 call

## 1-23
SYSTEM OPERATIONS AND RELIABILITY SUMMARY FOR 1/22/2001
Time of Conference Call 1/23/01 10:00 | All Time | 2001-01-22 |  | 2001-01-23 |  | 2001-01-24 |  | 2001-01-25 |  | 2001-01-26
Load Forecasts/Actual | Record | Load | Temp | Load | Temp | Load | Temp
PG&E | 23128 |  |  | 15100
SCE | 19935 |  |  | 12700
SDG&E |  |  |  | 2750
CAISO | 45884 | 30315 |  | 31883
Scheduling Coordinator Forecast |  |  |  | 24217 |  |  |  | 7660
SMUD | 2759
LADWP |  |  |  | 3500
Ties |  |  |  | 3135
Out of Market Purchases OOM
Interruptible Load shed |  | 350 |  | 500
Firm Load shed
CAISO % reserves |  | 7.4% |  | 5.4%
CA Generation Planned out |  |  |  | 2584
North Path 15 |  |  |  | 745
South Path 15 |  |  |  | 1839
CA Generation Forced out |  |  |  | 4467
North Path 15 |  |  |  | 1262
South Path 15 |  |  |  | 3205
CA Generation out for other reasons
Total CA generation out of service | 14646 |  |  | 7051
| All Time | 2001-01-23 |  | 10:00 | 13:30 | 16:00 | 16:30
Peak Load Forecasts/Actual | Record | Load | Temp | Load | Load | Load | Load
PG&E | 23128 | 15100 | 0
SCE | 19935 | 12700 | 0
SDG&E |  | 2750 | 0
CAISO | 45884 | 31883 |  | 31854
Scheduling Coordinator Forecast |  | 24217
SMUD | 2759 | 0 | 0
LADWP |  | 3500 | 0 |  |  |  |  | HE | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000
Ties |  | 3135 |  | 3135 |  |  |  | 1507 | preschedule
Out of Market Purchases OOM |  | 0
Interruptible Load shed |  | 500 |  | 400 |  |  |  |  | 7:30 |  | 10:00 |  | 13:00 | need MW
Firm Load shed |  | 0 | [5 empty] | hour | CA wide | SMUD |  | SMUD
CAISO % reserves |  | 5.4% |  | 5.3% |  |  |  | HE 10
CA Generation Planned out |  | 2584 | [5 empty] | HE 11
North Path 15 |  | 745 | [5 empty] | HE 12
South Path 15 |  | 1839 | [5 empty] | HE 13
CA Generation Forced out |  | 4467 | [5 empty] | HE 14
North Path 15 |  | 1262 | [5 empty] | HE 15
South Path 15 |  | 3205 | [5 empty] | HE 16
CA Generation out for other reasons |  | 0 | [5 empty] | HE 17
Total CA generation out of service | 14646 | 7051 | [5 empty] | HE 18
HE 19
7:30 | [7 empty] | HE 20
All interruptable in Northern CA gone | [7 empty] | HE 21
ZP26 still available
large thermal unit out and coming back in the north 750 MW
Nw interchange procured for morning to avoid load shed
NW deal was extened 2400 but that is no longer the case
[9 empty] | CA Wide | SMUD share
No firm load shed planned | [7 empty] | 1700-1800
1340 MW was flowing on the COI
DOE will run out tonight and requesting extention with new administration | [7 empty] | 1800-1900
1000 MW not arranged for tommorrow | [7 empty] | 1900-2000
helms has 14 hours of single unit availablity or 4 hours 3 unit operation | [7 empty] | 2000-2001
Converter 3 will be back tonight
State going out for auction today for long term
Limit on DC 1100 MW 720 ISO share
Next call 1000
1000 Call
Looking good for 19 to 20
Large unit in North is not turning on steam and two da
17 18 400 MW interuptible off
CDWR working on deals in the NW
LADWP has resources tonight
Next call 1330

## 1-26
SYSTEM OPERATIONS AND RELIABILITY SUMMARY FOR 1/26/2001
Time of Conference Call 1/26/01 7:30 | All Time | 2001-01-25 |  | 2001-01-26 |  | 2001-01-27 |  | 2001-01-28 |  | 2001-01-29
Load Forecasts/Actual | Record | Load | Temp | Load | Temp | Load | Temp
PG&E | 23128 |  |  | 15200
SCE | 19935 |  |  | 12450
SDG&E |  |  |  | 2850
CAISO | 45884 | 31357 |  | 30559 |  | 27620 |  | 27830 |  | 31532
Scheduling Coordinator Forecast |  |  |  | 24525
SMUD | 2759
LADWP |  |  |  | 3550
Ties |  | 3715 |  | 3300
Out of Market Purchases OOM
Interruptible Load shed
Firm Load shed | [9 empty] | 1050
CAISO % reserves |  | 6.7% |  | 7% | [5 empty] | 5%
CA Generation Planned out |  |  |  | 3224
North Path 15 |  |  |  | 890
South Path 15 |  |  |  | 2334
CA Generation Forced out |  |  |  | 4253
North Path 15 |  |  |  | 2243
South Path 15 |  |  |  | 2010
CA Generation out for other reasons
Total CA generation out of service | 14646
| All Time | 2001-01-26 |  | 10:00 | 13:30 | 16:00 | 16:30
Peak Load Forecasts/Actual | Record | Load | Temp | Load | Load | Load | Load
PG&E | 23128 | 15200 | 0
SCE | 19935 | 12450 | 0
SDG&E |  | 2850 | 0
CAISO | 45884 | 30559 |  |  | 30559
Scheduling Coordinator Forecast |  | 24525
SMUD | 2759 | 0 | 0
LADWP |  | 3550 | 0 |  |  |  |  | HE | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000
Ties |  | 3300 | [5 empty] | 1507 | preschedule
Out of Market Purchases OOM |  | 0
Interruptible Load shed |  | 0 |  | 1000 | 1000 |  |  |  | 7:30 |  | 10:00 |  | 13:00 | need MW
Firm Load shed |  | 0 | [5 empty] | hour | CA wide | SMUD |  | SMUD
CAISO % reserves |  | 7% |  |  | 5% |  |  | HE 10
CA Generation Planned out |  | 3224 |  |  | 260 |  |  | HE 11
North Path 15 |  | 890 | [5 empty] | HE 12
South Path 15 |  | 2334 | [5 empty] | HE 13
CA Generation Forced out |  | 4253 | [5 empty] | HE 14
North Path 15 |  | 2243 | [5 empty] | HE 15
South Path 15 |  | 2010 | [5 empty] | HE 16
CA Generation out for other reasons |  | 0 | [5 empty] | HE 17
Total CA generation out of service | 14646 | 0 | [5 empty] | HE 18
HE 19
7:30 | [7 empty] | HE 20
Stage 3 to get BPA emergency energy till noon | [7 empty] | HE 21
Returning energy
750 MW unit back on Monday 2000
22 hours of single unit Helms operation avaiable
some other unit at half power coming back
Next call 1330
1000 call
AZ and RM NERC Stage 2 1500 to 2000 MW less from SW
Shedding interruptables in SCE and SDG&E
800 MW below qf generation
ZP 26 interruptibles also
Interruptable for the duration for today
1330 call
Coal fired unit out in AZ
QF down 600 MW
Gas curtailment for SDG&E throu 1400
60 MW of CT not available
Curtailments of units on the coast 400 MW curtailment
Very little SDG&E contribution due to weather condition rain no rocks
units in SDG&E coming on line
import for east are being restored only 200 MW lower than yesterday
NERC stage 2 is off from this morning may be a mistake
Next call 1600
Interruptible off for duration
1600 call
Stage 3 tonight and the weekend with adequate reserves
0010-02 draft decision from CPUC relieves interruptible load
2 units in SDG&E are available and ramping up
No load off this weekend
They are expected to perform but don't have to
15 hours of single unit operation at Helms
Next call 0730

## 1-29
SYSTEM OPERATIONS AND RELIABILITY SUMMARY FOR 1/29/2001
Time of Conference Call 1/29/01 7:30 | All Time | 2001-01-28 |  | 2001-01-29 |  | 2001-01-30 |  | 2001-01-31 |  | 2001-02-01
Load Forecasts/Actual | Record | Load | Temp | Load | Temp | Load | Temp
PG&E | 23128 |  |  | 14900
SCE | 19935 |  |  | 12950
SDG&E |  |  |  | 2870
CAISO | 45884 | 26429 |  | 31217 |  | 31223
Scheduling Coordinator Forecast |  |  |  | 26028
SMUD | 2759
LADWP |  |  |  | 3577
Ties |  |  |  | 2690
Out of Market Purchases OOM
Interruptible Load shed |  |  |  | 0
Firm Load shed |  |  |  | 0
CAISO % reserves |  |  |  | 5.5%
CA Generation Planned out
North Path 15 |  |  |  | 1176
South Path 15 |  |  |  | 3632
CA Generation Forced out
North Path 15 |  |  |  | 1949
South Path 15 |  |  |  | 1966
CA Generation out for other reasons
Total CA generation out of service | 14646 |  |  | 8723
| All Time | 2001-01-29 |  | 10:00 | 13:30 | 16:00 | 16:30
Peak Load Forecasts/Actual | Record | Load | Temp | Load | Load | Load | Load
PG&E | 23128 | 14900 | 0
SCE | 19935 | 12950 | 0
SDG&E |  | 2870 | 0
CAISO | 45884 | 31217 |  |  | 31217
Scheduling Coordinator Forecast |  | 26028
SMUD | 2759 | 0 | 0
LADWP |  | 3577 | 0 |  |  |  |  | HE | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000
Ties |  | 2690 | [5 empty] | 1507 | preschedule
Out of Market Purchases OOM |  | 0
Interruptible Load shed |  | 0 | [6 empty] | 7:30 |  | 10:00 |  | 13:00 | need MW
Firm Load shed |  | 0 | [5 empty] | hour | CA wide | SMUD |  | SMUD
CAISO % reserves |  | 5.5% | [5 empty] | HE 10
CA Generation Planned out |  | 0 | [5 empty] | HE 11
North Path 15 |  | 1176 | [5 empty] | HE 12
South Path 15 |  | 3632 | [5 empty] | HE 13
CA Generation Forced out |  | 0 | [5 empty] | HE 14
North Path 15 |  | 1949 | [5 empty] | HE 15
South Path 15 |  | 1966 | [5 empty] | HE 16
CA Generation out for other reasons |  | 0 | [5 empty] | HE 17
Total CA generation out of service | 14646 | 8723 | [5 empty] | HE 18
HE 19
7:30 | [7 empty] | HE 20
900 to 1000 MW off on Friday 6.9 % reserves | [7 empty] | HE 21
26429 Sunday 7+ reserves
Stage 3 for BPA all day 500 MW per hour
750 1000 MW from CDWR
Ask for non-firm by ISO giving a total and the PTO should manage the communication and amount of call
If interruptibles don't perform then firm load shed
next call 1330
DOE certified for today
1330 call
still need 1000 MW of the ties
ISO will try to get nonfirm load if unsuccessful for 18 and 19
Around 1000MW have been show up each hour
ISO is fairly confident that they will get it
CDWR is still procuring
Some available from LADWP
Next call 1600
1600 call
same conditions tomorrow
secured the needed energy
load is running a little lower than forecast but one unit is not coming on as scheduled.

## 1-30
SYSTEM OPERATIONS AND RELIABILITY SUMMARY FOR 1/30/2001
Time of Conference Call 1/30/01 7:30 | All Time | 2001-01-29 |  | 2001-01-30 |  | 2001-01-31 |  | 2001-02-01 |  | 2001-02-02
Load Forecasts/Actual | Record | Load | Temp | Load | Temp | Load | Temp
PG&E | 23128 |  |  | 15100
SCE | 19935 |  |  | 12900
SDG&E |  |  |  | 2840
CAISO | 45884 | 30789 |  | 31223 |  | 30760
Scheduling Coordinator Forecast |  |  |  | 24825 |  |  |  | 6400
SMUD | 2759
LADWP |  |  |  | 3570
Ties |  | 3157
Out of Market Purchases OOM
Interruptible Load shed
Firm Load shed
CAISO % reserves |  | 4.5%
CA Generation Planned out
North Path 15 |  |  |  | 1098
South Path 15 |  |  |  | 3421
CA Generation Forced out
North Path 15 |  |  |  | 1997
South Path 15 |  |  |  | 2002
CA Generation out for other reasons
Total CA generation out of service | 14646 |  |  | 8518
| All Time | 2001-01-30 |  | 10:00 | 13:30 | 16:00 | 16:30
Peak Load Forecasts/Actual | Record | Load | Temp | Load | Load | Load | Load
PG&E | 23128 | 15100 | 0
SCE | 19935 | 12900 | 0
SDG&E |  | 2840 | 0
CAISO | 45884 | 31223 |  |  | 31009 | 31009
Scheduling Coordinator Forecast |  | 24825
SMUD | 2759 | 0 | 0
LADWP |  | 3570 | 0 |  |  |  |  | HE | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000
Ties |  | 0 | [5 empty] | 1507 | preschedule
Out of Market Purchases OOM |  | 0
Interruptible Load shed |  | 0 |  |  | 600 | 500 |  |  | 7:30 |  | 10:00 |  | 13:00 | need MW
Firm Load shed |  | 0 | [5 empty] | hour | CA wide | SMUD |  | SMUD
CAISO % reserves |  | 0% |  |  | 5.2% |  |  | HE 10
CA Generation Planned out |  | 0 | [5 empty] | HE 11
North Path 15 |  | 1098 | [5 empty] | HE 12
South Path 15 |  | 3421 | [5 empty] | HE 13
CA Generation Forced out |  | 0 | [5 empty] | HE 14
North Path 15 |  | 1997 | [5 empty] | HE 15
South Path 15 |  | 2002 | [5 empty] | HE 16
CA Generation out for other reasons |  | 0 | [5 empty] | HE 17
Total CA generation out of service | 14646 | 8518 | [5 empty] | HE 18 | 600 |  |  |  | 1836
[8 empty] | HE 19 | 300 |  |  |  | 1891
7:30 | [7 empty] | HE 20
Stage 3 15 strait day | [7 empty] | HE 21
Large unit in N CA has been extended a couple of days
Load is trending 1500 MW over yesterday
DGS is getting tired of Stage 3 Emergency
1000 MW on ties needed to make 5.0% reserves
3000 MWh scheduled from BPA used 2000 MWh already
CDWR is finding energy hour by hour
ISO will hold off on voluntary
49 hours at Helms
16 hours of three unit operation
QF are running 600 MW below yesterday
Next call 1000
1000 call
curtail pump load calling on muni gen and northern ca gen
Don't know what to shed or
700 MW cut on the COI, suspect it is financial
Tonight for the peak state wide but for now just NP 15
Path 15 3352 rating 3104 presently flowing
No nonfirm available in the north
PG&E will make requests for nonfirm anyway
may be curtailing in the next hour
Next call 1330
1330 Call
will need load off for HE 18 and 19 statewide
Hour by hour situation
Dodged the bullet this morning
700 MW deal went away, they will not do business with the ISO
Next call 1600
1600 Call
See what they can get with interruptibles
HE 18 is the only hour they need
300 MW of pump load
LADWP has indicated some energy available
1000 total from CDWR now and 1900 was available yesterday
No better shape for tommorrow
QF working deal with CDWR 475 MW

## 2-2
SYSTEM OPERATIONS AND RELIABILITY SUMMARY FOR 2/7/2001
Time of Conference Call 2/2/01 7:30 | All Time | 2001-02-06 |  | 2001-02-07 |  | 2001-02-08 |  | 2001-02-09 |  | 2001-02-10
Load Forecasts/Actual | Record | Load | Temp | Load | Temp | Load | Temp
PG&E | 23128 |  |  | 15200
SCE | 19935 |  |  | 12500
SDG&E |  |  |  | 2700
CAISO | 45884 | 30307 |  | 31000 |  | 30493
Scheduling Coordinator Forecast |  |  |  | 23061 |  |  |  | 7950
SMUD | 2759
LADWP |  |  |  | 3535
Ties |  | 4796 |  | 2607
Out of Market Purchases OOM
Interruptible Load shed |  |  |  | 0
Firm Load shed |  |  |  | 0
CAISO % reserves | 8% | 7% |  | 5.6%
CA Generation Planned out
North Path 15 |  |  |  | 934
South Path 15 |  |  |  | 1574
CA Generation Forced out
North Path 15 |  |  |  | 1507
South Path 15 |  |  |  | 4017
CA Generation out for other reasons
Total CA generation out of service | 14646 |  |  | 8032
| All Time | 2001-02-07 |  | 10:00 | 13:30 | 16:00 | 16:30
Peak Load Forecasts/Actual | Record | Load | Temp | Load | Load | Load | Load
PG&E | 23128 | 15200 | 0
SCE | 19935 | 12500 | 0
SDG&E |  | 2700 | 0
CAISO | 45884 | 31000 |  |  |  | 31000
Scheduling Coordinator Forecast |  | 23061
SMUD | 2759 | 0 | 0
LADWP |  | 3535 | 0 |  |  |  |  | HE | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000
Ties |  | 2607 | [5 empty] | 1507 | preschedule
Out of Market Purchases OOM |  | 0
Interruptible Load shed |  | 0 | [6 empty] | 7:30 |  | 10:00 |  | 13:00 | need MW
Firm Load shed |  | 0 | [5 empty] | hour | CA wide | SMUD |  | SMUD
CAISO % reserves |  | 5.6% | [5 empty] | HE 10
CA Generation Planned out |  | 0 | [5 empty] | HE 11
North Path 15 |  | 934 | [5 empty] | HE 12
South Path 15 |  | 1574 | [5 empty] | HE 13
CA Generation Forced out |  | 0 | [5 empty] | HE 14
North Path 15 |  | 1507 | [5 empty] | HE 15
South Path 15 |  | 4017 | [5 empty] | HE 16
CA Generation out for other reasons |  | 0 | [5 empty] | HE 17
Total CA generation out of service | 14646 | 8032 | [5 empty] | HE 18 | 600 |  |  |  | 1836
[8 empty] | HE 19 | 300 |  |  |  | 1891
7:30 | [7 empty] | HE 20
2000 large unit not back untill then | [7 empty] | HE 21
5300 QF generation this morning
1900 no load off and more than enough reserves
restraining order till the end of the hearing
Generators are to follow the ISO instructions
TRO temporary restraining order
Stage 3 for federal energy
Call at 1530
1530 call
adequate reserves
no word on hearing
External companies are commited to keep supply coming
No gas update either
Next call 0730