## Sheet1
| Corrected to 90F, 60%, 14.696 psia |  |  |  | Corrected to 15% O2
Gleason | Turbine | Net Electrical Output | Heat Rate | Aux. Loads | Nox (corr.) | CO (corr.) | Starts | Total Run-Hours
|  | (kW) | Btu/kWh (LHV) | (kW) | ppm | ppm
Unit 1 | Westinghouse 501FD | 178188 | 9908 | 293 | 24.45 | 10.44
Unit 2 | Westinghouse 501FD | 181976 | 9821 | 273 | 24.25 | 15.44
Unit 3 | Westinghouse 501FC | 180619 | 9888 | 369 | 23.9 | 13.8
Control System - Westinghouse WDPF
Wheatland
Unit 1 | Westinghouse 501D5A | 119445 | 10540 | 215 | 23 | 6.1
Unit 2 | Westinghouse 501D5A | 120217 | 10451 | 213 | 24.3 | 21.8
Unit 3 | Westinghouse 501D5A | 116109 | 10465 | 189 | 22.3 | 6.8
Unit 4 | Westinghouse 501D5A | 119227 | 10433 | 204 | 23.7 | 11.2
Control System - Westinghouse WDPF
Corrected to 90F, 60%, 14.34 psia
Wilton/Lincoln Center
Raw Emissions Data
Unit 1 | General Electric 7EA | 78166 | 10622 | 166 | 9.44 | 11.78
Unit 2 | General Electric 7EA | 77651 | 10641 | 166 | 9.18 | 18.37
Unit 3 | General Electric 7EA | 76539 | 10545 | 163 | 8.76 | 12.6
Unit 4 | General Electric 7EA | 76685 | 10650 | 158 | 8.84 | 33.11
Unit 5 | General Electric 7EA | 77293 | 10717 | 166 | 8.33 | 55.52
Unit 6 | General Electric 7EA | 78368 | 10641 | 159 | 9.53 | 15.73
Unit 7 | General Electric 7EA | 78360 | 10690 | 158 | 7.48 | 62.59
Unit 8 | General Electric 7EA | 77708 | 10694 | 160 | 7 | N/A
Control System - GE Mark V