## Summery - Base Load
Recommended Spare Parts
Enron Puerto Suarez/IPS-91209
MS 7001 EA, DLN1-25, Gas Fuel
| FIRED | INSPECT
YEAR | HOURS | HOURS | INSPECTION / PARTS | SETS | UNIT PRICE | SUB-TOTAL
0 |  |  | Combustion Inspection Capitals | 1 | 2094605.3 | 2094605.3
|  |  | Operational Spares | 1 | 339496.82 | 339496.82
|  |  | Controls | 1 | 127435.42 | 127435.42
|  |  | Generator Consumables | 1 | 9491.61 | 9491.61
|  |  | Generator Maintenance | 1 | 86576.43 | 86576.43
|  |  | Excitation | 1 | 66343.64 | 66343.64
1 | 8000 | 8000 | Combustion Inspection Consumables | 1 | 20332.17 | 20332.17
2 | 16000 | 16000 | Combustion Inspection Consumables | 1 | 20332.17 | 20332.17
3 | 24000 | 24000 | Combustion Inspection Consumables | 1 | 20332.17 | 20332.17
|  |  | Hot Gas Path Inspection | 1 | 11996 | 11996
4 | 32000 | 32000 | Combustion Inspection Consumables | 1 | 20332.17 | 20332.17
5 | 40000 | 40000 | Combustion Inspection Consumables | 1 | 20332.17 | 20332.17
6 | 48000 | 48000 | Combustion Inspection Consumables | 1 | 20332.17 | 20332.17
|  |  | Hot Gas Path Inspection | 1 | 11996 | 11996
|  |  | Turbine Capitals | 1 | 7760351.9 | 7760351.9
|  |  | Major Inspection | 1 | 122136.42 | 122136.42
|  |  | Generator Capitals | 1 | 294564.61 | 294564.61
|  |  | TOTAL: |  | 11046987.17 | 11046987.17
Assumptions:
List Types:

## CI Capitals
[7 empty] | List Total: |  |  |  | List Total: | Credit Total
[7 empty] | 1229457.53 |  |  |  | 2094605.3 | 0
GT Combustion Inspection Capitals
LINE | CATALOG | CAT | [6 empty] | SIMILAR-TO | UNIT
ITEM | NUMBER | LOC | PART NAME | PART DESCRIPTION | CYC | QTY | SYS PRICE | UM | DWG NUMBER | PRICE | LINE PRICE
____________
1 | G051300 |  | NOZZLE | FUEL NOZZLE, ASSEMBLY GAS | 13 | 10 | 37181 |  | 112E1994G017 | 37181 | 371810
2 | G056600 |  | NOZZLE | FUEL NZL, SECONDARY | 16 | 10 | 11766 |  | 112E6364G016 | 11766 | 117660
3 | G070101 | 1 | SLEEVE | CHAMBER ARR, FLOW SLEEVE | 19 | 1 | 7439 |  | 110E1161G006 | 7439 | 7439
4 | G070101 | 2 | SLEEVE | CHAMBER ARR, FLOW SLEEVE | 18 | 1 | 7439 |  | 110E1161G007 | 7439 | 7439
5 | G070101 | 3 | SLEEVE | CHAMBER ARR, FLOW SLEEVE | 18 | 1 | 7439 |  | 110E1161G009 | 7439 | 7439
6 | G070101 | 4 | SLEEVE | CHAMBER ARR, FLOW SLEEVE | 18 | 1 | 7439 |  | 110E1161G009 | 7439 | 7439
7 | G070101 | 5 | SLEEVE | CHAMBER ARR, FLOW SLEEVE | 18 | 1 | 7439 |  | 110E1161G007 | 7439 | 7439
8 | G070101 | 6 | SLEEVE | CHAMBER ARR, FLOW SLEEVE | 18 | 1 | 7439 |  | 110E1161G007 | 7439 | 7439
9 | G070101 | 7 | SLEEVE | CHAMBER ARR, FLOW SLEEVE | 19 | 1 | 7439 |  | 110E1161G008 | 7439 | 7439
10 | G070101 | 8 | SLEEVE | CHAMBER ARR, FLOW SLEEVE | 19 | 1 | 7439 |  | 110E1161G008 | 7439 | 7439
11 | G070101 | 9 | SLEEVE | CHAMBER ARR, FLOW SLEEVE | 18 | 1 | 7439 |  | 110E1161G007 | 7439 | 7439
12 | G070101 | 10 | SLEEVE | CHAMBER ARR, FLOW SLEEVE | 19 | 1 | 7439 |  | 110E1161G006 | 7439 | 7439
13 | G07016S |  | TUBE | CHAMBER ARR, XFIRE-MALE,TUBE | 11 | 10 | 371.7 |  | 169D3441P001 | 371.7 | 3717
14 | G07016V |  | TUBE | CHAMBER ARR, XFIRE OUTER,TUBE | 11 | 10 | 156.98 |  | 207C3557P001 | 156.98 | 1569.8
15 | G07016Y |  | TUBE | CHAMBER ARR, XFIRE-FEMALE,TUBE | 11 | 10 | 345.45 |  | 169D3442P001 | 345.45 | 3454.5
16 | G070200 |  | PIECE-TRANSITION | TRANS PC ASM, COMB, ASSEMBLY | 19 | 10 | 46306.4 |  | 943E0236G016 | 46306.4 | 463064
17 | G070301 | 1 | LINER | CAP & LINER ASSY, COMBUSTION,LINER | 18 | 1 | 105894 |  | 111E8955G005 | 105894 | 105894
18 | G070301 | 2 | LINER | CAP & LINER ASSY, COMBUSTION,LINER | 18 | 1 | 105894 |  | 111E8955G005 | 105894 | 105894
19 | G070301 | 3 | LINER | CAP & LINER ASSY, COMBUSTION,LINER | 18 | 1 | 105894 |  | 111E8955G005 | 105894 | 105894
20 | G070301 | 4 | LINER | CAP & LINER ASSY, COMBUSTION,LINER | 18 | 1 | 105894 |  | 111E8955G005 | 105894 | 105894
21 | G070301 | 5 | LINER | CAP & LINER ASSY, COMBUSTION,LINER | 18 | 1 | 105894 |  | 111E8955G005 | 105894 | 105894
22 | G070301 | 6 | LINER | CAP & LINER ASSY, COMBUSTION,LINER | 18 | 1 | 105894 |  | 111E8955G005 | 105894 | 105894
23 | G070301 | 7 | LINER | CAP & LINER ASSY, COMBUSTION,LINER | 18 | 1 | 105894 |  | 111E8955G005 | 105894 | 105894
24 | G070301 | 8 | LINER | CAP & LINER ASSY, COMBUSTION,LINER | 18 | 1 | 105894 |  | 111E8955G005 | 105894 | 105894
25 | G070301 | 9 | LINER | CAP & LINER ASSY, COMBUSTION,LINER | 18 | 1 | 105894 |  | 111E8955G005 | 105894 | 105894
26 | G070301 | 10 | LINER | CAP & LINER ASSY, COMBUSTION,LINER | 18 | 1 | 105894 |  | 111E8955G005 | 105894 | 105894

## CI Consumables
[7 empty] | List Total: |  |  |  | List Total: | Credit Total
[7 empty] | 2375.69 |  |  |  | 20332.17 | 0
GT Combustion Inspection Consumables
LINE | CATALOG | CAT | [6 empty] | SIMILAR-TO | UNIT
ITEM | NUMBER | LOC | PART NAME | PART DESCRIPTION | CYC | QTY | SYS PRICE | UM | DWG NUMBER | PRICE | LINE PRICE
____________
1 | G05660D |  | GASKET | FUEL NZL, SEC, FLM DET, GASKET | 8 | 10 | 7.81 |  | 302A4594P302 | 7.81 | 78.1
2 | G070107 |  | RETAINER | CHAMBER ARR, CROSSFIRE TUBE,RETNR | 11 | 20 | 164.22 |  | 207C3558P001 | 164.22 | 3284.4
3 | G07010A |  | BOLT | CHAMBER ARR, FLOW SLEEVE, BOLT | 5 | 40 | 2.36 |  | N28P25010 | 2.36 | 94.4
4 | G07010G |  | GASKET | CHAMBER ARR, FUEL NOZZLE, GASKET | 6 | 10 | 17 |  | 344A5938P008 | 17 | 170
5 | G07010M |  | BOLT | CHAMBER ARR, FUEL NOZZ, MNTNG BOLT | 14 | 12 | 31.9 |  | N733AP33072 | 31.9 | 382.8
6 | G07010P |  | BOLT | CHAMBER ARR, SPARK PLUG, MNTNG BOLT | 11 | 2 | 15.03 |  | N733AP33032 | 15.03 | 30.06
7 | G07010V |  | GASKET | CHAMBER ARR, SPARK PLUG, GASKET | 6 | 2 | 4.6 |  | 318A9713P038 | 4.6 | 9.2
8 | G07010Y |  | GASKET | CHAMBER ARR, FLAME DETECTOR, GASKET | 6 | 4 | 10.85 |  | 258B8786P002 | 10.85 | 43.4
9 | G07010Z |  | BUSHING | CHAMBER ARR, FLAME DETECTOR, BUSHNG | 11 | 4 | 85.68 |  | 223C2131P001 | 85.68 | 342.72
10 | G070114 |  | GASKET | CHAMBER ARR, CASING, COVER, GASKET | 3 | 10 | 41.11 |  | 318A9713P028 | 41.11 | 411.1
11 | G070117 |  | BOLT | CHAMBER ARR, CASING, COVER, BOLT | 20 | 40 | 9.38 |  | N733AP35072 | 9.38 | 375.2
12 | G07011A |  | BOLT | CHAMBER ARR, FLAME DTCTR, MNTNG BLT | 3 | 4 | 18.28 |  | N733AP33028 | 18.28 | 73.12
13 | G07012Y |  | BOLT | CHAMBER ARR, CROSSFIRE TUBE, BOLT | 3 | 120 | 40.69 |  | N733AP29020 | 40.69 | 4882.8
14 | G070174 |  | RING PKG | CHAMBER ARR, XFIRE ASSY,PKG RNG | 8 | 40 | 24.02 |  | 287A1614P001 | 24.02 | 960.8
15 | G07019V |  | WASHER | CHAMBER ARR, XFIRE TUBE FLNG,WASHER | 5 | 4 | 44.58 |  | 239B9456P001 | 44.58 | 178.32
16 | G0701AA |  | BOLT | CHAMBER ARR, CVR-ORIENT LOCTR,BOLT | 14 | 8 | 10.93 |  | N733AP35044 | 10.93 | 87.44
17 | G0701G4 |  | WASHER | CHAMBER ARR, SPARK PLUG,WASHER | 6 | 16 | 0.95 |  | N402P00017 | 0.95 | 15.2
18 | G0701G5 |  | WASHER | CHAMBER ARR, FLAME DET MTG, WASHER | 6 | 16 | 0.95 |  | N402P00017 | 0.95 | 15.2
19 | G071714 |  | PIN | TRNS PC ARR, AFT MNT LOCATOR PIN | 4 | 10 | 26.44 |  | 219B6731P001 | 26.44 | 264.4
20 | G071717 |  | SEAL | TRNS PC ARR, AFT SEAL, END SEAL | 15 | 10 | 126 |  | 197C3155G002 | 126 | 1260
21 | G07171A |  | RETAINER | TRNS PC ARR, AFT SEAL RETAINER | 6 | 10 | 51.03 |  | 315A4045G001 | 51.03 | 510.3
22 | G07172D |  | BOLT | TRNS PC ARR, KIT - COMPONENT | 3 | 16 | 24.74 |  | 186C1916P022 | 24.74 | 395.84
23 | G07172D |  | BOLT | TRNS PC ARR, KIT - COMPONENT | 20 | 16 | 29.69 |  | 186C1916P034 | 29.69 | 475.04
24 | G07172D |  | BOLT | TRNS PC ARR, KIT - COMPONENT | 3 | 8 | 16.94 |  | 186C1916P013 | 16.94 | 135.52
25 | G07172D |  | BOLT | TRNS PC ARR, KIT - COMPONENT | 3 | 20 | 50.54 |  | 219B6733P003 | 50.54 | 1010.8
26 | G07172D |  | BOLT | TRNS PC ARR, KIT - COMPONENT | 3 | 10 | 15.26 |  | 293A0910P006 | 15.26 | 152.6
27 | G07172D |  | PLATE-LOCK | TRNS PC ARR, KIT - COMPONENT | 6 | 10 | 13.97 |  | 224B9719P001 | 13.97 | 139.7
28 | G07172D |  | PLATE-LOCK | TRNS PC ARR, KIT - COMPONENT | 4 | 10 | 7.62 |  | 224B9719P002 | 7.62 | 76.2
29 | G07172D |  | PLATE-LOCK | TRNS PC ARR, KIT - COMPONENT | 4 | 8 | 2.76 |  | 258A4784P013 | 2.76 | 22.08
30 | G07172D |  | PLATE-LOCK | TRNS PC ARR, KIT - COMPONENT | 4 | 4 | 2.48 |  | 258A4784P015 | 2.48 | 9.92
31 | G07172D |  | PLATE-LOCK | TRNS PC ARR, KIT - COMPONENT | 4 | 10 | 2.57 |  | 294A0151P022 | 2.57 | 25.7
32 | G07190G | 2 | GASKET | CASE ARR, COMB-OTR, GSKT ELONGATED | 6 | 1 | 26.86 |  | 318A9711P001 | 26.86 | 26.86
33 | G07190G | 4 | GASKET | CASE ARR, COMB-OTR, GSKT ELONGATED | 6 | 1 | 26.86 |  | 318A9711P001 | 26.86 | 26.86
34 | G07190G | 7 | GASKET | CASE ARR, COMB-OTR, GSKT ELONGATED | 6 | 1 | 26.86 |  | 318A9711P001 | 26.86 | 26.86
35 | G07190G | 9 | GASKET | CASE ARR, COMB-OTR, GSKT ELONGATED | 6 | 1 | 26.86 |  | 318A9711P001 | 26.86 | 26.86
36 | G07191J |  | BOLT | CASE ARR, COMB-OTR, BOLT, AFT MOUNT | 20 | 34 | 28.28 |  | N733AP33044 | 28.28 | 961.52
37 | G07191M | 1 | GASKET | CASE ARR, COMB-OTR, GASKET-AFT | 8 | 1 | 17.37 |  | 318A9713P019 | 17.37 | 17.37
38 | G07191M | 3 | GASKET | CASE ARR, COMB-OTR, GASKET-AFT | 8 | 1 | 17.37 |  | 318A9713P019 | 17.37 | 17.37
39 | G07191M | 5 | GASKET | CASE ARR, COMB-OTR, GASKET-AFT | 8 | 1 | 17.37 |  | 318A9713P019 | 17.37 | 17.37
40 | G07191M | 6 | GASKET | CASE ARR, COMB-OTR, GASKET-AFT | 8 | 1 | 17.37 |  | 318A9713P019 | 17.37 | 17.37
41 | G07191M | 8 | GASKET | CASE ARR, COMB-OTR, GASKET-AFT | 8 | 1 | 17.37 |  | 318A9713P019 | 17.37 | 17.37
42 | G07191M | 10 | GASKET | CASE ARR, COMB-OTR, GASKET-AFT | 8 | 1 | 17.37 |  | 318A9713P019 | 17.37 | 17.37
43 | G09242D | UB34 | GASKET | PP AR, AIR EXTR, MANIFOLD | 3 | 4 | 16.44 |  | 302A4594P037 | 16.44 | 65.76
44 | G09242J | UB34 | GASKET | PP AR, AIR EXTR, PIGTAIL | 3 | 25 | 4.14 |  | 302A4594P065 | 4.14 | 103.5
45 | G09242P | UB34 | BOLT | PP AR, AIR EXTR, BOLT, MNFLD FLNG | 9 | 10 | 5.24 |  | N14P37076 | 5.24 | 52.4
46 | G09242Y | UB34 | BOLT | PP AR, AIR EXTR, BOLT, PIGTAIL | 6 | 26 | 1.26 |  | N14P35064 | 1.26 | 32.76
47 | G09243A | UB34 | NUT-LOCK | PP, AIR EXTR, NUT-SLFLKG, PGTL | 3 | 41 | 3.05 |  | N265BP00035 | 3.05 | 125.05
48 | G09246562 | UB34 | NUT-LOCK | PP, AIR EXTR, NUT, SELF-LOCKING | 3 | 48 | 2.21 |  | N265BP00037 | 2.21 | 106.08
49 | G09621Y | LB50 | BOLT | PP ARR, GAS TRBN, BOLT, GAS SUPPLY | 6 | 6 | 1.26 |  | N14P35064 | 1.26 | 7.56
50 | G09622P | LB50 | BOLT | PP ARR, GAS TRBN, BOLT, SPPRT CHNL | 6 | 8 | 7.35 |  | N14P25016 | 7.35 | 58.8
51 | G09623307 | LB50 | STRIP-LOCK | PP ARR, GAS-TRBN, STRIP, LOCKING | 4 | 6 | 15.9 |  | 184A8790P019 | 15.9 | 95.4
52 | G09626050 | LB50 | BOLT | PP ARR, FUEL GAS, BOLT | 3 | 2 | 2.31 |  | N14P35060 | 2.31 | 4.62
53 | G096262 | UB34 | GASKET | PP ARR, GAS, PRM, PIGTAIL, GASKET | 3 | 20 | 4.6 |  | 302A4594P029 | 4.6 | 92
54 | G096267 | UB34 | BOLT | PP ARR, GAS, PRM MNFLD/NOZZ, BOLT | 6 | 32 | 4.73 |  | N14P33048 | 4.73 | 151.36
55 | G09626A | UB34 | NUT-LOCK | PP ARR, GAS, PRM MNFLD/NOZZ, NUT-LK | 3 | 32 | 1.05 |  | N265BP00033 | 1.05 | 33.6
56 | G09626G | LB50 | GASKET | PP ARR, GAS, PRM MNFLD, GASKET | 3 | 2 | 6.89 |  | 302A4594P033 | 6.89 | 13.78
57 | G09626J | LB50 | BOLT | PP ARR, GAS, PRM MNFLD, BOLT | 6 | 4 | 1.26 |  | N14P35064 | 1.26 | 5.04
58 | G09626M | LB50 | NUT-LOCK | PP ARR, GAS, PRM MNFLD, NUT-LOCK | 3 | 5 | 3.05 |  | N265BP00035 | 3.05 | 15.25
59 | G09626S | LB50 | GASKET | PP ARR, GAS, PRM SUPPLY, GASKET | 3 | 2 | 11.39 |  | 302A4594P035 | 11.39 | 22.78
60 | G09626V | LB50 | BOLT | PP ARR, GAS, PRM SUPPLY, BOLT | 6 | 4 | 1.05 |  | N14P35072 | 1.05 | 4.2
61 | G09626Y | LB50 | NUT-LOCK | PP ARR, GAS, PRM SUPPLY, NUT-LOCK | 3 | 2 | 3.05 |  | N265BP00035 | 3.05 | 6.1
62 | G096274 | UB34 | GASKET | PP ARR, GAS, SCN MNFLD/NOZZ, GASKET | 3 | 20 | 3.31 |  | 302A4594P061 | 3.31 | 66.2
63 | G096277 | UB34 | BOLT | PP ARR, GAS, SCN MNFLD/NOZZ, BOLT | 6 | 16 | 1.4 |  | N14P33044 | 1.4 | 22.4
64 | G096278 | UB34 | NUT-LOCK | PP ARR, GAS, SCN, PIGTAIL, NUT-LOCK | 3 | 16 | 1.05 |  | N265BP00033 | 1.05 | 16.8
65 | G09627G | LB50 | GASKET | PP ARR, GAS, SCN MNFLD, GASKET | 3 | 4 | 10.02 |  | 302A4594P032 | 10.02 | 40.08
66 | G09627J | LB50 | BOLT | PP ARR, GAS, SCN MNFLD, BOLT | 3 | 5 | 2.31 |  | N14P35060 | 2.31 | 11.55
67 | G09627M | LB50 | NUT-LOCK | PP ARR, GAS, SCN MNFLD, NUT-LOCK | 3 | 8 | 3.05 |  | N265BP00035 | 3.05 | 24.4
68 | G09627S | LB50 | GASKET | PP ARR, GAS, SCN SUPPLY, GASKET | 3 | 1 | 10.02 |  | 302A4594P032 | 10.02 | 10.02
69 | G09627V | LB50 | BOLT | PP ARR, GAS, SCN SUPPLY, BOLT | 6 | 4 | 1.26 |  | N14P35064 | 1.26 | 5.04
70 | G096284 | UB34 | GASKET | PP ARR, GAS, TRN MNFLD/NOZZ, GASKET | 3 | 20 | 3.31 |  | 302A4594P061 | 3.31 | 66.2
71 | G096287 | UB34 | BOLT | PP ARR, GAS, TRN MNFLD/NOZZ, BOLT | 6 | 16 | 1.4 |  | N14P33044 | 1.4 | 22.4
72 | G096288 | UB34 | BOLT | PP ARR, GAS, TRN, PGTL/NOZZ, BOLT | 3 | 16 | 1.05 |  | N265BP00033 | 1.05 | 16.8
73 | G09628G | LB50 | GASKET | PP ARR, GAS, TRN MNFLD, GASKET | 3 | 4 | 10.02 |  | 302A4594P032 | 10.02 | 40.08
74 | G09628J | LB50 | BOLT | PP ARR, GAS, TRN MNFLD, BOLT | 3 | 7 | 2.31 |  | N14P35060 | 2.31 | 16.17
75 | G09628M | LB50 | NUT-LOCK | PP ARR, GAS, TRN MNFLD, NUT-LOCK | 3 | 8 | 3.05 |  | N265BP00035 | 3.05 | 24.4
76 | G09628S | LB50 | GASKET | PP ARR, GAS, TRN SUPPLY, GASKET | 3 | 1 | 10.02 |  | 302A4594P032 | 10.02 | 10.02
77 | G09628V | LB50 | BOLT | PP ARR, GAS, TRN SUPPLY, BOLT | 6 | 4 | 1.26 |  | N14P35064 | 1.26 | 5.04
78 | G11210A |  | BOLT | DTCTR, FLME (28FD), BOLT, MNTNG | 6 | 16 | 6.83 |  | N14TP29022 | 6.83 | 109.28
79 | G121431 |  | IGNITER | SPRK PLG, BALL JOINT, IGNITER | 18 | 2 | 589.26 |  | 356A3217P001 | 589.26 | 1178.52
80 | G121437 |  | ASSEMBLY | SPRK PLG, BALL JOINT, SLV&BALL ASM | 9 | 1 | 433.49 |  | 207C3512G003 | 433.49 | 433.49
81 | G12143G |  | RING-PACKING | SPRK PLG, BALL JOINT, RING, PACKING | 6 | 4 | 21.13 |  | 324A9179P001 | 21.13 | 84.52
82 | G12143J |  | GASKET | SPRK PLG, BALL JOINT, GASKET | 6 | 2 | 4.6 |  | 318A9713P038 | 4.6 | 9.2
83 | G12143M |  | BOLT | SPRK PLG, BALL JOINT, BOLT 12PT | 14 | 2 | 18.99 |  | N733AP33040 | 18.99 | 37.98

## HGP Inspection
[7 empty] | List Total: |  |  |  | List Total: | Credit Total
[7 empty] | 2664.01 |  |  |  | 11996 | 0
GT Hot Gas Path Inspection
LINE | CATALOG | CAT | [6 empty] | SIMILAR-TO | UNIT
ITEM | NUMBER | LOC | PART NAME | PART DESCRIPTION | CYC | QTY | SYS PRICE | UM | DWG NUMBER | PRICE | LINE PRICE
____________
1 | G07055D |  | INSERT | CASE ARR,TURB, INST-VT CL FWD OUTSD | 4 | 4 | 6.56 |  | N926CP00335H2 | 6.56 | 26.24
2 | G07055S |  | STUD-BB | CASE ARR,TURB, HRZ JNT-BB STUD | 10 | 1 | 70.56 |  | 156A1591P018 | 70.56 | 70.56
3 | G070561 |  | BOLT | CASE ARR,TURB, HRZ JNT-BOLT | 14 | 4 | 147.32 |  | N733AP50158 | 147.32 | 589.28
4 | G070564 |  | BOLT | CASE ARR,TURB, HRZ JNT-BOLT | 6 | 2 | 33.7 |  | N733AP50096 | 33.7 | 67.4
5 | G07056G |  | NUT | CASE ARR,TURB, HRZ JNT-COVERED NUT | 10 | 2 | 78.12 |  | 114A8032P003 | 78.12 | 156.24
6 | G07056J |  | NUT-LOCK | CASE ARR,TURB, HRZ JNT-LOCK NUT | 6 | 4 | 10.5 |  | N272QP00050 | 10.5 | 42
7 | G09090G | UB26 | GASKET | PP ARR C&SA, GSKT, BRNG SLNG PIPING | 3 | 3 | 6.15 |  | 302A4594P009 | 6.15 | 18.45
8 | G09090S | UB26 | BOLT | PP ARR C&SA, BLT, BRG SLG PIPEFLNG | 3 | 3 | 1.42 |  | N14P33052 | 1.42 | 4.26
9 | G09091A | UB26 | BOLT | PP ARR C&SA, BLT, AE11 CSNG FLNG | 10 | 7 | 0.84 |  | N14P35036 | 0.84 | 5.88
10 | G09092P | UB26 | GASKET | PP ARR C&SA, GSKT, AE11 CSNG FLNG | 3 | 4 | 12.86 |  | 302A4594P014 | 12.86 | 51.44
11 | G09093325 | SUMM | PLATE-LOCK | PP ARR C&SA, PLATE,LOCKING,NUT&BOLT | 9 | 8 | 1.13 |  | 294A0150P006 | 1.13 | 9.04
12 | G09093325 | UB26 | PLATE-LOCK | PP ARR C&SA, PLATE,LOCKING,NUT&BOLT | 9 | 32 | 1.13 |  | 294A0150P006 | 1.13 | 36.16
13 | G09093325 | UB33 | PLATE-LOCK | PP ARR C&SA, PLATE,LOCKING,NUT&BOLT | 9 | 8 | 1.13 |  | 294A0150P006 | 1.13 | 9.04
14 | G09093413 | SUMM | GASKET | PP ARR C&SA, GASKET,SPIRAL-WOUND | 3 | 4 | 5.24 |  | 302A4594P007 | 5.24 | 20.96
15 | G09093413 | UB26 | GASKET | PP ARR C&SA, GASKET,SPIRAL-WOUND | 3 | 7 | 5.24 |  | 302A4594P007 | 5.24 | 36.68
16 | G09093413 | UB33 | GASKET | PP ARR C&SA, GASKET,SPIRAL-WOUND | 3 | 4 | 5.24 |  | 302A4594P007 | 5.24 | 20.96
17 | G09093414 | SUMM | GASKET | PP ARR C&SA, GASKET,SPIRAL-WOUND | 3 | 24 | 6.15 |  | 302A4594P009 | 6.15 | 147.6
18 | G09093414 | UB26 | GASKET | PP ARR C&SA, GASKET,SPIRAL-WOUND | 3 | 3 | 6.15 |  | 302A4594P009 | 6.15 | 18.45
19 | G09093414 | UB33 | GASKET | PP ARR C&SA, GASKET,SPIRAL-WOUND | 3 | 18 | 6.15 |  | 302A4594P009 | 6.15 | 110.7
20 | G09093415 | SUMM | GASKET | PP ARR C&SA, GASKET,SPIRAL-WOUND | 3 | 2 | 7.72 |  | 302A4594P011 | 7.72 | 15.44
21 | G09093415 | UB33 | GASKET | PP ARR C&SA, GASKET,SPIRAL-WOUND | 3 | 2 | 7.72 |  | 302A4594P011 | 7.72 | 15.44
22 | G09093416 | MSDM | GASKET | PP ARR C&SA, GASKET,SPIRAL-WOUND | 3 | 2 | 9.09 |  | 302A4594P013 | 9.09 | 18.18
23 | G09093416 | SUMM | GASKET | PP ARR C&SA, GASKET,SPIRAL-WOUND | 3 | 5 | 9.09 |  | 302A4594P013 | 9.09 | 45.45
24 | G09093416 | UB33 | GASKET | PP ARR C&SA, GASKET,SPIRAL-WOUND | 3 | 3 | 9.09 |  | 302A4594P013 | 9.09 | 27.27
25 | G09093417 | UB26 | GASKET | PP ARR C&SA, GASKET,SPIRAL-WOUND | 3 | 10 | 12.86 |  | 302A4594P014 | 12.86 | 128.6
26 | G09093418 | SUMM | GASKET | PP ARR C&SA, GASKET,SPIRAL-WOUND | 3 | 1 | 13.97 |  | 302A4594P015 | 13.97 | 13.97
27 | G09093418 | UB33 | GASKET | PP ARR C&SA, GASKET,SPIRAL-WOUND | 3 | 1 | 13.97 |  | 302A4594P015 | 13.97 | 13.97
28 | G09094Y | UB26 | GASKET | PP ARR C&SA,GSKT,BFLY VLV AE11/SPCR | 3 | 10 | 13.97 |  | 302A4594P015 | 13.97 | 139.7
29 | G09096026 | SUMM | BOLT | PP ARR C&SA, BOLT,HEX HEAD | 6 | 5 | 0.53 |  | N14P33036 | 0.53 | 2.65
30 | G09096028 | SUMM | BOLT | PP ARR C&SA, BOLT,HEX HEAD | 6 | 3 | 1.4 |  | N14P33044 | 1.4 | 4.2
31 | G09096028 | UB26 | BOLT | PP ARR C&SA, BOLT,HEX HEAD | 6 | 3 | 1.4 |  | N14P33044 | 1.4 | 4.2
32 | G09096028 | UB33 | BOLT | PP ARR C&SA, BOLT,HEX HEAD | 6 | 3 | 1.4 |  | N14P33044 | 1.4 | 4.2
33 | G09096029 | UB26 | BOLT | PP ARR C&SA, BOLT,HEX HEAD | 6 | 2 | 4.73 |  | N14P33048 | 4.73 | 9.46
34 | G09096030 | SUMM | BOLT | PP ARR C&SA, BOLT,HEX HEAD | 3 | 9 | 1.42 |  | N14P33052 | 1.42 | 12.78
35 | G09096030 | UB26 | BOLT | PP ARR C&SA, BOLT,HEX HEAD | 3 | 3 | 1.42 |  | N14P33052 | 1.42 | 4.26
36 | G09096030 | UB33 | BOLT | PP ARR C&SA, BOLT,HEX HEAD | 3 | 9 | 1.42 |  | N14P33052 | 1.42 | 12.78
37 | G09096031 | SUMM | BOLT | PP ARR C&SA, BOLT,HEX HEAD | 3 | 2 | 2.21 |  | N14P33056 | 2.21 | 4.42
38 | G09096031 | UB33 | BOLT | PP ARR C&SA, BOLT,HEX HEAD | 3 | 2 | 2.21 |  | N14P33056 | 2.21 | 4.42
39 | G09096032 | SUMM | BOLT | PP ARR C&SA, BOLT,HEX HEAD | 6 | 1 | 0.63 |  | N14P33072 | 0.63 | 0.63
40 | G09096032 | UB33 | BOLT | PP ARR C&SA, BOLT,HEX HEAD | 6 | 1 | 0.63 |  | N14P33072 | 0.63 | 0.63
41 | G09096033 | SUMM | BOLT | PP ARR C&SA, BOLT,HEX HEAD | 3 | 1 | 2.68 |  | N14P33088 | 2.68 | 2.68
42 | G09096033 | UB33 | BOLT | PP ARR C&SA, BOLT,HEX HEAD | 3 | 1 | 2.68 |  | N14P33088 | 2.68 | 2.68
43 | G09096048 | MSDM | BOLT | PP ARR C&SA, BOLT,HEX HEAD | 3 | 4 | 2.68 |  | N14P35052 | 2.68 | 10.72
44 | G09096048 | SUMM | BOLT | PP ARR C&SA, BOLT,HEX HEAD | 3 | 5 | 2.68 |  | N14P35052 | 2.68 | 13.4
45 | G09096048 | UB33 | BOLT | PP ARR C&SA, BOLT,HEX HEAD | 3 | 2 | 2.68 |  | N14P35052 | 2.68 | 5.36
46 | G09096049 | SUMM | BOLT | PP ARR C&SA, BOLT,HEX HEAD | 6 | 4 | 4.11 |  | N14P35056 | 4.11 | 16.44
47 | G09096049 | UB33 | BOLT | PP ARR C&SA, BOLT,HEX HEAD | 6 | 4 | 4.11 |  | N14P35056 | 4.11 | 16.44
48 | G09096101 | UB26 | BOLT | PP ARR C&SA, BOLT,HEX HEAD | 6 | 1 | 1.89 |  | N22P21008 | 1.89 | 1.89
49 | G09096556 | SUMM | NUT-LOCK | PP ARR C&SA, NUT,SELF-LOCKING | 3 | 2 | 2.21 |  | N265BP00025 | 2.21 | 4.42
50 | G09096556 | UA40 | NUT-LOCK | PP ARR C&SA, NUT,SELF-LOCKING | 3 | 1 | 2.21 |  | N265BP00025 | 2.21 | 2.21
51 | G09096556 | UB26 | NUT-LOCK | PP ARR C&SA, NUT,SELF-LOCKING | 3 | 1 | 2.21 |  | N265BP00025 | 2.21 | 2.21
52 | G09096557 | MSDM | NUT-LOCK | PP ARR C&SA, NUT,SELF-LOCKING | 3 | 1 | 6.62 |  | N265BP00029 | 6.62 | 6.62
53 | G09096557 | SUMM | NUT-LOCK | PP ARR C&SA, NUT,SELF-LOCKING | 3 | 2 | 6.62 |  | N265BP00029 | 6.62 | 13.24
54 | G09096557 | UB26 | NUT-LOCK | PP ARR C&SA, NUT,SELF-LOCKING | 3 | 1 | 6.62 |  | N265BP00029 | 6.62 | 6.62
55 | G09096558 | SUMM | NUT-LOCK | PP ARR C&SA, NUT,SELF-LOCKING | 3 | 15 | 1.05 |  | N265BP00033 | 1.05 | 15.75
56 | G09096558 | UB26 | NUT-LOCK | PP ARR C&SA, NUT,SELF-LOCKING | 3 | 8 | 1.05 |  | N265BP00033 | 1.05 | 8.4
57 | G09096558 | UB33 | NUT-LOCK | PP ARR C&SA, NUT,SELF-LOCKING | 3 | 15 | 1.05 |  | N265BP00033 | 1.05 | 15.75
58 | G09096559 | MSDM | NUT-LOCK | PP ARR C&SA, NUT,SELF-LOCKING | 3 | 4 | 3.05 |  | N265BP00035 | 3.05 | 12.2
59 | G09096559 | SUMM | NUT-LOCK | PP ARR C&SA, NUT,SELF-LOCKING | 3 | 7 | 3.05 |  | N265BP00035 | 3.05 | 21.35
60 | G09096559 | UB26 | NUT-LOCK | PP ARR C&SA, NUT,SELF-LOCKING | 3 | 7 | 3.05 |  | N265BP00035 | 3.05 | 21.35
61 | G09096559 | UB33 | NUT-LOCK | PP ARR C&SA, NUT,SELF-LOCKING | 3 | 4 | 3.05 |  | N265BP00035 | 3.05 | 12.2
62 | G14011D |  | BOLT | NOZZ 1ST-STG, ECCENT RET PIN - BOLT | 9 | 1 | 9.87 |  | N14TP35036 | 9.87 | 9.87
63 | G14011G |  | BOLT | NOZZ 1ST-STG, HOR HLD DWN CLMP BOLT | 9 | 1 | 56.7 |  | N14TP39112 | 56.7 | 56.7
64 | G14011M |  | PLATE-LOCK | NOZZ 1ST-STG, ECCENT RET PIN LKPL | 9 | 4 | 1.13 |  | 294A0150P006 | 1.13 | 4.52
65 | G14014G |  | BOLT | NOZZ 1ST-STG, RTNG RING BOLT | 11 | 1 | 228.22 |  | N733CP39052 | 228.22 | 228.22
66 | G14014J | 1 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 14 | 1 | 11.21 |  | N926CP00325H2 | 11.21 | 11.21
67 | G14014J | 2 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
68 | G14014J | 3 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
69 | G14014J | 4 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
70 | G14014J | 5 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 14 | 1 | 11.21 |  | N926CP00325H2 | 11.21 | 11.21
71 | G14014J | 6 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
72 | G14014J | 7 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
73 | G14014J | 8 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
74 | G14014J | 9 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 14 | 1 | 11.21 |  | N926CP00325H2 | 11.21 | 11.21
75 | G14014J | 10 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
76 | G14014J | 11 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
77 | G14014J | 12 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
78 | G14014J | 13 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 14 | 1 | 11.21 |  | N926CP00325H2 | 11.21 | 11.21
79 | G14014J | 14 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
80 | G14014J | 15 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
81 | G14014J | 16 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
82 | G14014J | 17 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 14 | 1 | 11.21 |  | N926CP00325H2 | 11.21 | 11.21
83 | G14014J | 18 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
84 | G14014J | 19 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
85 | G14014J | 20 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
86 | G14014J | 21 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 14 | 1 | 11.21 |  | N926CP00325H2 | 11.21 | 11.21
87 | G14014J | 22 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
88 | G14014J | 23 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
89 | G14014J | 24 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
90 | G14014J | 25 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 14 | 1 | 11.21 |  | N926CP00325H2 | 11.21 | 11.21
91 | G14014J | 26 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
92 | G14014J | 27 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
93 | G14014J | 28 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
94 | G14014J | 29 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 14 | 1 | 11.21 |  | N926CP00325H2 | 11.21 | 11.21
95 | G14014J | 30 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
96 | G14014J | 31 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
97 | G14014J | 32 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
98 | G14014J | 33 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 14 | 1 | 11.21 |  | N926CP00325H2 | 11.21 | 11.21
99 | G14014J | 34 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
100 | G14014J | 35 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
101 | G14014J | 36 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
102 | G14014J | 37 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 14 | 1 | 11.21 |  | N926CP00325H2 | 11.21 | 11.21
103 | G14014J | 38 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
104 | G14014J | 39 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
105 | G14014J | 40 | INSERT | NOZZ 1ST-STG, RTG RNG WIR-LK INSERT | 12 | 1 | 11.76 |  | N926CP00333H2 | 11.76 | 11.76
106 | G14014M |  | INSERT | NOZZ 1ST-STG, RTG RG WIR-LK BLT INS | 14 | 1 | 14.32 |  | N926CP00339H2 | 14.32 | 14.32
107 | G14020M |  | PLATE-LOCK | NOZZ 2ND STG, NOZ RET PN PLT LKPL | 4 | 2 | 0.95 |  | 294A0150P004 | 0.95 | 1.9
108 | G14021S |  | BOLT | NOZZ 2ND STG, NOZ RET PIN PLT BLT | 6 | 2 | 6.83 |  | N14TP29022 | 6.83 | 13.66
109 | G14030D |  | BOLT | SPPRT RNG, 1ST-STG, RNG MNT BOLT | 5 | 5 | 21.9 |  | N733AP39058 | 21.9 | 109.5
110 | G14030G |  | SCREW | SPPRT RNG, 1ST-STG, SHIM SCREW | 4 | 4 | 5.15 |  | N646P25016 | 5.15 | 20.6
111 | G140311 |  | INSERT | SPPRT RNG, 1ST-STG, INSERT | 14 | 24 | 14.32 |  | N926CP00339H2 | 14.32 | 343.68
112 | G16040J | UA10 | BOLT | B & D ARR, BLT, DSCH CASE/COMB WRPR | 14 | 23 | 9.38 |  | N733AP35048 | 9.38 | 215.74
113 | G16040V | UA10 | BOLT | B & D ARR, BLT, CMP DSCH/TURB SHELL | 14 | 4 | 70.56 |  | N733AP52096 | 70.56 | 282.24
114 | G16040Y | UA10 | BOLT | B & D ARR,BLT,CMB WRPR/TB SHELL-INR | 5 | 16 | 15.03 |  | N733AP39080 | 15.03 | 240.48
115 | G160414 | UA10 | BOLT | B & D ARR, BLT, TURB SHELL/EXH FRM | 14 | 5 | 16.44 |  | N733AP39088 | 16.44 | 82.2
116 | G16045P | UA10 | BOLT | B&D ARR,BLT,CMB WRPR/TRB SHELL-OTR | 11 | 1 | 31.19 |  | N733AP39144 | 31.19 | 31.19
117 | G16046Y | UA10 | NUT | B & D ARR, NUT, TRB SHELL/EXH FRAME | 11 | 5 | 10.5 |  | N271TP00039 | 10.5 | 52.5
118 | G160517 |  | WASHER | ENCL TO BASE ARR,WSHR,RUBB-FLSH ENC | 6 | 2 | 0.63 |  | 235A6934P001 | 0.63 | 1.26
119 | G16051A |  | WASHER | ENCL TO BASE ARR,WSHR,PLN-FLSH ENC | 6 | 9 | 7.25 |  | N402P00043 | 7.25 | 65.25
120 | G16051D |  | BOLT | ENCL TO BASE ARR,BOLT-FLSH/ENC 3.5 | 6 | 2 | 0.21 |  | N22P25056 | 0.21 | 0.42
121 | G16052J |  | GASKET | ENCL-BASE, GSKT,DRY ADHSV INL PLNM | 6 | 360 | 0.95 |  | 158A5453P002 | 0.95 | 342
122 | G16140D | UB34 | GASKET | ENCL ASM,CMPT,GSKT,FLSH-FBGL BLB | 8 | 20 | 13.42 |  | 298A8961P001 | 13.42 | 268.4
123 | G16140P | UB34 | BOLT | ENCL ASM,CMPT,BOLT,INLT PLNM/SDE FR | 6 | 9 | 0.84 |  | N14P29032 | 0.84 | 7.56
124 | G16140Y | UB34 | BOLT | ENCL ASM,CMPT,BOLT,ROOF COV/FRAME | 9 | 3 | 0.47 |  | N14P29012 | 0.47 | 1.41
125 | G16141A | UB34 | WASHER | ENCL ASM,CMPT,WSHR, INLT PLN/TB CMP | 6 | 9 | 0.32 |  | N402P00045 | 0.32 | 2.88
126 | G16141Y | UB34 | NUT | ENCL ASM,CMPT,INLT PLNM NUT | 6 | 9 | 7.25 |  | N214P00029 | 7.25 | 65.25
127 | G16146001 | UB34 | BOLT | ENCL ASM,CMPT,BOLT, HEX HEAD | 9 | 3 | 0.47 |  | N14P29012 | 0.47 | 1.41
128 | G16146503 | UB34 | NUT | ENCL ASM,CMPT,NUT, HEX | 6 | 3 | 7.35 |  | N203P00029 | 7.35 | 22.05
129 | G162501 | UB20 | BOLT | PLNM ASM EX, BOLT, EXP JNT SEG-FWD | 11 | 40 | 58.83 |  | 293A0911P007 | 58.83 | 2353.2
130 | G162504 | UB20 | EXPANSION-JT | PLNM ASM EX, EXP JNT SEGMENT-FWD | 9 | 20 | 68.04 |  | 239A5100P002 | 68.04 | 1360.8
131 | G162507 | UB20 | GASKET | PLNM ASM EX, GSKT, EXP JNT SEG-FWD | 9 | 1 | 245.12 |  | 239A5101P002 | 245.12 | 245.12
132 | G16250A | UB20 | BOLT | PLNM ASM EX, BOLT, EXP JNT SEG-AFT | 6 | 40 | 5.15 |  | N14P29028 | 5.15 | 206
133 | G16250G | UB20 | EXPANSION-JT | PLNM ASM EX, EXP JNT FLX PL SEG-AFT | 9 | 20 | 46.7 |  | 192B3816P001 | 46.7 | 934
134 | G16250J | UB20 | GASKET | PLNM ASM EX, GSKT, FLX PL SEG-AFT | 9 | 4 | 123.48 |  | 192B3815P001 | 123.48 | 493.92
135 | G16250P | UB20 | GASKET | PLNM ASM EX,GSKT,C/L HORIZ JNT | 10 | 4 | 253.58 |  | 287A7192P001 | 253.58 | 1014.32
136 | G16251H | UB20 | GASKET | PLNM ASM EX, GSKT, CL TRNVRS JT | 10 | 1 | 253.58 |  | 287A7192P001 | 253.58 | 253.58
137 | G16251N | UB20 | BOLT | PLNM ASM EX, BOLT, CL TRNSVRS JT | 9 | 3 | 2.11 |  | N14P35038 | 2.11 | 6.33
138 | G16256559 | UB20 | NUT | PLNM ASM EX, NUT, CL TRNSVRS JT | 3 | 14 | 3.05 |  | N265BP00035 | 3.05 | 42.7

## Major Inspection
[7 empty] | List Total: |  |  |  | List Total: | Credit Total
[7 empty] | 91507.96 |  |  |  | 122136.42 | 0
GT Major Inspection
LINE | CATALOG | CAT | [6 empty] | SIMILAR-TO | UNIT
ITEM | NUMBER | LOC | PART NAME | PART DESCRIPTION | CYC | QTY | SYS PRICE | UM | DWG NUMBER | PRICE | LINE PRICE
____________
1 | G07050V |  | KEY | CASE ARR,TURB, STG 1 SHRD KEY,HZ JT | 18 | 2 | 116.55 |  | 172C9091P001 | 116.55 | 233.1
2 | G07050Y |  | KEY | CASE ARR,TURB, STG 1 SHROUD KEY | 18 | 46 | 66.15 |  | 172C9090P001 | 66.15 | 3042.9
3 | G070511 |  | KEY | CASE ARR,TURB, STG 2 SHRD KEY,HZ JT | 18 | 2 | 90.72 |  | 172C9091P004 | 90.72 | 181.44
4 | G070514 |  | KEY | CASE ARR,TURB, STG 2 SHROUD KEY | 18 | 46 | 65.07 |  | 172C9090P004 | 65.07 | 2993.22
5 | G070517 |  | KEY | CASE ARR,TURB, STG 3 SHRD KEY,HZ JT | 18 | 2 | 119.7 |  | 172C9091P003 | 119.7 | 239.4
6 | G07051A |  | KEY | CASE ARR,TURB, STG 3 SHROUD KEY | 18 | 30 | 65.07 |  | 172C9090P003 | 65.07 | 1952.1
7 | G070602 | UA10 | TOOTH-SEAL | FAB&MACH EX FR,TOOTH,VRTCL STATONRY | 6 | 33 | 12.68 |  | 302A1607P001 | 12.68 | 418.44
8 | G070603 | UA10 | TOOTH-SEAL | FAB&MACH EX FR,TOOTH,HORIZ STATONRY | 6 | 34 | 10.11 |  | 302A1606P001 | 10.11 | 343.74
9 | G070607 | UA10 | BOLT | FRAME EXHST ASMBLY, 12PT HEAD BOLT | 20 | 3 | 33.88 |  | N733BP44064 | 33.88 | 101.64
10 | G07060A | UA10 | BOLT | FRAME EXHST ASMBLY, HEX HEAD BOLT | 14 | 2 | 125.58 |  | N733BP44080 | 125.58 | 251.16
11 | G07060D | UA10 | NUT | FRAME EXHST ASMBLY, SELF LCKNG NUT | 11 | 10 | 17.54 |  | N271TP00044 | 17.54 | 175.4
12 | G07060G | UA10 | STUD | FRAME EXHST ASMBLY, BODY BOUND STUD | 10 | 1 | 75.6 |  | 156A1591P016 | 75.6 | 75.6
13 | G07060P | UA10 | BOLT | FR EX ASM,BLT,DIFF ASM/EX DIF INRNG | 3 | 4 | 16.16 |  | N733AP33064 | 16.16 | 64.64
14 | G07064V | UA10 | NUT | EXHST FRM ASM,HOOD FRM BAFFLE,NUT | 6 | 1 | 41.11 |  | 244A0139P005 | 41.11 | 41.11
15 | G07065A | UA10 | WASHER | EXHST FRM ASM,UPPER BAFFLE,WASHER | 6 | 12 | 7.25 |  | N402P00043 | 7.25 | 87
16 | G07065G | UA10 | WASHER | EXHST FRM,INSULATION COVER,WSH | 10 | 36 | 15.59 |  | 322B4360P001 | 15.59 | 561.24
17 | G07065J | UA10 | BOLT | EXHST FRM,INSULATION COVER,BOLT | 8 | 8 | 9.38 |  | 114A5500P015 | 9.38 | 75.04
18 | G07066G | UA10 | INSERT | EXHST FRM, INSERT OUTER CASING | 14 | 52 | 16.36 |  | N926AP00233H2 | 16.36 | 850.72
19 | G070671 | UA10 | BOLT | FRAME EXHST ASMBLY,RET OTR FLNG BLT | 14 | 11 | 35.93 |  | N733DP33020 | 35.93 | 395.23
20 | G070677 | UA10 | NUT | FRAME EXHST ASMBLY,RET OTR FLNG NUT | 11 | 4 | 9.87 |  | N272QP00033 | 9.87 | 39.48
21 | G07067A | UA10 | PLATE-LOCK | FRAME EXHST ASM,RET OTR FLNG LK-PLT | 6 | 8 | 27.71 |  | 294A0151P015 | 27.71 | 221.68
22 | G07067M | UA10 | PLATE-LOCK | FRM EXHST ASM,INSLTN PCK CVR,LK-PLT | 6 | 8 | 9.92 |  | 315A9175P001 | 9.92 | 79.36
23 | G07067P | UA10 | BOLT | FRM EXHST ASM,INSLTN PCK CVR,BLT | 9 | 3 | 46.49 |  | 293A0912P014 | 46.49 | 139.47
24 | G07067S | UA10 | BOLT | FR EXHST,OTR HRZNTL JT FLG THRU,BLT | 14 | 5 | 65.64 |  | N733BP44104 | 65.64 | 328.2
25 | G07067V | UA10 | BOLT | FR EXHST,INR HRZNTL JT FLG THRU,BLT | 14 | 4 | 53.87 |  | N733BP44088 | 53.87 | 215.48
26 | G07067Y | UA10 | BOLT | FR EXHST,INR DIFFUSER WALL,BLT | 11 | 6 | 15.03 |  | N733AP33032 | 15.03 | 90.18
27 | G070683 | UA10 | PLATE-LOCK | FR EXHST,INSLTN PCK HRZNTL,LK-PLATE | 9 | 12 | 27.71 |  | 294A0151P020 | 27.71 | 332.52
28 | G0706A8 | UA10 | PIN-DOWEL | FRM EXH, DIFFSR-INR HOR JNT DOWL | 9 | 6 | 193.2 |  | 239A5124P003 | 193.2 | 1159.2
29 | G071201 |  | BOLT | CASE,COMB-OUT WRPR, BOLT | 14 | 6 | 86.94 |  | N733AP50224 | 86.94 | 521.64
30 | G071204 |  | STUD-BB | CASE,COMB-OUT WRPR, STUD | 6 | 1 | 138.86 |  | 255A4485P002 | 138.86 | 138.86
31 | G071207 |  | NUT | CASE,COMB-OUT WRPR, NUT | 14 | 8 | 76.65 |  | N271TP00050 | 76.65 | 613.2
32 | G07120A |  | BOLT | CASE,COMB-OUT WRPR, BOLT | 14 | 2 | 47.06 |  | N733AP39216 | 47.06 | 94.12
33 | G07120D |  | NUT | CASE,COMB-OUT WRPR, NUT | 11 | 2 | 10.5 |  | N271TP00039 | 10.5 | 21
34 | G07120J |  | BOLT | CASE,COMB-OUT WRPR, PIPE FLNG BOLT | 3 | 80 | 2.31 |  | N14P35060 | 2.31 | 184.8
35 | G07120M |  | NUT-LOCK | CASE,COMB-OUT WRPR, NUT-LOCK PP FLG | 3 | 16 | 3.05 |  | N265BP00035 | 3.05 | 48.8
36 | G07120V |  | BOLT | CASE,CMB-OUT WRPR,BLT HOR CSNG FLG | 11 | 2 | 65.13 |  | N733AP50176 | 65.13 | 130.26
37 | G080104 |  | SEAL ASM | CASE-CPR INLT&1BRG,STAT OIL SEAL | 12 | 2 | 602.54 |  | 201B3363G001 | 602.54 | 1205.08
38 | G080107 |  | LINER | CASE-CPR INLT&1BRG,LINER ASSEMBLY | 14 | 1 | 6022.3 |  | 112E1679G001 | 6022.3 | 6022.3
39 | G08010D |  | DEFLECTOR | CASE-CPR INLT&1BRG,AIR DEFLECTOR | 8 | 1 | 1110.9 |  | 143B3045G003 | 1110.9 | 1110.9
40 | G08012A |  | SEAL | CASE-CPR INLT&1BRG,OIL SEAL - FWD | 9 | 1 | 1499.4 |  | 143B3026G006 | 1499.4 | 1499.4
41 | G08012P |  | PIN-LOCK | CASE-CPR INLT&1BRG,OIL SL LK PN,FWD | 11 | 1 | 35.72 |  | 211A9053P003 | 35.72 | 35.72
42 | G08013P |  | SEAL | CASE-CPR INLT&1BRG,OIL SEAL - AFT | 11 | 1 | 2716.56 |  | 138C9173G003 | 2716.56 | 2716.56
43 | G080201 |  | BOLT | CMP CASE-FWD, HOR JOINT BOLT | 3 | 2 | 18.64 |  | N733P39080 | 18.64 | 37.28
44 | G080204 |  | STUD | CMP CASE-FWD, HOR JOINT STUD | 9 | 2 | 135.24 |  | 156A1591P020 | 135.24 | 270.48
45 | G080207 |  | NUT | CMP CASE-FWD, HOR JOINT NUT | 11 | 6 | 10.5 |  | N271TP00039 | 10.5 | 63
46 | G08020G |  | BOLT | CMP CASE-FWD, HOR JOINT BOLT-AFT | 7 | 4 | 42.67 |  | N733P39128 | 42.67 | 170.68
47 | G080504 | UA10 | SCREW | CASE-CPRSR DISCH,DISCH CASE SCREW | 9 | 3 | 39.41 |  | N733AP44136 | 39.41 | 118.23
48 | G080507 | UA10 | SCREW | CASE-CPRSR DISCH,DISCH CASE SCREW | 11 | 2 | 43.38 |  | N733AP44072 | 43.38 | 86.76
49 | G08050D | UA10 | STUD-BB | CASE-CPRSR DISCH,DISCH CASE BB STUD | 8 | 1 | 126.79 |  | 156A1591P014 | 126.79 | 126.79
50 | G08050G | UA10 | STUD-BB | CASE-CPRSR DISCH,DISCH CASE BB STUD | 15 | 1 | 70.88 |  | 156A1591P015 | 70.88 | 70.88
51 | G08050M | UA10 | NUT | CASE-CPRSR DISCH,DISCH CASE NUT | 14 | 6 | 19.74 |  | N272QP00044 | 19.74 | 118.44
52 | G08050P | UA10 | INSERT | CASE-CPRSR DISCH,DISCH CASE INSERT | 11 | 24 | 35.23 |  | N926CP00344H2 | 35.23 | 845.52
53 | G08050Y | UA10 | SCREW | CASE-CPRSR DISCH,INNER CASE SCREW | 11 | 2 | 23.39 |  | N733AP39040 | 23.39 | 46.78
54 | G08051J | UA40 | SCREW | CASE-CPRSR DISCH,FLANGE SCREW | 6 | 2 | 7.25 |  | N170P35036 | 7.25 | 14.5
55 | G08051P | UA40 | GASKET | CASE-CPRSR DISCH,PIPE FLANGE GASKET | 6 | 1 | 18.78 |  | 328A6992P002 | 18.78 | 18.78
56 | G08051S | UA40 | BOLT | CASE-CPRSR DISCH,GLAND BOLT | 3 | 1 | 2.8 |  | N14P29024 | 2.8 | 2.8
57 | G08051V | UA50 | BOLT | CASE-CPRSR DISCH,VENT RING BOLT | 6 | 1 | 0.74 |  | N14P29020 | 0.74 | 0.74
58 | G08053P | UA50 | PLATE-LOCK | CASE-CPRSR DISCH,RING BOLT LKPLT | 4 | 4 | 0.95 |  | 294A0150P004 | 0.95 | 3.8
59 | G08054M | UA10 | BOLT | CASE-CPRSR DISCH,DISCH CASE BOLT | 9 | 4 | 28.14 |  | N14TP44060 | 28.14 | 112.56
60 | G08055D | UA10 | INSERT | CASE-CPRSR DISCH,DISCH CASE INSERT | 11 | 8 | 14.52 |  | N926AP00229H2 | 14.52 | 116.16
61 | G08055G | UA10 | INSERT | CASE-CPRSR DISCH,DISCH CASE INSERT | 11 | 1 | 3.31 |  | N926P00235 | 3.31 | 3.31
62 | G080587 | UA10 | INSERT | CSE CMP DSCH, CMB CHMBR FL INSRT | 4 | 1 | 6.56 |  | N926CP00335H2 | 6.56 | 6.56
63 | G08058A | UA10 | INSERT | CSE CMP DSCH, VERT FLANGE INSRT | 8 | 4 | 9.74 |  | N926AP00235H2 | 9.74 | 38.96
64 | G08058D | UA10 | BOLT | CSE CMP DSCH, CDC HARDWARE KIT - COMP | 11 | 8 | 23.39 |  | N733AP39040 | 23.39 | 187.12
65 | G08058D | UA10 | PIN-STRT HDLS | CSE CMP DSCH, CDC HARDWARE KIT - COMP | 8 | 2 | 29.2 |  | 158A5457P021 | 29.2 | 58.4
66 | G08058G | UA10 | INSERT | CSE CMP DSCH, INNR BBL HARDWARE KIT - COMP | 5 | 4 | 4.23 |  | N926BP00335 | 4.23 | 16.92
67 | G08058G | UA10 | PIN-DOWEL | CSE CMP DSCH, INNR BBL HARDWARE KIT - COMP | 10 | 4 | 16.44 |  | 158A5457P058 | 16.44 | 65.76
68 | G08058G | UA10 | SCREW | CSE CMP DSCH, INNR BBL HARDWARE KIT - COMP | 6 | 1 | 8.27 |  | N173P03516 | 8.27 | 8.27
69 | G08058G | UA10 | SCREW | CSE CMP DSCH, INNR BBL HARDWARE KIT - COMP | 5 | 4 | 6.44 |  | N733P35060 | 6.44 | 25.76
70 | G08058J | UA10 | BOLT | CSE CMP DSCH, CDC ASM HARDWARE KIT - COMP | 9 | 16 | 28.14 |  | 293A0905P012 | 28.14 | 450.24
71 | G08058J | UA10 | BOLT | CSE CMP DSCH, CDC ASM HARDWARE KIT - COMP | 9 | 1 | 94 |  | 293A0903P003 | 94 | 94
72 | G08058J | UA10 | INSERT | CSE CMP DSCH, CDC ASM HARDWARE KIT - COMP | 11 | 4 | 6.8 |  | N926CP00329H2 | 6.8 | 27.2
73 | G08058J | UA10 | KIT | CSE CMP DSCH, CDC ASM HARDWARE KIT | -1 | 1 | 0 |  | 344A9579G003 | 0 | NA
74 | G08058J | UA10 | PLATE-LOCK | CSE CMP DSCH, CDC ASM HARDWARE KIT - COMP | 9 | 1 | 1.13 |  | 294A0150P006 | 1.13 | 1.13
75 | G08058J | UA10 | PLUG-PIPE | CSE CMP DSCH, CDC ASM HARDWARE KIT - COMP | 9 | 2 | 22.83 |  | 302A1620P003 | 22.83 | 45.66
76 | G08058J | UA10 | PLUG-PIPE | CSE CMP DSCH, CDC ASM HARDWARE KIT - COMP | 6 | 4 | 51.39 |  | 302A1620P004 | 51.39 | 205.56
77 | G08058J | UA10 | PLUG-PIPE | CSE CMP DSCH, CDC ASM HARDWARE KIT - COMP | 5 | 6 | 2.21 |  | 286A6290P003 | 2.21 | 13.26
78 | G08058J | UA10 | SCREW | CSE CMP DSCH, CDC ASM HARDWARE KIT - COMP | 6 | 1 | 8.27 |  | N173P03516 | 8.27 | 8.27
79 | G08120A |  | NUT | CASE, INLET BRG #1, NUT | 6 | 4 | 7.25 |  | N204P00039 | 7.25 | 29
80 | G08120D |  | STUD | CASE, INLET BRG #1,BODY BOUND,STUD | 9 | 2 | 124.74 |  | 156A1591P013 | 124.74 | 249.48
81 | G08120J |  | BOLT | CASE, INLET BRG #1, BOLT | 8 | 8 | 118.44 |  | 239B5236P302 | 118.44 | 947.52
82 | G08120P |  | BOLT | CASE, INLET BRG #1, BOLT | 6 | 2 | 20.6 |  | N733P39112 | 20.6 | 41.2
83 | G08120S |  | INSERT | CASE, INLET BRG #1, INSERT | 11 | 6 | 5.97 |  | N926BP00339 | 5.97 | 35.82
84 | G08120V |  | BOLT | CASE, INLET BRG #1, BOLT | 11 | 1 | 38.77 |  | N733P50096 | 38.77 | 38.77
85 | G081217 |  | INSERT | CASE, INLET BRG #1, INSERT | 10 | 6 | 18.2 |  | N926BP00350 | 18.2 | 109.2
86 | G081270 |  | INSERT | CASE, INLET BRG #1, HARDWARE KIT - COMP | 11 | 12 | 2.03 |  | N926BP00421 | 2.03 | 24.36
87 | G081270 |  | INSERT | CASE, INLET BRG #1, HARDWARE KIT - COMP | 4 | 40 | 8.8 |  | N926BP00429 | 8.8 | 352
88 | G081270 |  | KIT | CASE, INLET BRG #1, HARDWARE KIT - COMP | -1 | 1 | 0 |  | 354A1060G003 | 0 | NA
89 | G081270 |  | NUT | CASE, INLET BRG #1, HARDWARE KIT - COMP | 6 | 16 | 7.25 |  | N204P00039 | 7.25 | 116
90 | G081270 |  | PIN-DOWEL | CASE, INLET BRG #1, HARDWARE KIT - COMP | 9 | 4 | 19.77 |  | 158A5457P081 | 19.77 | 79.08
91 | G081270 |  | PIN-GRVD STR | CASE, INLET BRG #1, HARDWARE KIT - COMP | 6 | 4 | 1.58 |  | N511P01910 | 1.58 | 6.32
92 | G081270 |  | PLATE-LOCK | CASE, INLET BRG #1, HARDWARE KIT - COMP | 4 | 18 | 3.13 |  | 294A0150P007 | 3.13 | 56.34
93 | G081270 |  | PLUG | CASE, INLET BRG #1, HARDWARE KIT - COMP | 5 | 4 | 131.25 |  | 208B7200P002 | 131.25 | 525
94 | G081270 |  | PLUG-PIPE | CASE, INLET BRG #1, HARDWARE KIT - COMP | 5 | 4 | 2.21 |  | 286A6290P002 | 2.21 | 8.84
95 | G081270 |  | PLUG-PIPE | CASE, INLET BRG #1, HARDWARE KIT - COMP | 5 | 2 | 3.15 |  | 286A6290P005 | 3.15 | 6.3
96 | G081270 |  | PLUG-PIPE | CASE, INLET BRG #1, HARDWARE KIT - COMP | 9 | 2 | 8.18 |  | 286A6290P009 | 8.18 | 16.36
97 | G081270 |  | SCREW | CASE, INLET BRG #1, HARDWARE KIT - COMP | 6 | 16 | 0.32 |  | N22P21014 | 0.32 | 5.12
98 | G081270 |  | SLEEVE | CASE, INLET BRG #1, HARDWARE KIT - COMP | 11 | 2 | 107.1 |  | 331B1540P001 | 107.1 | 214.2
99 | G081270 |  | WASHER | CASE, INLET BRG #1, HARDWARE KIT - COMP | 6 | 16 | 2.21 |  | N402P00041 | 2.21 | 35.36
100 | G081281 |  | INSERT | CASE, INLET BRG #1, INSERT | 11 | 2 | 10.11 |  | N926BP00321 | 10.11 | 20.22
101 | G090507 | LB50 | GASKET | PP ARR,LO FD&DRN BASE, GASKET | 6 | 1 | 8.55 |  | 302A4594P010 | 8.55 | 8.55
102 | G09183435 |  | GASKET | PPG ARR,FL NZL PRG,GSKT,SPRL WOUND | 3 | 2 | 6.89 |  | 302A4594P033 | 6.89 | 13.78
103 | G09183437 |  | GASKET | PPG ARR,FL NZL PRG,GSKT,SPRL WOUND | 3 | 1 | 10.11 |  | 302A4594P036 | 10.11 | 10.11
104 | G09186559 |  | NUT | PPG ARR,FUEL NZL PRG,NUT,SELF LCKNG | 3 | 6 | 3.05 |  | N265BP00035 | 3.05 | 18.3
105 | G095301 | UB34 | GASKET | PPNG ARR,GSKT,HRZNTL JT WTR WSHMFD | 3 | 9 | 4.41 |  | 302A4594P006 | 4.41 | 39.69
106 | G095304 | UB34 | BOLT | PPNG ARR,BOLT,HZNTL JT WTR WSH MNFD | 3 | 36 | 1.89 |  | N14P29040 | 1.89 | 68.04
107 | G095307 | UB34 | NUT | PPNG ARR,NUT,HZNTL JT WTR WSH MNFLD | 3 | 36 | 6.62 |  | N265BP00029 | 6.62 | 238.32
108 | G097201 |  | PLATE-LOCK | PPG ARR, EX FR CLG, LKPL, CSNG FLNG | 9 | 32 | 1.13 |  | 294A0150P006 | 1.13 | 36.16
109 | G097204 |  | GASKET | PPG ARR, EX FRM CLG, GSKT, SUP FLNG | 3 | 2 | 12.86 |  | 302A4594P014 | 12.86 | 25.72
110 | G09720A |  | GASKET | PPG ARR, EX FR CLG, GSKT, CSNG FLNG | 3 | 4 | 9.09 |  | 302A4594P013 | 9.09 | 36.36
111 | G09720J |  | BOLT | PPG ARR, EX FR CLG, BOLT, CSNG FLNG | 10 | 7 | 0.84 |  | N14P35036 | 0.84 | 5.88
112 | G09720M |  | BOLT | PPG ARR,EX FR CLG,BOLT SPLY FLNGJT | 6 | 4 | 4.11 |  | N14P35056 | 4.11 | 16.44
113 | G09720V |  | NUT | PPG ARR,EX FR CLG,NUT,SPLY FLNG JTS | 3 | 4 | 3.05 |  | N265BP00035 | 3.05 | 12.2
114 | G09826558 |  | NUT-LOCK | NUT,SELF-LOCKING | 3 | 3 | 1.05 |  | N265BP00033 | 1.05 | 3.15
115 | G09826574 |  | NUT-LOCK | NUT,SELF-LOCKING | 3 | 1 | 2.21 |  | N265BP00025 | 2.21 | 2.21
116 | G140317 |  | SCREW | SPPRT RNG, 1ST-STG, SCRW-HOR JNT | 5 | 1 | 43.09 |  | N733AP50112 | 43.09 | 43.09
117 | G14031G |  | INSERT | SPPRT RNG, 1ST-STG, INSRT-H JNT SCR | 3 | 2 | 38.99 |  | N926CP00350H2 | 38.99 | 77.98
118 | G150201 |  | LINER | BRNG ASM,NO 2, LINER ASSEMBLY | 22 | 1 | 13851.6 |  | 193D2251G001 | 13851.6 | 13851.6
119 | G15020P |  | SEAL | BRNG ASM,NO 2, OIL SEAL | 12 | 2 | 2863.56 |  | 163C4798G001 | 2863.56 | 5727.12
120 | G15022D |  | PLATE-LOCK | BRNG ASM,NO 2, STRAP MTG LCK PLT | 9 | 4 | 5.15 |  | 294A0150P009 | 5.15 | 20.6
121 | G15026S |  | PLATE-LOCK | BRNG ASM,NO 2, HSG FLG SCR LCK PLT | 4 | 4 | 3.13 |  | 294A0150P007 | 3.13 | 12.52
122 | G150274 |  | PLATE-LOCK | BRNG ASM,NO 2, HSG FLG SCR LKPT-MDL | 8 | 8 | 7.54 |  | 258A4784P007 | 7.54 | 60.32
123 | G150277 |  | PLATE-LOCK | BRNG ASM,NO 2, HSG FLG SCR LKPT-END | 8 | 4 | 13.42 |  | 258A4784P008 | 13.42 | 53.68
124 | G15027Y |  | SEAL | BRNG ASM,NO 2, AIR SEAL - OTR | 14 | 2 | 3116.4 |  | 163C4108G006 | 3116.4 | 6232.8
125 | G15028D |  | BOLT | BRNG ASM,NO 2, LNR SL TOOTH MTG BLT | 3 | 5 | 1.26 |  | N14P25012 | 1.26 | 6.3
126 | G1502AA |  | PLATE-LOCK | BRG 2, LNR ASM, INSUL PCK LKPLT-SDE | 4 | 12 | 5.42 |  | 114A6734P005 | 5.42 | 65.04
127 | G1502AB |  | BOLT | BRG 2, LNR ASM, INSUL PCK BOLT-SDE | 3 | 3 | 0.95 |  | N14P29052 | 0.95 | 2.85
128 | G1502AJ |  | PLATE-LOCK | BRG 2, LKPLT, INSUL PCK/HSNG-AFT | 11 | 4 | 2.36 |  | 302A7200P001 | 2.36 | 9.44
129 | G1502AP |  | PLATE-LOCK | BRG 2, LKPLT, INSUL PCK UPR/LWR | 9 | 8 | 7.54 |  | 302A4357P001 | 7.54 | 60.32
130 | G150301 |  | LINER | BRNG ASM, NO 3, LINER ASSEMBLY | 16 | 1 | 23512.65 |  | 112E1292G001 | 23512.65 | 23512.65
131 | G15030V |  | SEAL | BRNG ASM, NO 3, FWD-AFT OIL SEAL | 9 | 2 | 2362.58 |  | 201C7968G001 | 2362.58 | 4725.16
132 | G150314 |  | DEFLECTOR | BRNG ASM, NO 3, DEFLECTOR - FWD | 24 | 1 | 1284.19 |  | 239A5622G001 | 1284.19 | 1284.19
133 | G15031G |  | PLATE-LOCK | BRNG ASM, NO 3, STRAP BOLT LCKPLT | 8 | 4 | 14.61 |  | 114A6734P018 | 14.61 | 58.44
134 | G15031J |  | BOLT | BRNG ASM, NO 3, STRAP MNTNG BOLT | 6 | 1 | 55.65 |  | N14TP50160 | 55.65 | 55.65
135 | G15031P |  | PLATE-LOCK | BRNG ASM, NO 3, HSNG FLNG BLT LKPLT | 8 | 4 | 17.16 |  | 258A4784P006 | 17.16 | 68.64
136 | G15031S |  | PLATE-LOCK | BRNG ASM, NO 3, HSNG FLNG BLT LKPLT | 6 | 2 | 88.2 |  | 268A1431P001 | 88.2 | 176.4
137 | G15032M |  | PLATE-LOCK | BRNG ASM, NO 3, SHIM-HOR LCKPLT | 9 | 8 | 10.48 |  | 114A6734P008 | 10.48 | 83.84
138 | G150364 |  | BOLT | BRNG ASM, NO 3, GUIDE TUBE MTG BOLT | 6 | 1 | 0.32 |  | N22P21014 | 0.32 | 0.32
139 | G150701 |  | SHIM | BRNG ARR, THRST-HP, SHIM (LOADED) | 10 | 1 | 373.12 |  | 324A9583G001 | 373.12 | 373.12
140 | G150707 |  | BEARING | BRNG ARR, THRST-HP, BRNG (LOADED) | 12 | 1 | 19224.98 |  | 275A8411P001 | 19224.98 | 19224.98
141 | G15070A |  | BEARING | BRNG ARR, THRST-HP, BRNG (UNLOADED) | 14 | 1 | 8279.04 |  | 248A6443P004 | 8279.04 | 8279.04
142 | G15070D |  | SHIM | BRNG ARR, THRST-HP, SHIM (UNLOADED) | 9 | 1 | 582.02 |  | 215A3219G002 | 582.02 | 582.02
143 | G160401 | UA10 | BOLT | B&D ARR, BOLT, INLT/CMP CSNG | 6 | 12 | 6.5 |  | N733P39064 | 6.5 | 78
144 | G160404 | UA10 | DOWEL | B & D ARR, DWL, INLET/FWD CMP CSNG | 10 | 2 | 20.84 |  | 158A5457P082 | 20.84 | 41.68
145 | G16040D | UA10 | BOLT | B & D ARR, BLT, CMP CASE/DISCH CASE | 11 | 10 | 34.3 |  | N733AP44088 | 34.3 | 343
146 | G160471 | UA10 | BOLT | B & D ARR, BOLT, TRB SHELL/EXH FRM | 17 | 2 | 108.36 |  | N733BP39056 | 108.36 | 216.72
147 | G16049M | UA10 | BOLT | B & D ARR, BLT, COMB WRPR/DSCH CASE | 20 | 3 | 9.38 |  | N733AP35072 | 9.38 | 28.14
148 | G16049P | UA10 | NUT | B & D ARR, NUT, COMB WRPR/DSCH CASE | 5 | 3 | 11.5 |  | N272QP00035 | 11.5 | 34.5
149 | G16049S | UA10 | WASHER | B & D ARR, WSHR, CMB WRPR/DSCH CASE | 3 | 3 | 6.93 |  | N402P00018 | 6.93 | 20.79
150 | G16120V |  | BOLT | PLNM,INLT-ASM, BLT,PLNM/BLL-FWDWSR | 3 | 13 | 58 |  | N14P33024 | 58 | 754
151 | G16120Y |  | WASHER | PLNM,INLT-ASM,WSHR,PLNM/BLL-FWD BLT | 6 | 13 | 0.63 |  | N402P00077 | 0.63 | 8.19

## Turbine Capitals
[7 empty] | List Total: |  |  |  | List Total: | Credit Total
[7 empty] | 7760351.9 |  |  |  | 7760351.9 | 0
GT Turbine Capitals
LINE | CATALOG | CAT | [6 empty] | SIMILAR-TO | UNIT
ITEM | NUMBER | LOC | PART NAME | PART DESCRIPTION | CYC | QTY | SYS PRICE | UM | DWG NUMBER | PRICE | LINE PRICE
____________
1 | G0705L1 |  | KIT | CASE ARR, TURB, SHROUD KIT - STG1 | 15 | 1 | 182902 |  | 339A9964G002 | 182902 | 182902
2 | G0705LA |  | KIT | CASE ARR, TURB, SHROUD KIT - STG2 | 19 | 1 | 137414 |  | 339A9965G005 | 137414 | 137414
3 | G0705LG |  | KIT | CASE ARR, TURB, SHROUD KIT - STG3 | 37 | 1 | 74762 |  | 339A9966G005 | 74762 | 74762
4 | G13014X | UA40 | KIT | CMPRSR STATR, VANE ARR, KIT -BLADES | 29 | 1 | 892751 |  | 106L1708G002 | 892751 | 892751
5 | G13014Z | TB02 | KIT | CMPRSR STATR, VANE SET, IGV, KIT | 37 | 1 | 207783 |  | 317A9589G004 | 207783 | 207783
6 | G13032S |  | KIT | CMPRSSR RTR, BLADE KIT | 19 | 1 | 811394 |  | 106L1709G001 | 811394 | 811394
7 | G13052J |  | KIT | ROTOR, TRBN, BUCKET KIT - 1ST STG | 21 | 1 | 910540 |  | 314B7165G020 | 910540 | 910540
8 | G13052M |  | KIT | ROTOR, TRBN, BUCKET KIT - 2ND STG | 33 | 1 | 901965 |  | 314B7166G023 | 901965 | 901965
9 | G13052P |  | KIT | ROTOR, TRBN, BUCKET KIT - 3RD STG | 13 | 1 | 791255 |  | 314B7167G019 | 791255 | 791255
10 | G140100 |  | NOZZLE-ASM | NOZZ 1ST-STG, ASSEMBLY | 17 | 1 | 899488 |  | 109E3735G018 | 899488 | 899488
11 | G140200 |  | NOZZLE-ASM | NOZZ 2ND STG, ASSEMBLY | 29 | 1 | 926971 |  | 116E1417G001 | 926971 | 926971
12 | G140300 |  | RING-ASM | SPPRT RNG, 1ST-STG ASSEMBLY | 24 | 1 | 36558.9 |  | 227C5682G005 | 36558.9 | 36558.9
13 | G140900 |  | NOZZLE-ASM | NOZZLE 3RD STG, ASSEMBLY | 25 | 1 | 986568 |  | 112E6649G001 | 986568 | 986568

## Turbine Ops
[7 empty] | List Total: |  |  |  | List Total: | Credit Total
[7 empty] | 312328.31 |  |  |  | 339496.82 | 0
GT Turbine Operationals
LINE | CATALOG | CAT | [6 empty] | SIMILAR-TO | UNIT
ITEM | NUMBER | LOC | PART NAME | PART DESCRIPTION | CYC | QTY | SYS PRICE | UM | DWG NUMBER | PRICE | LINE PRICE
____________
1 | G02290V | SUMM | THERMOMETER | INSTM,TRBN LO, LO TANK THERMOMETER | 6 | 1 | 119.7 |  | 272A6619P005 | 119.7 | 119.7
2 | G02291K | SUMM | THERMOMETER | INSTM,TRBN LO, TMP SW | 6 | 1 | 109.62 |  | 272A6619P004 | 109.62 | 109.62
3 | G0235A0V | UA30 | QUILL | INST ARR, BRG#1, QUILL | 8 | 1 | 156.45 |  | 322B4207P001 | 156.45 | 156.45
4 | G0235A1H | UA30 | PROXIMITOR | INST ARR, BRG#1, PRXMTR (39VS12) | 6 | 1 | 429.51 |  | 109E3763P700 | 429.51 | 429.51
5 | G0235A1K | UA30 | PROXIMITOR | INST ARR, BRG#1, PRXMTR (39VS11) | 6 | 1 | 429.51 |  | 109E3763P700 | 429.51 | 429.51
6 | G0235A1N | UA30 | PROXIMITOR | INST ARR, BRG#1, PRXMTR (77RP11) | 6 | 1 | 429.51 |  | 109E3763P700 | 429.51 | 429.51
7 | G0235A1R | UA30 | PROXIMITOR | INST ARR, BRG#1, PRXMTR (96VC12) | 6 | 1 | 429.51 |  | 109E3763P700 | 429.51 | 429.51
8 | G0235A1T | UA30 | PROXIMITOR | INST ARR, BRG#1, PRXMTR (96VC11) | 6 | 1 | 429.51 |  | 109E3763P700 | 429.51 | 429.51
9 | G0235A9J | UA30 | EXTENSION | INST ARR,BRG #1, VIB DET EXT 96VC12 | 14 | 1 | 273 |  | 109E3763P602 | 273 | 273
10 | G0235A9M | UA30 | EXTENSION | INST ARR,BRG #1, VIB DET EXT 96VC11 | 14 | 1 | 273 |  | 109E3763P602 | 273 | 273
11 | G0235AHD | UA30 | EXTENSION | INST ARR,BRG #1,VIB DET EXT 39VS11 | 14 | 1 | 273 |  | 109E3763P602 | 273 | 273
12 | G0235AHE | UA30 | EXTENSION | INST ARR,BRG #1,VIB DET EXT 39VS12 | 14 | 1 | 273 |  | 109E3763P602 | 273 | 273
13 | G0235AHG | UA30 | EXTENSION | INST ARR,BRG #1,VIB DET EXT 77RP11 | 14 | 1 | 383.99 |  | 109E3763P601 | 383.99 | 383.99
14 | G0235BAJ | UA30 | PROXIMITOR | INST ARR, BRG#2, PRXMTR (39VS22) | 6 | 1 | 429.51 |  | 109E3763P700 | 429.51 | 429.51
15 | G0235BAK | UA30 | PROXIMITOR | INST ARR, BRG#2, PRXMTR (39VS21) | 6 | 1 | 429.51 |  | 109E3763P700 | 429.51 | 429.51
16 | G0235BAL | UA30 | PROXIMITOR | INST ARR, BRG#2, PRXMTR (39VS23) | 6 | 1 | 429.51 |  | 109E3763P700 | 429.51 | 429.51
17 | G0235BAM | UA30 | PROXIMITOR | INST ARR, BRG#2, PRXMTR (39VS24) | 6 | 1 | 429.51 |  | 109E3763P700 | 429.51 | 429.51
18 | G0235C3A | UA30 | QUILL | INST ARR, BRG#3, QUILL | 6 | 2 | 150.94 |  | 227B9160P002 | 150.94 | 301.88
19 | G0235CAM | UA30 | PROXIMITOR | INST ARR,BRG NO 3, VIB DTCTR PRXMTR | 6 | 2 | 429.51 |  | 109E3763P700 | 429.51 | 859.02
20 | G0235CBY | UA30 | EXTENSION | INST ARR,BRG NO. 3 EXT, VIB DETCTR | 4 | 2 | 216.3 |  | 109E3763P500 | 216.3 | 432.6
21 | G050202 | AB20 | ACCUM | CNTRL ARR,ACCESS SYSTEM,ACCUMULATOR | 14 | 2 | 1440.6 |  | 348A4766P004 | 1440.6 | 2881.2
22 | G05020G | AB20 | WASHER-LCK | SLND ARR-HYDR DUMP WASHER-LOCK | 6 | 4 | 0.63 |  | N405P00045 | 0.63 | 2.52
23 | G05020S | AB20 | WASHER-LCK | SLND AR-STRT CLT&HDR DMP WSHR-LK | 6 | 8 | 3.13 |  | N403P00062 | 3.13 | 25.04
24 | G0507 |  | BEARING | STOP/ SPEED RATIO VALVE, LINED BEARING | 6 | 2 | 58 |  | 356A4367P012-19 | 58 | 116
25 | G0507 |  | KEY | STOP/ SPEED RATIO VALVE, TAPER KEY | 6 | 1 | 46.2 |  | 356A4367P012-16 | 46.2 | 46.2
26 | G0507 |  | PACKING | STOP/ SPEED RATIO VALVE, PACKING RING | 6 | 1 | 14.7 |  | 356A4367P012-17 | 14.7 | 14.7
27 | G0507 |  | PACKING SET | STOP/ SPEED RATIO VALVE, PACKING SET | 6 | 1 | 33.1 |  | 356A4367P012-15 | 33.1 | 33.1
28 | G0507 |  | PIN | STOP/ SPEED RATIO VALVE, GROOVE PIN | 6 | 1 | 8.9 |  | 356A4367P012-18 | 8.9 | 8.9
29 | G0507 |  | REPAIR KIT | STOP/ SPEED RATIO VALVE, REPAIR KIT | 6 | 1 | 1030 |  | 356A4367P012-14 | 1030 | 1030
30 | G0507 |  | SPARES KIT | STOP/ SPEED RATIO VALVE, ACTUATOR | 8 | 1 | 5743 |  | 356A4367P012-KIT | 5743 | 5743
31 | G050801 |  | PICKUP | FLW DVDR & MAG PCKUP ARR, PICKUP | 8 | 3 | 123.48 |  | 185A1117P011 | 123.48 | 370.44
32 | G05080A |  | PLATE-LOCK | FLW DVDR & MAG PCKUP ARR, LCKPLT | 6 | 2 | 3.31 |  | N405P00043 | 3.31 | 6.62
33 | G0509 |  | GASKET | STOP/ SPEED RATIO VALVE, GASKET | 6 | 1 | 42.1 |  | 356A4368P003-18 | 42.1 | 42.1
34 | G0509 |  | GROOVE PIN | STOP/ SPEED RATIO VALVE, GROOVE PIN | 6 | 1 | 5 |  | 356A4368P003-16 | 5 | 5
35 | G0509 |  | PLUG STEM | STOP/ SPEED RATIO VALVE, PLUG STEM | 6 | 1 | 543 |  | 356A4368P003-19 | 543 | 543
36 | G0509 |  | PLUG VALVE | STOP/ SPEED RATIO VALVE, PLUG VALVE | 6 | 1 | 2068 |  | 356A4368P003-17 | 2068 | 2068
37 | G0509 |  | REPAIR KIT | STOP/ SPEED RATIO VALVE, REPAIR KIT | 6 | 1 | 147 |  | 356A4368P003-20 | 147 | 147
38 | G0509 |  | SEAT / LINER | STOP/ SPEED RATIO VALVE, SEAT / LINER | 6 | 1 | 4337 |  | 356A4368P003-15 | 4337 | 4337
39 | G0509 |  | SPARES KIT | STOP/ SPEED RATIO VALVE, ACTUATOR | 8 | 1 | 4234 |  | 356A4368P003-KIT | 4234 | 4234
40 | G054601 |  | PICKUP | MAG PICKUP ARR-HP, MAG PICKUP | 11 | 3 | 138.86 |  | 351A3236P001 | 138.86 | 416.58
41 | G054807 |  | FILTER | ACTUATOR ASSEMBLY, IGV, HYD FILTER | 12 | 1 | 878.85 |  | 315A2660P001 | 878.85 | 878.85
42 | G05480A |  | TRANSDUCER | ACTUATOR ASSEMBLY, IGV, TRANSDUCER | 20 | 2 | 1515.86 |  | 311A5178P011 | 1515.86 | 3031.72
43 | G0557T4G |  | VALVE | TRNSDCR ARR, BALL VALVE | 9 | 3 | 743.82 |  | 356A1582P001 | 743.82 | 2231.46
44 | G055904 |  | PROBE | SNSR ARR, INL/EXH, PRBE, EXH DCT PR | 7 | 2 | 131.62 |  | 318A9784G002 | 131.62 | 263.24
45 | G05590D |  | VALVE | SNSR ARR, INL/EXH, VLV, 3-WAY VALVE | 7 | 1 | 276.15 |  | 361A5107P001 | 276.15 | 276.15
46 | G05641D | MSDM | INDICATOR | VALVE, SPLITTER, PRIMARY VLV POS | 5 | 2 | 31.5 |  | 342A2328P001 | 31.5 | 63
47 | G05641G | MSDM | BEARING | VALVE, SPLITTER, LVDT | 5 | 2 | 31.5 |  | 298A0259P011 | 31.5 | 63
48 | G056443 | MSDM | GASKET | VALVE, SPLITTER,VLV CTRL MDL,CVR-PL | 12 | 1 | 12.6 |  | 318A9732P001 | 12.6 | 12.6
49 | G05644D | MSDM | O-RING | VALVE, SPLITTER,VLV CTRL MDL | 3 | 2 | 12.6 |  | 185A1354P117 | 12.6 | 25.2
50 | G056801 | MSDM | VLV-SERVO | SERVO ARR,TRANS VALVE,SERVOVALVE | 12 | 1 | 2467.25 |  | 312A6077P002 | 2467.25 | 2467.25
51 | G062700 |  | PUMP-HYD | PUMP, HYDRLC-HP | 13 | 1 | 1141.09 |  | 351A9554P001 | 1141.09 | 1141.09
52 | G062801 |  | PUMP | PUMP, HYD-AUX, PUMP | 13 | 1 | 1141.09 |  | 351A9554P001 | 1141.09 | 1141.09
53 | G062804 |  | MOTOR | PUMP, HYD-AUX, MOTOR | 28 | 1 | 1987.44 |  | 351A9553P001 | 1987.44 | 1987.44
54 | G06374M | UA40 | CONNECTOR | TC ARR,REMOVBL,CONNECTOR,TTWS3FO1 | 3 | 1 | 22.83 |  | 287A1399P010 | 22.83 | 22.83
55 | G06374P | UA40 | CONNECTOR | TC ARR,REMOVBL,CONNECTOR,TTWS2AO1 | 3 | 1 | 22.83 |  | 287A1399P010 | 22.83 | 22.83
56 | G06374S | UA40 | CONNECTOR | TC ARR,REMOVBL,CONNECTOR,TTWS1AO1 | 3 | 1 | 22.83 |  | 287A1399P010 | 22.83 | 22.83
57 | G06374V | UA40 | CONNECTOR | TC ARR,REMOVBL,CONNECTOR,TTWS2FO1 | 3 | 1 | 22.83 |  | 287A1399P010 | 22.83 | 22.83
58 | G06374Y | UA40 | CONNECTOR | TC ARR,REMOVBL,CONNECTOR,TTWS3FO2 | 3 | 1 | 22.83 |  | 287A1399P010 | 22.83 | 22.83
59 | G063751 | UA40 | CONNECTOR | TC ARR,REMOVBL,CONNECTOR,TTWS2AO2 | 3 | 1 | 22.83 |  | 287A1399P010 | 22.83 | 22.83
60 | G063754 | UA40 | CONNECTOR | TC ARR,REMOVBL,CONNECTOR,TTWS2FO2 | 3 | 1 | 22.83 |  | 287A1399P010 | 22.83 | 22.83
61 | G063757 | UA40 | CONNECTOR | TC ARR,REMOVBL,CONNECTOR,TTWS1AO2 | 3 | 1 | 22.83 |  | 287A1399P010 | 22.83 | 22.83
62 | G06375D | UA40 | REDUCER | TC ARR,REMOVBL,REDUCER,TTIB1 | 5 | 1 | 1.89 |  | 286A6292P006 | 1.89 | 1.89
63 | G06375G | UA40 | CONNECTOR | TC ARR,REMOVBL,CONNECTOR,TTWS1FI2 | 11 | 1 | 41.37 |  | 287A1399P018 | 41.37 | 41.37
64 | G06375P | UA40 | CONNECTOR | TC ARR,REMOVBL,CONNECTOR,TTWS1FI1 | 11 | 1 | 41.37 |  | 287A1399P018 | 41.37 | 41.37
65 | G06375S | UA40 | REDUCER | TC ARR,REMOVBL,REDUCER,TTIB2 | 5 | 1 | 1.89 |  | 286A6292P006 | 1.89 | 1.89
66 | G06375V | UA40 | CONNECTOR | TC ARR,REMOVBL,CONNECTOR, TTIB1 | 3 | 1 | 29.2 |  | 156A1085P014 | 29.2 | 29.2
67 | G0637BW | UA40 | REDUCER | TC ARR,REMOVBL,REDUCER,TTIB3 | 5 | 1 | 1.89 |  | 286A6292P006 | 1.89 | 1.89
68 | G06390S | SUMM | MANIFOLD | FL GS FLW MEAS SYS,MTR TB 5-VLV MFD | 11 | 1 | 777.63 |  | 334A7915P001 | 777.63 | 777.63
69 | G09030D |  | VLV-CHECK | PPG ARR, L O , PUMP DISCH CHK VALVE | 11 | 1 | 352.59 |  | 226A1362P003 | 352.59 | 352.59
70 | G09046P |  | GASKET | PP,OIL TNK EXT, GSKT, AUX HYD PMP | 3 | 1 | 17.46 |  | 318A9450P001 | 17.46 | 17.46
71 | G09052X | LB50 | SIGHT | PP LO FD&DRN, SIGHT FL, BRG3 DRN\BS | 9 | 2 | 348.97 |  | 255A4908P005 | 348.97 | 697.94
72 | G09082J |  | VLV-CHECK | PP AR, CO-INT, CHECK VALVE | 13 | 2 | 155.77 |  | 114A3759P009 | 155.77 | 311.54
73 | G09096C | UB33 | VLV-BUTTERFLY | PP C&SA, BFLY VLV, AIR CLNR INLET | 11 | 1 | 736.58 |  | 287A1496P001 | 736.58 | 736.58
74 | G09096D | UB26 | VLV-BALL | PP ARR C&SA, BLL VLV, AIR CLN BLWDN | 14 | 4 | 341.72 |  | 286A6199P001 | 341.72 | 1366.88
75 | G09096E | UB33 | VLV-BUTTERFLY | PP C&SA, BFLY VLV, AIR CLN BLWDN | 16 | 1 | 266.86 |  | 279A2388P002 | 266.86 | 266.86
76 | G091407 |  | VLV-BUTTERFLY | PP ARR, CLG WTR, LO HT EX ISOL VLV | 9 | 1 | 361.04 |  | 348A5706P006 | 361.04 | 361.04
77 | G091608 |  | HOSE | PP AR,ST MNS,HS-FLX,FD PMP INLET | 11 | 1 | 1465.3 |  | 351A9543P003 | 1465.3 | 1465.3
78 | G091609 |  | HOSE | PP AR,ST MNS,HS-FLX,FD PMP OUTLET | 11 | 1 | 842.84 |  | 351A9543P004 | 842.84 | 842.84
79 | G091627 |  | VLV-BUTTERFLY | PP, STRT MNS, BFLY VLV, STRNR INLET | 11 | 1 | 736.58 |  | 287A1496P001 | 736.58 | 736.58
80 | G09261J |  | GAUGE | CBNT ASM,GAUGE,PR,DL IND (OL-2) | 14 | 1 | 78.12 |  | 235A9761P003 | 78.12 | 78.12
81 | G09261M |  | GAUGE | CBNT ASM,GAUGE,PR,DL IND (OL-3) | 14 | 1 | 78.12 |  | 235A9761P003 | 78.12 | 78.12
82 | G09261S |  | GAUGE | CBNT ASM,GAUGE,PR,DL IND (OL-4) | 10 | 1 | 74.34 |  | 235A9761P006 | 74.34 | 74.34
83 | G09261V |  | GAUGE | CBNT ASM,GAUGE,PR,DL IND (OL-5) | 10 | 1 | 74.34 |  | 235A9761P006 | 74.34 | 74.34
84 | G092624 |  | GAUGE | CBNT ASM,GAUGE,PR,DL IND (OL-1) | 10 | 1 | 74.34 |  | 235A9761P006 | 74.34 | 74.34
85 | G092627 |  | GAUGE | CBNT ASM,GAUGE,PR,DL IND (OH-1) | 14 | 1 | 90.72 |  | 235A9761P013 | 90.72 | 90.72
86 | G09262A |  | GAUGE | CBNT ASM,GAUGE,PR,DL IND (MLF) | 10 | 1 | 216.14 |  | 272A6132P042 | 216.14 | 216.14
87 | G09262D |  | GAUGE | CBNT ASM,GAUGE,PR,DL IND (HPF1) | 10 | 1 | 212.52 |  | 272A6132P045 | 212.52 | 212.52
88 | G092687 |  | VALVE | CBNT ASM, VALVE, GAUGE ISOLATION | 3 | 3 | 118.44 |  | 351A3295P010 | 118.44 | 355.32
89 | G09268A |  | VALVE | CBNT ASM, VALVE, TEST | 14 | 1 | 297.05 |  | 318A9758P013 | 297.05 | 297.05
90 | G09268P |  | BOTTLE | CBNT ASM, GAUGE, BOTTLE,SAMPLE | 4 | 1 | 6.15 |  | 235A8443P001 | 6.15 | 6.15
91 | G092901 |  | STRAINER | STRAINER ASSY, FUEL GAS, STRAINER | 14 | 1 | 2969.4 |  | 185A1632P005 | 2969.4 | 2969.4
92 | G09530K | UB34 | NOZZLE | CMPRSR WSH,WTR WSH NZL ASM-ON-LINE | 9 | 3 | 398.48 |  | 247B5094G001 | 398.48 | 1195.44
93 | G09530L | UB34 | NOZZLE | CMPRSR WSH,WTR WSH NZL ASM-OFF-LINE | 9 | 3 | 935.81 |  | 186C1887G005 | 935.81 | 2807.43
94 | G09530M | UB34 | NOZZLE | CMPR WSH, W WSH NZL ASM-ON-LINE-FWD | 9 | 3 | 275.31 |  | 242B9459G003 | 275.31 | 825.93
95 | G095311 | SUMM | VLV-NEEDLE | CMPRSR WSH, DRAIN VALVE | 11 | 1 | 143.69 |  | 256A1129P016 | 143.69 | 143.69
96 | G097901 | SUMM | VLV-BALL | PPG ARR, INLT PLNM DRN, VLV,WTR DRN | 14 | 1 | 421.42 |  | 298A7785P003 | 421.42 | 421.42
97 | G09821J |  | FILTER | PP ARR C&SA,FLTR,FLD PR CONTRL AIR | 9 | 1 | 422.63 |  | 357A1233P004 | 422.63 | 422.63
98 | G101600 |  | VLV-RELIEF | VLV, RELIEF, LUBE OIL (VR-1) | 5 | 1 | 1761.65 |  | 248A5994P002 | 1761.65 | 1761.65
99 | G101900 |  | VALVE-SOL | VLV, SOLENOID (20FG,20FL,20TV,20HD) | 10 | 1 | 5122.66 |  | 354A1617P001 | 5122.66 | 5122.66
100 | G102200 |  | VALVE | VLV, CONT 4TH&10TH STG EXT(VA2-1,2) | 14 | 1 | 7123.03 |  | 354A1107P001 | 7123.03 | 7123.03
101 | G102300 |  | VALVE | VALVE, RGLTR,PRESS-LO,ASSY, VPR2-1 | 14 | 1 | 3038.7 |  | 156A1413P054 | 3038.7 | 3038.7
102 | G102600 |  | VALVE | VLV, REG-FALSE STRT DRN (VA17) | 14 | 1 | 1540.56 |  | 314A5266P001 | 1540.56 | 1540.56
103 | G103500 |  | VALVE | VLV,CLNG WTR,LUBE OIL (VTR1-1) | 20 | 1 | 6882.9 |  | 347A5759P001 | 6882.9 | 6882.9
104 | G103800 |  | SWITCH | SWTCH, LIQ LVL-LUBE OIL, 71QH/71QL | 8 | 1 | 1754 |  | 361A2111P001 | 1754 | 1754
105 | G105104 |  | CARTRIDGE | FILTER-HYDRALIC SUPPLY, CARTRIDGE | 8 | 2 | 160 |  | 258A4860P002 | 160 | 320
106 | G105300 |  | CARTRIDGE | CARTRIDGE, FILTER-MAIN LUBE OIL | 6 | 24 | 14.2 |  | 342A2581P002 | 14.2 | 340.8
107 | G107100 |  | VALVE-SOL | VLV, SOLENOID-CMPRSR BLEED (20CB-1) | 14 | 1 | 3956.06 |  | 347A5056P001 | 3956.06 | 3956.06
108 | G108200 |  | VALVE | GAS FUEL SYSTEM PURGE VALVE | 20 | 1 | 7599.31 |  | 358A7146P002 | 7599.31 | 7599.31
109 | G112101 |  | DETECTOR | DTCTR, FLME (28FD), DETECTOR | 40 | 4 | 3171 |  | 261A1812P012 | 3171 | 12684
110 | G121301 |  | LEAD | IGNITION SYS, LEAD, SPRK PLG | 18 | 2 | 738.99 |  | 354A1513P014 | 738.99 | 1477.98
111 | G12130A |  | EXCITER | IGNITION SYS, EXCITER (95SG) | 26 | 1 | 5162 |  | 354A1709P001 | 5162 | 5162
112 | G121400 |  | ASM-SPARK PLUG | SPRK PLG ASM | 12 | 2 | 1934.52 |  | 109E9348G003 | 1934.52 | 3869.04
113 | G1218A1J |  | WIRE-LOCK | SENSOR ARR, VBRTN, WIRE-LOCK | 15 | 2 | 21.69 |  | 35068 | 21.69 | 43.38
114 | G1218A8Y |  | WASHER-LCK | SENSOR ARR,VBRTN,WSHR,SNSR MTG WSHR | 9 | 8 | 1.26 |  | 344A6211P003 | 1.26 | 10.08
115 | G1218A91 |  | SCREW-CAP | SENSOR ARR,VBRTN,SCRW,SNSR MTG SCRW | 3 | 8 | 6.44 |  | N170P13010 | 6.44 | 51.52
116 | G1218B8Y |  | WASHER-LCK | SENSOR ARR,VBRTN,WSHR,SNSR MTG WSHR | 9 | 4 | 1.26 |  | 344A6211P003 | 1.26 | 5.04
117 | G1218B91 |  | SCREW-CAP | SENSOR ARR,VBRTN,SCRW,SNSR MTG SCRW | 3 | 4 | 6.44 |  | N170P13010 | 6.44 | 25.76
118 | G1218C1J |  | WIRE-LOCK | SENSOR ARR, VBRTN, WIRE-LOCK | 15 | 2 | 21.69 |  | 35068 | 21.69 | 43.38
119 | G1218C8Y |  | WASHER-LCK | SENSOR ARR,VBRTN,WSHR,SNSR MTG WSHR | 9 | 8 | 1.26 |  | 344A6211P003 | 1.26 | 10.08
120 | G1218C91 |  | SCREW-CAP | SENSOR ARR,VBRTN,SCRW,SNSR MTG SCRW | 3 | 8 | 6.44 |  | N170P13010 | 6.44 | 51.52
121 | G130321 |  | PICKUP | CMPRSSR RTR, SPEED PICKUP | 22 | 1 | 8529.15 |  | 118D6689P001 | 8529.15 | 8529.15
122 | G130900 | PT13 | HARDWARE | HARDWARE, LOAD COUPLING | 20 | 1 | 6431.54 |  | 358A7395P003 | 6431.54 | 6431.54
123 | G130900 |  | HARDWARE | HARDWARE, LOAD COUPLING | 22 | 1 | 8747.09 |  | 358A7395P005 | 8747.09 | 8747.09
124 | G131300 |  | COUPLING | COUPLING, ACC GEAR ASSEMBLY | 24 | 1 | 12000.45 |  | 307A9219G001 | 12000.45 | 12000.45
125 | G131900 |  | COUPLING | COUPLING,OUTPUT | 28 | 1 | 81916.8 |  | 347A5542P001 | 81916.8 | 81916.8
126 | G20TW1 | 953 | VALVE | TB(CPRSR)WSH WI SOL(MTR) VLV-OFF-LN | 13 | 1 | 1205.4 |  | 311A5449P005 | 1205.4 | 1205.4
127 | G20TW3 | 953 | VALVE | TRB(CPRSR)WSH WI SOL(MTR)VLV-ON-LNE | 13 | 1 | 1205.4 |  | 311A5449P005 | 1205.4 | 1205.4
128 | G23QT-1 | 938 | HEATER | IMMERSION HEATER LUBE OIL TANK | 13 | 1 | 584.85 |  | 361A2376P001 | 584.85 | 584.85
129 | G23QT-2 | 938 | HEATER | IMMERSION HEATER LUBE OIL TANK | 13 | 1 | 584.85 |  | 361A2376P001 | 584.85 | 584.85
130 | G26BT-1 | 414T | SWITCH | SWITCH, TURB COMPT TEMP | 13 | 1 | 484 |  | 351A9092P028 | 484 | 484
131 | G26BT-2 | 414T | SWITCH | SWITCH, TURB COMPT TEMP | 13 | 1 | 484 |  | 351A9092P029 | 484 | 484
132 | G26HA-3 | 414A | THERMOSTAT | ACCESSORY COMPARTMENT THERMOSTAT | 13 | 1 | 291 |  | 351A9092P027 | 291 | 291
133 | G26QA-1 | 414A | SWITCH | LUBE OIL HEADER HIGH TEMP ALARM | 13 | 1 | 335 |  | 351A9092P023 | 335 | 335
134 | G26QL-1 | 938 | SW-TEMP | LUBE OIL TANK TEMP , HEATERS ON/OFF | 10 | 1 | 21.42 |  | 351A3496P017 | 21.42 | 21.42
135 | G26QL-1 | 414A | SW-TEMP | LUBE OIL TANK TEMP , HEATERS ON/OFF | 13 | 1 | 335 |  | 351A9092P023 | 335 | 335
136 | G26QN-1 | 938 | SW-TEMP | LUBE OIL TANK TEMPERATURE NORMAL | 10 | 1 | 21.42 |  | 351A3496P017 | 21.42 | 21.42
137 | G26QN-1 | 414A | SW-TEMP | LUBE OIL TANK TEMPERATURE NORMAL | 13 | 1 | 335 |  | 351A9092P023 | 335 | 335
138 | G26QT-1A | 414A | SWITCH | LUBE OIL HEADER HIGH TEMP TRIP | 13 | 1 | 339 |  | 351A9092P022 | 339 | 339
139 | G26QT-1B | 414A | SWITCH | LUBE OIL HEADER HIGH TEMP TRIP | 13 | 1 | 339 |  | 351A9092P022 | 339 | 339
140 | G26VG-1 | 414T | THERMOSTAT | THRMST,LOAD COMPT HIGH TEMP-ALARM | 13 | 1 | 484 |  | 351A9092P028 | 484 | 484
141 | G26VG-2 | 414T | THERMOSTAT | THRMST,LOAD CPLG COMPT VENTILATING | 13 | 1 | 484 |  | 351A9092P029 | 484 | 484
142 | G39V-1A | 1218 | SENSOR | SENSOR ARR, VBRTN, SENSOR | 11 | 1 | 1287.72 |  | 329A3529P001 | 1287.72 | 1287.72
143 | G39V-1B | 1218 | SENSOR | SENSOR ARR, VBRTN, SENSOR | 11 | 1 | 1287.72 |  | 329A3529P001 | 1287.72 | 1287.72
144 | G39V-2A | 1218 | SENSOR | VIBRATION SENSOR TURBINE | 11 | 1 | 1287.72 |  | 329A3529P001 | 1287.72 | 1287.72
145 | G39V-3A | 1218 | SENSOR | SENSOR ARR, VBRTN, SENSOR | 11 | 1 | 1287.72 |  | 329A3529P001 | 1287.72 | 1287.72
146 | G39V-3B | 1218 | SENSOR | SENSOR ARR, VBRTN, SENSOR | 11 | 1 | 1287.72 |  | 329A3529P001 | 1287.72 | 1287.72
147 | G39VS-11 | 235 | PROBE | VIBRATION SENSOR (NON-CONTACTING) | 4 | 1 | 660.45 |  | 109E3763P951 | 660.45 | 660.45
148 | G39VS-21 | 235 | PROBE | VIBRATION SENSOR (NON-CONTACTING) | 7 | 1 | 243.6 |  | 109E3763P200 | 243.6 | 243.6
149 | G39VS-22 | 235 | PROBE | VIBRATION SENSOR (NON-CONTACTING) | 7 | 1 | 243.6 |  | 109E3763P200 | 243.6 | 243.6
150 | G39VS-23 | 235 | PROBE | VIBRATION SENSOR (NON-CONTACTING) | 18 | 1 | 267.75 |  | 109E3763P202 | 267.75 | 267.75
151 | G39VS-24 | 235 | PROBE | VIBRATION SENSOR (NON-CONTACTING) | 18 | 1 | 267.75 |  | 109E3763P202 | 267.75 | 267.75
152 | G39VS-31 | 235 | PROBE | VIBRATION SENSOR (NON-CONTACTING) | 7 | 1 | 272.9 |  | 109E3763P300 | 272.9 | 272.9
153 | G39VS-32 | 235 | PROBE | VIBRATION SENSOR (NON-CONTACTING) | 7 | 1 | 272.9 |  | 109E3763P300 | 272.9 | 272.9
154 | G43HR-1 | 1165 | SWITCH | HYDRAULIC RATCHET CONTROL SWITCH | 11 | 1 | 214.2 |  | 302A4545P002 | 214.2 | 214.2
155 | G45FLC-20A | 1160 | DETECTOR | FIRE DETECTOR-TURBINE COMPARTMENT | 24 | 1 | 429 |  | 361A2285P008 | 429 | 429
156 | G45FLC-20B | 1160 | DETECTOR | FIRE DETECTOR-TURBINE COMPARTMENT | 24 | 1 | 429 |  | 361A2285P008 | 429 | 429
157 | G45FLC-21A | 1160 | DETECTOR | FIRE DETECTOR-TURBINE COMPARTMENT | 24 | 1 | 429 |  | 361A2285P007 | 429 | 429
158 | G45FLC-21B | 1160 | DETECTOR | FIRE DETECTOR-TURBINE COMPARTMENT | 24 | 1 | 429 |  | 361A2285P007 | 429 | 429
159 | G45FT-1A | 1103 | DETECTOR | FIRE DETECTOR-TURBINE COMPARTMENT | 24 | 1 | 429 |  | 361A2285P007 | 429 | 429
160 | G45FT-1B | 1103 | DETECTOR | FIRE DETECTOR-TURBINE COMPARTMENT | 24 | 1 | 429 |  | 361A2285P007 | 429 | 429
161 | G45FT-2A | 1154 | DETECTOR | FIRE DETECTOR-TURBINE COMPARTMENT | 24 | 1 | 429 |  | 361A2285P007 | 429 | 429
162 | G45FT-2B | 1154 | DETECTOR | FIRE DETECTOR-TURBINE COMPARTMENT | 24 | 1 | 429 |  | 361A2285P007 | 429 | 429
163 | G45FT-3A | 1154 | DETECTOR | FIRE DETECTOR-TURBINE COMPARTMENT | 24 | 1 | 429 |  | 361A2285P007 | 429 | 429
164 | G45FT-3B | 1154 | DETECTOR | FIRE DETECTOR-TURBINE COMPARTMENT | 24 | 1 | 429 |  | 361A2285P007 | 429 | 429
165 | G63EA-1 | 559 | SW-PRESS | EXHAUST DUCT PRESSURE HIGH SWITCH | 10 | 1 | 299.25 |  | 355A7420P001 | 299.25 | 299.25
166 | G63ET-1 | 559 | SW-PRESS | EXHAUST DUCT PRESSURE HIGH HIGH | 10 | 1 | 299.25 |  | 355A7420P001 | 299.25 | 299.25
167 | G63ET-2 | 559 | SW-PRESS | EXHAUST DUCT PRESSURE HIGH HIGH | 10 | 1 | 299.25 |  | 355A7420P001 | 299.25 | 299.25
168 | G63HF-1 | 926 | SWITCH | HYD FLTR DFFRNTL PRSSR ALARM | 9 | 1 | 501.11 |  | 351A9091P002 | 501.11 | 501.11
169 | G63HQ-1 | 926 | SWITCH | LO HYD SPPL PRSSP-AUX HYD PMP STRT | 13 | 1 | 283 |  | 351A9090P020 | 283 | 283
170 | G63QA-1 | 926 | SWITCH | LOW LUBE OIL PRESS-AUX PUMP START | 13 | 1 | 260 |  | 351A9090P018 | 260 | 260
171 | G63QQ-1 | 926 | SWITCH | MN LUB OIL FLTR DFFRNTL PRESS-ALARM | 13 | 1 | 416 |  | 351A9091P010 | 416 | 416
172 | G65GC-1 | 509 | VLV-SERVO | GAS CNTRL VLV SRVO VLV | 3 | 1 | 2537.81 |  | 312A6077P008 | 2537.81 | 2537.81
173 | G65GS-1 | 565 | VLV-SERVO | GAS FUEL SPLITTER VALVE SERVO VALVE | 12 | 1 | 2467.25 |  | 312A6077P002 | 2467.25 | 2467.25
174 | G77RP11 | 235 | INDICATOR | KEYPHASOR BRG #1 (INDICATOR) | 7 | 1 | 272.9 |  | 109E3763P300 | 272.9 | 272.9
175 | G90SR-1 | 507 | VLV-SERVO | STOP/SPEED (PRESS) RATIO SERVO VLV | 3 | 1 | 2537.81 |  | 312A6077P008 | 2537.81 | 2537.81
176 | G96AP-1A | 559 | TRANSMITTER | BAROMETRIC PRESSURE TRANSMITTER | 12 | 1 | 1383.9 |  | 353A4330P021 | 1383.9 | 1383.9
177 | G96AP-1B | 559 | TRANSMITTER | BAROMETRIC PRESSURE TRANSMITTER | 12 | 1 | 1383.9 |  | 353A4330P021 | 1383.9 | 1383.9
178 | G96AP-1C | 559 | TRANSMITTER | BAROMETRIC PRESSURE TRANSMITTER | 12 | 1 | 1383.9 |  | 353A4330P021 | 1383.9 | 1383.9
179 | G96BD-1 | 559 | TRANSMITTER | TRB CMPR INLT BLMTH DIFF PR TRNSMTR | 12 | 1 | 2562 |  | 353A4330P013 | 2562 | 2562
180 | G96CS-1 | 559 | TRANSMITTER | INLET AIR TOTAL PRSSR TRNSMTTR | 8 | 1 | 2469 |  | 353A4330P009 | 2469 | 2469
181 | G96EP-1 | 559 | TRANSMITTER | EXHAUST PRESSURE TRANSMITTER | 8 | 1 | 2400.3 |  | 353A4330P010 | 2400.3 | 2400.3
182 | G96FF-1 | 639 | TRANSMITTER | FUEL GAS FLOW ORIFICE DIFF PRESSURE | 12 | 1 | 2696.57 |  | 353A4330P012 | 2696.57 | 2696.57
183 | G96FF-2 | 639 | TRANSMITTER | FUEL GAS FLOW ORIFICE DIFF PRESSURE | 12 | 1 | 2562 |  | 353A4330P013 | 2562 | 2562
184 | G96FG-1 | 639 | TRANSMITTER | FUEL GAS FLW ORFC UPSTRM PRS XMTR | 12 | 1 | 1549.97 |  | 353A4330P005 | 1549.97 | 1549.97
185 | G96GC-5 | 509 | TRANSDUCER | GAS CONTROL VALVE LVDT | 18 | 1 | 1507.63 |  | 311A5178P006 | 1507.63 | 1507.63
186 | G96GC-6 | 509 | TRANSDUCER | GAS CONTROL VALVE LVDT | 18 | 1 | 1507.63 |  | 311A5178P006 | 1507.63 | 1507.63
187 | G96GS-1 | 564 | TRANSDUCER | GAS FUEL SPLITTER VALVE LVDT | 12 | 1 | 2927.06 |  | 311A5178P023 | 2927.06 | 2927.06
188 | G96GS-2 | 564 | TRANSDUCER | GAS FUEL SPLITTER VALVE LVDT | 12 | 1 | 2927.06 |  | 311A5178P023 | 2927.06 | 2927.06
189 | G96SR-1 | 507 | TRANSDUCER | STOP/SPEED RATIO VALVE LVDT | 12 | 1 | 1771.35 |  | 311A5178P024 | 1771.35 | 1771.35
190 | G96SR-2 | 507 | TRANSDUCER | STOP/SPEED RATIO VALVE LVDT | 12 | 1 | 1771.35 |  | 311A5178P024 | 1771.35 | 1771.35
191 | G96TV-1 | 548 | TRANSDUCER | TURB INLET GUIDE VANE LVDT | 20 | 1 | 1515.86 |  | 311A5178P011 | 1515.86 | 1515.86
192 | G96TV-2 | 548 | TRANSDUCER | TURB INLET GUIDE VANE LVDT | 20 | 1 | 1515.86 |  | 311A5178P011 | 1515.86 | 1515.86
193 | G96VC11 | 235 | TRANSMITTER | SHAFT AXIAL POS TRANSMITTER, BRNG 1 | 4 | 1 | 660.45 |  | 109E3763P950 | 660.45 | 660.45
194 | G96VC12 | 235 | TRANSMITTER | SHAFT AXIAL POS TRANSMITTER, BRNG 1 | 4 | 1 | 660.45 |  | 109E3763P950 | 660.45 | 660.45
195 | GA1220A |  | GASKET | SENSOR ARR,HUMDTY, GSKT, SENSOR ASM | 6 | 1 | 63.79 |  | 315A2005P001 | 63.79 | 63.79
196 | GA1220G |  | WASHER-LCK | SENSOR ARR,HUMDTY,WSHR,SENSOR ASM | 4 | 8 | 2.84 |  | N405P00073 | 2.84 | 22.72
197 | GA12504 |  | VLV-BALL | PP ARR,LO FLSH-FLD,VLV,#2 BRG DRAIN | 8 | 6 | 491.45 |  | 275A8828P006 | 491.45 | 2948.7
198 | GA12509 |  | VLV-BALL | PP ARR,LO FLSH-FLD,VLV,#3 BRG DRAIN | 12 | 1 | 330.86 |  | 275A8828P003 | 330.86 | 330.86
199 | GA1251E |  | VLV-BALL | PP ARR, LO FLSH-FLD, BALL VALVE | 11 | 1 | 179.92 |  | 275A8828P002 | 179.92 | 179.92
200 | GA1251J |  | STRAINER | PP ARR, LO FLSH-FLD, STRAINER | 9 | 1 | 70.56 |  | 351A3480P007 | 70.56 | 70.56
201 | GA1251JR |  | STRAINER | PP ARR, LO FLSH-FLD, STRAINER, REPL | 14 | 1 | 73.08 |  | 351A3480P057 | 73.08 | 73.08
202 | GA1251K |  | STRAINER | PP ARR, LO FLSH-FLD, STRAINER | 9 | 1 | 44.3 |  | 351A3480P005 | 44.3 | 44.3
203 | GA1251KR |  | STRAINER | PP ARR, LO FLSH-FLD, STRAINER, REPL | 5 | 2 | 23.68 |  | 351A3480P055 | 23.68 | 47.36
204 | GA1251L |  | STRAINER | PP ARR, LO FLSH-FLD, STRAINER | 5 | 2 | 64.05 |  | 351A3480P058 | 64.05 | 128.1
205 | GBTJ11A&B | 235 | TCPL | TCPL BRG METAL TEMP | 13 | 1 | 158.55 |  | 361A2373G001 | 158.55 | 158.55
206 | GBTJ12A&B | 235 | TCPL | TCPL BRG METAL TEMP | 13 | 1 | 158.55 |  | 361A2373G001 | 158.55 | 158.55
207 | GBTJ21A&B | 235 | TCPL | TCPL BRG METAL TEMP A, BRNG 2 | 13 | 1 | 158.55 |  | 361A2373G001 | 158.55 | 158.55
208 | GBTJ22A&B | 235 | TCPL | TCPL BRG METAL TEMP A, BRNG 2 | 13 | 1 | 158.55 |  | 361A2373G001 | 158.55 | 158.55
209 | GBTJ31A&B | 235 | TCPL | BEARING METAL TEMP | 13 | 1 | 158.55 |  | 361A2373G001 | 158.55 | 158.55
210 | GBTJ32A&B | 235 | TCPL | BEARING METAL TEMP | 13 | 1 | 158.55 |  | 361A2373G001 | 158.55 | 158.55
211 | GBTTA11A&B | 235 | TCPL | TCPL BRG METAL TEMP - THRUST ACTIVE | 13 | 1 | 158.55 |  | 361A2373G001 | 158.55 | 158.55
212 | GBTTA12A&B | 235 | TCPL | TCPL BRG METAL TEMP - THRUST ACTIVE | 13 | 1 | 158.55 |  | 361A2373G001 | 158.55 | 158.55
213 | GBTTI11A&B | 235 | TCPL | TCPL BRG METAL TMP - THRUST INACTVE | 13 | 1 | 158.55 |  | 361A2373G001 | 158.55 | 158.55
214 | GBTTI12A&B | 235 | TCPL | TCPL BRG METAL TMP - THRUST INACTVE | 13 | 1 | 158.55 |  | 361A2373G001 | 158.55 | 158.55
215 | GCT-DA-1 | 637 | TCPL | TCPL, COMPRESSOR DISCHARGE TEMP 1 | 14 | 1 | 773.85 |  | 361A2289P208 | 773.85 | 773.85
216 | GCT-DA-2 | 637 | TCPL | TCPL, COMPRESSOR DISCHARGE TEMP 2 | 14 | 1 | 773.85 |  | 361A2289P208 | 773.85 | 773.85
217 | GCT-DA-3 | 637 | TCPL | TCPL, COMPRESSOR DISCHARGE TEMP 3 | 14 | 1 | 773.85 |  | 361A2289P208 | 773.85 | 773.85
218 | GCTIF1A&B | 637 | TCPL | COMP. INLET THERMOCOUPLE | 11 | 1 | 276.52 |  | 351A3445P023 | 276.52 | 276.52
219 | GCTIF2A&B | 637 | TCPL | COMP. INLET THERMOCOUPLE | 11 | 1 | 276.52 |  | 351A3445P023 | 276.52 | 276.52
220 | GCT-IF-3/R | 637 | RTD | COMP. INLET DETECTOR | 11 | 1 | 224.6 |  | 351A9616P001 | 224.6 | 224.6
221 | GFH14-1 | 564 | FILTER | HYDRAULIC SUPPLY FILTER-SPLITTR VLV | 12 | 1 | 878.85 |  | 315A2660P001 | 878.85 | 878.85
222 | GFH6-1 | 548 | FILTER | IGV SERVO HYDRAULIC SUPPLY FILTER | 12 | 1 | 878.85 |  | 315A2660P001 | 878.85 | 878.85
223 | GFH7-1 | 507 | FILTER | FUEL GAS SRVO HYD OIL SUPPLY FILTER | 12 | 1 | 878.85 |  | 315A2660P001 | 878.85 | 878.85
224 | GFH8-1 | 509 | FILTER | GAS FUEL SERVO HYDRLC SUPPLY FILTER | 12 | 1 | 878.85 |  | 315A2660P001 | 878.85 | 878.85
225 | GFT-GI-1 | 639 | TCPL | FUEL GAS TEMP SENSOR | 10 | 1 | 309.12 |  | 351A3445P001 | 309.12 | 309.12
226 | GLTB1D1A&B | 637 | TCPL | LO THERMOCOUPLE NO 1 BRNG DRAIN | 10 | 1 | 322.4 |  | 351A3445P002 | 322.4 | 322.4
227 | GLTB2D1A&B | 637 | TCPL | LO THERMOCOUPLE NO2 BRNG DRAIN | 10 | 1 | 322.4 |  | 351A3445P002 | 322.4 | 322.4
228 | GLTB3D1A&B | 637 | TCPL | LO THERMOCOUPLE NO3 BRNG DRAIN | 10 | 1 | 322.4 |  | 351A3445P002 | 322.4 | 322.4
229 | GLTTH1A&B | 637 | TCPL | LO THERMOCOUPLE TURBINE HEADER | 10 | 1 | 316.37 |  | 351A3445P003 | 316.37 | 316.37
230 | GTT-IB-1 | 637 | TCPL | TCPL,TURB TEMP INNER BARREL | 14 | 1 | 356.21 |  | 351A3488P003 | 356.21 | 356.21
231 | GTT-IB-2 | 637 | TCPL | TCPL,TURB TEMP INNER BARREL | 14 | 1 | 356.21 |  | 351A3488P003 | 356.21 | 356.21
232 | GTT-IB-3 | 637 | TCPL | TCPL,TURB TEMP INNER BARREL | 14 | 3 | 356.21 |  | 351A3488P003 | 356.21 | 1068.63
233 | GTT-WS1AO-1 | 637 | TCPL | TCPL, WHLSPC -STG 1 AFT OUTER -1 | 14 | 1 | 732.9 |  | 361A2289P333 | 732.9 | 732.9
234 | GTT-WS1AO-2 | 637 | TCPL | TCPL, WHLSPC -STG 1 AFT OUTER -2 | 14 | 1 | 732.9 |  | 361A2289P333 | 732.9 | 732.9
235 | GTT-WS1FI-1 | 637 | TCPL | TURB TEMP, WLSPC STG-1 FWD INR -1 | 14 | 1 | 732.9 |  | 361A2289P367 | 732.9 | 732.9
236 | GTT-WS1FI-2 | 637 | TCPL | TURB TEMP, WLSPC STG-1 FWD INR -2 | 14 | 1 | 732.9 |  | 361A2289P367 | 732.9 | 732.9
237 | GTT-WS2AO-1 | 637 | TCPL | TCPL, WHLSPC -STG 2 AFT OUTER -1 | 14 | 1 | 732.9 |  | 361A2289P336 | 732.9 | 732.9
238 | GTT-WS2AO-2 | 637 | TCPL | TCPL, WHLSPC -STG 2 AFT OUTER -2 | 14 | 1 | 732.9 |  | 361A2289P336 | 732.9 | 732.9
239 | GTT-WS2FO-1 | 637 | TCPL | TCPL, WHLSPC -STG 2 FWD OUTER -1 | 14 | 1 | 732.9 |  | 361A2289P329 | 732.9 | 732.9
240 | GTT-WS2FO-2 | 637 | TCPL | TCPL, WHLSPC -STG 2 FWD OUTER -2 | 14 | 1 | 732.9 |  | 361A2289P329 | 732.9 | 732.9
241 | GTT-WS3AO-1 | 637 | TCPL | TCPL, WHLSPC -STG 3 AFT OUTER -1 | 10 | 1 | 380.36 |  | 351A3488P005 | 380.36 | 380.36
242 | GTT-WS3AO-2 | 637 | TCPL | TCPL, WHLSPC -STG 3 AFT OUTER -2 | 10 | 1 | 380.36 |  | 351A3488P005 | 380.36 | 380.36
243 | GTT-WS3FO-1 | 637 | TCPL | TCPL, WHLSPC -STG 3 FWD OUTER -1 | 14 | 1 | 732.9 |  | 361A2289P333 | 732.9 | 732.9
244 | GTT-WS3FO-2 | 637 | TCPL | TCPL, WHLSPC -STG 3 FWD OUTER -2 | 14 | 1 | 732.9 |  | 361A2289P333 | 732.9 | 732.9
245 | GVAB1-1 | 947 | VLV-BLEED | HYDRAULC SYSTEM AIR BLEED VLV(MAIN) | 10 | 1 | 298.25 |  | 185A1527P001 | 298.25 | 298.25
246 | GVAB2-1 | 947 | VLV-BLEED | HYDRAULC SYSTEM AIR BLEED VLV (AUX) | 10 | 1 | 298.25 |  | 185A1527P001 | 298.25 | 298.25
247 | GVCK3-1 | 947 | VLV-CHECK | HYDRAULIC PUMP CHECK VALVE | 10 | 1 | 312.74 |  | 185A1526P003 | 312.74 | 312.74
248 | GVCK3-2 | 947 | VLV-CHECK | HYDRAULIC PUMP CHECK VALVE | 10 | 1 | 312.74 |  | 185A1526P003 | 312.74 | 312.74
249 | GVH5-1 | 507 | VALVE | STOP/SPEED RATIO VALVE, DUMP VALVE | 16 | 1 | 4113.65 |  | 166D1585G001 | 4113.65 | 4113.65
250 | GVR21-1 | 947 | VLV-RELIEF | MAIN HYD SPPLY PMP PRESS RELIEF VLV | 14 | 1 | 1252.44 |  | 185A1525P007 | 1252.44 | 1252.44
251 | GVR22-1 | 947 | VLV-RELIEF | AUX HYD SPPLY PMP PRESS RELIEF VLV | 14 | 1 | 1252.44 |  | 185A1525P007 | 1252.44 | 1252.44

## Mark V TMR
[7 empty] | List Total: |  |  |  | List Total: | Credit Total
[7 empty] | 127090.42 |  |  |  | 127435.42 | 0
MARK V TMR Spares
LINE | CATALOG | CAT | [6 empty] | SIMILAR-TO | UNIT
ITEM | NUMBER | LOC | PART NAME | PART DESCRIPTION | CYC | QTY | SYS PRICE | UM | DWG NUMBER | PRICE | LINE PRICE
____________
1 |  |  |  | TERMINATOR (93 OHMS) | 10 | 1 | 29 |  | 278A3360P9 | 29 | 29
2 |  |  |  | 2AG FUSE 1.5A,250V | 6 | 10 | 3 |  | 104X109AD 109 | 3 | 30
3 |  |  |  | RES 50 5% 40W WW | 12 | 1 | 33 |  | 104X123DE 016 | 33 | 33
4 |  |  |  | DIODE MOD,1200V-45A,SKKD46/12 | 5 | 1 | 50 |  | 104X125DC 014 | 50 | 50
5 |  |  |  | KEYPAD | 12 | 1 | 81.9 |  | 104X152AE 002 | 81.9 | 81.9
6 |  |  |  | SHUNT | 12 | 1 | 8 |  | 232A6552G1 | 8 | 8
7 |  |  |  | GROUND STRAP 7 INCH | 12 | 1 | 12 |  | 232A6552G3 | 12 | 12
8 |  |  |  | ARCNET CONTRL BD | 9 | 1 | 825 |  | 278A2181VRP3 | 825 | 825
9 |  |  |  | PRINTER RIBBON/CARTRIDGE | 5 | 1 | 113.7 |  | 278A2181VVP1A | 113.7 | 113.7
10 |  |  |  | RESISTOR | 12 | 1 | 15.95 |  | 323A2354P1 | 15.95 | 15.95
11 |  |  |  | RESISTOR | 12 | 1 | 59 |  | 323A2354P2 | 59 | 59
12 |  |  |  | FUSE (5 A) | 7 | 10 | 4 |  | 323A2357P1 | 4 | 40
13 |  |  |  | FUSE (7 A) | 7 | 10 | 4 |  | 323A2357P2 | 4 | 40
14 |  |  |  | FUSE (1.5A) | 6 | 10 | 4 |  | 323A2357P21 | 4 | 40
15 |  |  |  | FUSE (10A) | 7 | 10 | 4 |  | 323A2357P3 | 4 | 40
16 |  |  |  | FUSE (15A) | 7 | 10 | 4 |  | 323A2357P4 | 4 | 40
17 |  |  |  | FUSE 5 A | 7 | 10 | 6 |  | 323A2396P155 | 6 | 60
18 |  |  |  | FUSE 8 A | 7 | 10 | 6 |  | 323A2396P18 | 6 | 60
19 |  |  |  | FUSE 3.2A/250V, SLO-BLOW | 5 | 10 | 3 |  | 323A2396P81 | 3 | 30
20 |  |  |  | COMP ENET ADAPTER | 8 | 1 | 746 |  | 323A4747ETP6 | 746 | 746
21 |  |  |  | CAP-METALLIZED-MYLAR | 15 | 1 | 29 |  | 68A7052P1B10 | 29 | 29
22 |  |  |  | RELAY, DPDT, SEALED, NO LAMP | 23 | 1 | 12 |  | 68A9663PDC24XN | 12 | 12
23 |  |  |  | 30A FILTER | 12 | 1 | 245 |  | COR#30ESK6 | 245 | 245
24 |  |  |  | TERM. BD (C) | 8 | 1 | 4486.15 |  | DS200CTBAG1A | 4486.15 | 4486.15
25 |  |  |  | TERM. DIGITAL CONT. IN | 7 | 1 | 4486.15 |  | DS200DTBAG1A | 4486.15 | 4486.15
26 |  |  |  | TERM. BD DIGITAL CONT. IN | 7 | 1 | 4486.15 |  | DS200DTBBG1A | 4486.15 | 4486.15
27 |  |  |  | TERM. BD RLY/SOLENOID | 7 | 1 | 4486.15 |  | DS200DTBCG1A | 4486.15 | 4486.15
28 |  |  |  | TERM. BD RLY SOLENOID | 7 | 1 | 3901 |  | DS200DTBDG1A | 3901 | 3901
29 |  |  |  | TERMINATION BD.<P> MODULE | 9 | 1 | 4300.85 |  | DS200PTBAG1B | 4300.85 | 4300.85
30 |  |  |  | TERM. BOARD (R-S-T) | 8 | 1 | 4486.15 |  | DS200QTBAG1A | 4486.15 | 4486.15
31 |  |  |  | DRIVE CONTROL CARD | 8 | 1 | 5673 |  | DS200SDCCG4A | 5673 | 5673
32 |  |  |  | LAN COMM CARD | 7 | 1 | 7652.1 |  | DS200SLCCG3A | 7652.1 | 7652.1
33 |  |  |  | TERM. BD (C) ANALOG I/O | 7 | 1 | 4486.15 |  | DS200TBCAG1A | 4486.15 | 4486.15
34 |  |  |  | TERM.BD (C)R-S-T TC I/O | 7 | 1 | 4486.15 |  | DS200TBQAG1A | 4486.15 | 4486.15
35 |  |  |  | TERM BD(R-S-T) ANALOG I/O | 7 | 1 | 4486.15 |  | DS200TBQBG1A | 4486.15 | 4486.15
36 |  |  |  | TC2000 COMMON ANALOG I/O | 8 | 1 | 5192.25 |  | DS200TCCAG1B | 5192.25 | 5192.25
37 |  |  |  | DIG. I/O BD. CONF. COAT | 10 | 1 | 5005 |  | DS200TCDAH1BGD | 5005 | 5005
38 |  |  |  | EMERGENCY OVER SPEED BOARD | 8 | 1 | 7409.45 |  | DS200TCEAG1B | 7409.45 | 7409.45
39 |  |  |  | COMM. CIRCUITS FOR THE EOS BD. | 9 | 1 | 7955.82 |  | DS200TCEBG1B | 7955.82 | 7955.82
40 |  |  |  | POWER DISTRIBUTION MODULE | 7 | 1 | 5768.4 |  | DS200TCPDG1B | 5768.4 | 5768.4
41 |  |  |  | DC INPUT PWR SUPPLY BOARD | 8 | 1 | 7409.45 |  | DS200TCPSG1A | 7409.45 | 7409.45
42 |  |  |  | (RST) ANALOG I/O BOARD | 8 | 1 | 7409.45 |  | DS200TCQAG1B | 7409.45 | 7409.45
43 |  |  |  | (RST) OVERFLOW BOARD | 8 | 1 | 7409.45 |  | DS200TCQCG1B | 7409.45 | 7409.45
44 |  |  |  | RELAY OUTPUT BOARD | 7 | 1 | 6338.65 |  | DS200TCRAG1A | 6338.65 | 6338.65
45 |  |  |  | GT TMR/SIMPLEX TRIP BD | 7 | 1 | 6891.8 |  | DS200TCTGG1A | 6891.8 | 6891.8
46 |  |  |  | MOV | 4 | 2 | 3 |  | PDVR1000P001 | 3 | 6
47 |  |  |  | SILCONE FLAME DETECTOR | 8 | 1 | 551 |  | REU#FSM-1002-002 | 551 | 551
48 |  |  |  | CONTACT BLOCK | 7 | 1 | 33 |  | TQI#ZB2BZ104 | 33 | 33

## Gen Excitation
[7 empty] | List Total: |  |  |  | List Total: | Credit Total
[7 empty] | 66337.64 |  |  |  | 66343.64 | 0
Generator Excitation
LINE | CATALOG | CAT | [6 empty] | SIMILAR-TO | UNIT
ITEM | NUMBER | LOC | PART NAME | PART DESCRIPTION | CYC | QTY | SYS PRICE | UM | DWG NUMBER | PRICE | LINE PRICE
____________
1 |  |  | BOARD | ACDC2000 TERMINAL BOARD | 6 | 1 | 5236.73 |  | 531X305NTBANG1 | 5236.73 | 5236.73
2 |  |  | BREAKER | BREAKER | 5 | 1 | 231 |  | TED124030WL | 231 | 231
3 |  |  | BREAKER | BREAKER | 5 | 1 | 399 |  | TED136030WL | 399 | 399
4 |  |  | CAP | CAP 1MF 2000VAC 10% P/PLYPROP | 15 | 1 | 58 |  | 104X122AA 452 | 58 | 58
5 |  |  | CAP | CAP 1700 500V 30% ELEC ALUM | 14 | 1 | 218.56 |  | PDCA1001J17P50 | 218.56 | 218.56
6 |  |  | CAP | CAP .1 100V 10% CERAMIC | 8 | 1 | 3 |  | PDCC1000F10P10B | 3 | 3
7 |  |  | CAPACITOR | CAPACITOR,.1MFD 1500VAC 5% | 18 | 1 | 64.26 |  | 104X122AA 448 | 64.26 | 64.26
8 |  |  | CARD | I/O TB CARD | 11 | 1 | 4631 |  | 531X307LTBAJG1 | 4631 | 4631
9 |  |  | CARD | ARCNET CARD | 8 | 1 | 1058 |  | DS200ACNAG1A | 1058 | 1058
10 |  |  | CARD | IGBT AA/AB SNUBBER CARD | 9 | 1 | 6544.44 |  | DS200IAXSG1A | 6544.44 | 6544.44
11 |  |  | CARD | DRIVE LAN/CTRL CD. | 10 | 1 | 5382 |  | DS200LDCCH1AHA | 5382 | 5382
12 |  |  | CARD | RELAY CARD | 8 | 1 | 4230 |  | DS200RTBAG2A | 4230 | 4230
13 |  |  | CARD | TC2000 (C) EXP. ANALOG I | 8 | 1 | 6958 |  | DS200TCCBG3B | 6958 | 6958
14 |  |  | CONDITIONER | SIGNAL CONDITIONER | 7 | 1 | 4193 |  | DS200PTCTG1B | 4193 | 4193
15 |  |  | CONT | CONT | 13 | 1 | 1359 |  | DS303A2C01FXA021XH | 1359 | 1359
16 |  |  | DRIVER | EX2000 PWM GATE DR. & DD | 8 | 1 | 5211 |  | IS200GDDDG1A | 5211 | 5211
17 |  |  | DRIVER | EX2000 PWM PS & CONT. DR | 9 | 1 | 5189.69 |  | IS200PSCDG1A | 5189.69 | 5189.69
18 |  |  | FUSE | 2AG FUSE 0.5A,250V | 6 | 1 | 3 |  | 104X109AD 102 | 3 | 3
19 |  |  | FUSE | 2AG FUSE 1.0A,250V | 7 | 1 | 3 |  | 104X109AD 103 | 3 | 3
20 |  |  | FUSE | 2AG FUSE 3.0A,250V | 11 | 1 | 5.51 |  | 104X109AD 104 | 5.51 | 5.51
21 |  |  | FUSE | FUSE 7 A | 7 | 2 | 6 |  | 323A2396P157 | 6 | 12
22 |  |  | MODULE | DIODE MODULE | 13 | 1 | 309.12 |  | 104X125DC 015 | 309.12 | 309.12
23 |  |  | MOV | MOV | 15 | 1 | 632.73 |  | V511BA60 | 632.73 | 632.73
24 |  |  | REACTOR | D. C. REACTOR | 9 | 1 | 1186.65 |  | 237B6174G1 | 1186.65 | 1186.65
25 |  |  | RES | RES 50 5% 40W WW | 16 | 1 | 52 |  | 104X123DE 018 | 52 | 52
26 |  |  | RES | RES 5K 5% 40W WIRE LEAD | 4 | 1 | 25.2 |  | 323A2354P33 | 25.2 | 25.2
27 |  |  | RES | LGH 4 RES | 9 | 1 | 84 |  | IC9033A4H7 | 84 | 84
28 |  |  | RESISTOR | RESISTOR | 4 | 1 | 22.05 |  | 323A2354P3 | 22.05 | 22.05
29 |  |  | SENSOR | TEMP. SENSOR,AX FRAME | 4 | 1 | 12971.7 |  | 323A5758G1 | 12971.7 | 12971.7
30 |  |  | SHUNT | SHUNT 100MV 15A | 7 | 1 | 41 |  | 323A2440P15 | 41 | 41
31 |  |  | TERMINATOR | TERMINATOR (93 OHMS) | 10 | 1 | 29 |  | 278A3360P9 | 29 | 29

## Gen Consumables
[7 empty] | List Total: |  |  |  | List Total: | Credit Total
[7 empty] | 5515.1 |  |  |  | 9491.61 | 0
Generator Consumable
LINE | CATALOG | CAT | [6 empty] | SIMILAR-TO | UNIT
ITEM | NUMBER | LOC | PART NAME | PART DESCRIPTION | CYC | QTY | SYS PRICE | UM | DWG NUMBER | PRICE | LINE PRICE
____________
1 |  |  | BAL WGT ASM (0.75 OZ/IN) | ROTOR ASSY | 8 | 6 | 159.39 |  | 0438B758G0001 | 159.39 | 956.34
2 |  |  | BALANCE WEIGHTS | ROTOR ASSY | 17 | 1 | 4688.71 |  | 0699L984G0001 | 4688.71 | 4688.71
3 |  |  | BREATHER CAP | PIPING HARDWARE | 12 | 2 | 165.43 |  | 323B5821P0002 | 165.43 | 330.86
4 |  |  | CARBON BRUSH (W/PIGTAIL) | GROUND BRUSH RIGGING | 13 | 4 | 30.33 |  | 323B7989P0008 | 30.33 | 121.32
5 |  |  | GASKET | BASE ASSY | 5 | 2 | 9.24 |  | 314A2518P0001 | 9.24 | 18.48
6 |  |  | GASKET | BASE ASSY | 6 | 1 | 5.88 |  | 314A2553P0001 | 5.88 | 5.88
7 |  |  | GASKET | BASE ASSY | 6 | 60 | 1.68 |  | 0659A937P0017 | 1.68 | 100.8
8 |  |  | GASKET | OUTER FRAME | 5 | 20 | 0.42 |  | 0659A937P0036 | 0.42 | 8.4
9 |  |  | GASKET | OUTER FRAME | 6 | 2 | 14.28 |  | 341A1811P0001 | 14.28 | 28.56
10 |  |  | GASKET | WEB SUPPORT | 6 | 20 | 0.74 |  | 0659A937P0018 | 0.74 | 14.8
11 |  |  | GASKET | SHP LSE TW/BR/GL/GSHMS | 6 | 2 | 14.28 |  | 341A1811P0001 | 14.28 | 28.56
12 |  |  | GASKET | LINE BOX INSERT | 6 | 2 | 4.83 |  | 236B5451P0001 | 4.83 | 9.66
13 |  |  | GASKET | LINE BOX INSERT | 6 | 2 | 3.99 |  | 236B5451P0002 | 3.99 | 7.98
14 |  |  | GASKET(.25TX2.25WX30.50L) | COOL-PKG ASSY | 6 | 8 | 28.07 |  | 224B4026P0002 | 28.07 | 224.56
15 |  |  | GASKET(.25TX2.25WX33.00L) | COOL-PKG ASSY | 6 | 8 | 35.3 |  | 224B4026P0003 | 35.3 | 282.4
16 |  |  | GASKET,HEATER FLANGE | OUTER FRAME | 6 | 2 | 15.86 |  | 341A4032P0001 | 15.86 | 31.72
17 |  |  | GASKET-EDGE SEAL | ORT AIR SHLD/OV | 8 | 21 | 15.26 |  | 341A1812P0001 | 15.26 | 320.46
18 |  |  | GASKET-NEOPRENE(.50X3.00) | OUTER FRAME | 6 | 160 | 2.52 |  | 313A7331P0001 | 2.52 | 403.2
19 |  |  | GASKET-NEOPRENE(.50X3.00) | CE SEALING | 6 | 1 | 2.52 |  | 313A7331P0001 | 2.52 | 2.52
20 |  |  | GASKET-NEOPRENE(.50X3.00) | SHP LSE TW/BR/GL/GSHMS | 6 | 110 | 2.52 |  | 313A7331P0001 | 2.52 | 277.2
21 |  |  | GASKET-NEOPRENE(1.00X1.25 | TE-SEALING | 4 | 20 | 10.4 |  | 313A7331P0003 | 10.4 | 208
22 |  |  | GASKET-NEOPRENE(1.00X1.25 | CE SEALING | 4 | 20 | 10.4 |  | 313A7331P0003 | 10.4 | 208
23 |  |  | GASKET-SPIRAL WOUND(2.00) | OUTER FRAME | 6 | 2 | 6.09 |  | N5605P02001C1 | 6.09 | 12.18
24 |  |  | GASKET-SPIRAL WOUND(2.00) | MIST ELIMI FIELD MOD | 6 | 1 | 11.76 |  | N5605P02001G1 | 11.76 | 11.76
25 |  |  | GEN/BASE GASKET | GEN FINAL ASSY | 18 | 1 | 242.55 |  | 108E3072G0008 | 242.55 | 242.55
26 |  |  | LINE LEAD SEAL | LINE BOX INSERT | 6 | 3 | 6.93 |  | 341A6408P0001 | 6.93 | 20.79
27 |  |  | SEAL | STA FRM SEAL | 6 | 50 | 12.86 |  | 313A7323P0001 | 12.86 | 643
28 |  |  | SEAL | COOL-PKG ASSY | 6 | 22 | 12.86 |  | 313A7323P0001 | 12.86 | 282.92

## Gen Capitals
[7 empty] | List Total: |  |  |  | List Total: | Credit Total
[7 empty] | 181515.55 |  |  |  | 294564.61 | 0
Generator Capital
LINE | CATALOG | CAT | [6 empty] | SIMILAR-TO | UNIT
ITEM | NUMBER | LOC | PART NAME | PART DESCRIPTION | CYC | QTY | SYS PRICE | UM | DWG NUMBER | PRICE | LINE PRICE
____________
1 |  |  | CURRENT XFMR | 1 SET CURRENT TRANSFORMERS | 10 | 6 | 1606.42 |  | 196C7940P0015 | 1606.42 | 9638.52
2 |  |  | LINING CE | PED ASSY CE EPOXY | 16 | 1 | 41945.4 |  | 0966E946P0022 | 41945.4 | 41945.4
3 |  |  | LINING TE | PED ASSY TE EPOXY | 16 | 1 | 39388.65 |  | 0966E946P0021 | 39388.65 | 39388.65
4 |  |  | NEUT GRD RES | B9Y ACCESSORIES | 8 | 1 | 3120.6 |  | 314A4813P0001 | 3120.6 | 3120.6
5 |  |  | NEUT GRD XFM | B9Y ACCESSORIES | 7 | 1 | 3017.62 |  | 314A4814P0001 | 3017.62 | 3017.62
6 |  |  | RETAINING RING | ROTOR ASSY | 26 | 2 | 84138.6 |  | 190D4458P0001 | 84138.6 | 168277.2
7 |  |  | RTD-7A7 SLOT | STATOR WIRING RTDS | 7 | 12 | 475.76 |  | U7357S082P0394518 | 475.76 | 5709.12
8 |  |  | STATOR BARS TOP BAR | STATOR ASSY | 11 | 3 | 7822.5 |  | 104E4211G0001 | 7822.5 | 23467.5

## Gen Maintenance
[7 empty] | List Total: |  |  |  | List Total: | Credit Total
[7 empty] | 44050.75 |  |  |  | 86576.43 | 0
Generator Maintenance
LINE | CATALOG | CAT | [6 empty] | SIMILAR-TO | UNIT
ITEM | NUMBER | LOC | PART NAME | PART DESCRIPTION | CYC | QTY | SYS PRICE | UM | DWG NUMBER | PRICE | LINE PRICE
____________
1 |  |  | 7A6 BRG. PAD SET (5) | BEARING | 20 | 2 | 15531.6 |  | 196C8937P0004 | 15531.6 | 31063.2
2 |  |  | AIR FILTER ASSY | OP480 BRLS EXTR DUCT | 12 | 1 | 3346.35 |  | 341A6523P0001 | 3346.35 | 3346.35
3 |  |  | BEARING SEAL 7A6 | BEARING | 8 | 2 | 532.51 |  | 196C8937P0001 | 532.51 | 1065.02
4 |  |  | BENTLY NEVADA PROBE-3300 | GEN FINAL ASSY | 14 | 2 | 1043.7 |  | 0699L971G0005 | 1043.7 | 2087.4
5 |  |  | BRUSH HOLDER ASM SINGLE | MONITOR BRUSH RIGGING | 19 | 4 | 607.95 |  | 0328B691G0012 | 607.95 | 2431.8
6 |  |  | GAS RTD ELEMENT | AIR RTD ftS HEATERS | 8 | 4 | 179.92 |  | U7193SXXXXPXXX40 | 179.92 | 719.68
7 |  |  | LEVEL SWITCH | BASE ASSEMBLY | 9 | 2 | 567.53 |  | 236B6152P0001 | 567.53 | 1135.06
8 |  |  | OIL DEFLECTOR (MACH) EPOX | PED ASSY CE/TE EPOXY | 12 | 2 | 9049.32 |  | 190D5502G0002 | 9049.32 | 18098.64
9 |  |  | OIL DFTR NO VAPOR EXTR | PED ASSY CE/TE EPOXY | 12 | 2 | 3888.15 |  | 190D5502G0004 | 3888.15 | 7776.3
10 |  |  | RET RING INSUL ASSY | ROTOR WIND | 9 | 2 | 2150.9 |  | 326B8352G0001 | 2150.9 | 4301.8
11 |  |  | STRIP HEATER | GLAC ASSY | 15 | 1 | 126.79 |  | 341A3898P0001 | 126.79 | 126.79
12 |  |  | STRIP HEATER-750W/480V | BASE ASSY | 7 | 6 | 176.4 |  | 02028J49P0002 | 176.4 | 1058.4
13 |  |  | SWITCH PRESS | BLK & PORT/6A3/7A6 | 6 | 1 | 425.04 |  | 236B3898P0001 | 425.04 | 425.04
14 |  |  | SWITCH PRESS | BLK & PORT/6A3/7A6 | 6 | 1 | 364.67 |  | 196C8617P0001 | 364.67 | 364.67
15 |  |  | TERMINAL ASM/MAIN 7A6 | ROTOR ASSY | 9 | 2 | 5831.7 |  | 236B2333G0001 | 5831.7 | 11663.4
16 |  |  | THERMOCOUPLE | BEARING | 7 | 4 | 228.22 |  | U7025K101U060 | 228.22 | 912.88