## Systems
| List of Available subsystems | [5 empty] | (off-line units included)
Not shown sub index | Subsystem Name | # Buses | #Part Bus | Adjustment Type | Total Gen | Net Intrchng | MaxImport | MaxExport | Change
1 | ERCOT_GENS | 362 | 290 | ExportSpecOff | 40801.5 | 40648.5 | 0 | 14219.9
2 | NORTH2001 | 85 | 74 | ExportSpecOff | 11296.2 | 11263.9 | 0 | 3178.6
3 | SOUTH2001 | 226 | 177 | ExportSpecOff | 25643.3 | 25547 | 0 | 9317.3
4 | WEST2001 | 51 | 39 | ExportSpecOff | 3862 | 3837.6 | 0 | 1724

## AC FCITC Summary
AC FCITC Multiple Transfers Report
*** MUST 4.00 *** MON, APR 23 2001 10:26 ***
01SUM1N - 2001 SUMMER ON-PEAK BASE CASE - ERCOT ESC SSTF
PASS 8 - 12/01/00 - ERCOT
Subsys.File D:\ATC_3zones_01\Gens_2csc_3z.sub
Monit.File D:\allmon_.mon
Contin.File D:\Wichita\All_contingencies.con
Exclud.File D:\Wichita\excludefile.exc
Study transfer. From NORTH2001 To SOUTH2001 . Transfer level - 20000.0 MW
AC DC Delta L: Limiting constraint PreShft PostShf AC_TDF
FCITC FCITC FCITC C: Contingency description Ncon MVA/MW MVA/MW Rating
1034.9 1046.8 -11.9 L: 3410 LAKE CRK 138 3415 TEMP SS 138 1 109.8 187.9 186.0 0.07548
C:Open 3409 LAKE CRK 345 3414 TEMP SS 345 1
Open 3405 T HOUSE 345 3414 TEMP SS 345 1
1557.2 1544.5 12.7 L: 3661 SALTY M 138 3430 SANDOW 138 1 103.6 212.4 214.0 0.06988
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
1562.1 1583.7 -21.6 L: 7500 TURNER13 138 7501 GOFORT13 138 1 98.7 223.8 220.0 0.08011
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
1600.3 1595.6 4.6 L: 3659 THORNDAL 138 3661 SALTY M 138 1 100.5 212.4 214.0 0.06990
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
1669.5 1673.7 -4.2 L: 3658 TAYLOR 138 3659 THORNDAL 138 1 95.6 212.3 214.0 0.06991
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
1650.3 1677.0 -26.8 L: 7501 GOFORT13 138 7515 ROHR 13 138 1 91.8 223.8 220.0 0.07999
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
1721.5 1753.7 -32.2 L: 7200 CANYON13 138 7515 ROHR 13 138 1 86.3 223.8 220.0 0.07990
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
2084.4 2067.7 16.7 L: 3650 ELGIN SS 138 3430 SANDOW 138 1 65.8 214.6 214.0 0.07137
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
1936.5 2123.5 -187.0 L: 7192 SANMAR13 138 7200 CANYON13 138 1 62.6 217.5 220.0 0.07999
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
2159.7 2155.3 4.4 L: 3409 LAKE CRK 345 3414 TEMP SS 345 1 355.3 956.2 956.0 0.27823
C:Open 3405 T HOUSE 345 3414 TEMP SS 345 1
2210.1 2207.4 2.7 L: 3409 LAKE CRK 345 3414 TEMP SS 345 1 348.0 956.2 956.0 0.27521
C:Open 3405 T HOUSE 345 3409 LAKE CRK 345 1
Open 3405 T HOUSE 345 3414 TEMP SS 345 1
2252.1 2218.6 33.5 L: 3405 T HOUSE 345 3409 LAKE CRK 345 2 391.8 956.9 956.0 0.25095
C:Open 3405 T HOUSE 345 3409 LAKE CRK 345 1
Open 3405 T HOUSE 345 3414 TEMP SS 345 1
2333.1 2274.2 58.9 L: 7332 ELGIN 13 138 3650 ELGIN SS 138 1 17.9 215.0 214.0 0.08446
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
2321.7 2320.8 1.0 L: 3405 T HOUSE 345 3414 TEMP SS 345 1 341.4 956.3 956.0 0.26485
C:Open 3409 LAKE CRK 345 3414 TEMP SS 345 1
2710.7 2488.0 222.8 L: 967 GIBCRK B 345 44500 OBRIEN 5 345 1 525.0 1085.3 1088.0 0.20671
C:Open 40600 FRONTR 345 40900 KING 5 345 &1
Open 46500 TOMBAL 5 345 3391 JEWETT N 345 1
2223.0 2611.7 -388.7 L: 3409 LAKE CRK 345 3410 LAKE CRK 138 1 331.5 536.7 537.0 0.09227
C:Open 3409 LAKE CRK 345 3414 TEMP SS 345 1
Open 3405 T HOUSE 345 3414 TEMP SS 345 1
2985.7 2955.9 29.8 L: 3429 SANDOW 345 7040 AUSTRO34 345 1 157.5 717.0 716.0 0.18737
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 2
2937.1 3034.9 -97.8 L: 7334 MCNEIL13 138 7336 GILLEL13 138 1 18.0 219.9 220.0 0.06876
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
3219.4 3062.8 156.7 L: 7334 MCNEIL13 138 9079 MCNEILN 138 1 58.1 302.8 304.0 0.07603
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
2919.7 3085.3 -165.6 L: 3414 TEMP SS 345 3415 TEMP SS 138 1 264.2 543.4 543.0 0.09565
C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
Open 3414 TEMP SS 345 3429 SANDOW 345 1
3074.7 3140.9 -66.2 L: 9074 LYTTON 345 7042 ZORN 34 345 1 389.2 1100.2 1100.0 0.23122
C:Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
3233.0 3205.5 27.4 L: 3429 SANDOW 345 7040 AUSTRO34 345 2 157.5 788.2 789.0 0.19508
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
3302.7 3308.0 -5.3 L: 3413 TEMPSSLT 345 3414 TEMP SS 345 1 147.2 1071.2 1072.0 0.27978
C:Open 3414 TEMP SS 345 3429 SANDOW 345 1
3724.8 3363.8 361.0 L:46500 TOMBAL 5 345 3391 JEWETT N 345 1 274.5 952.4 956.0 0.18199
C:Open 45500 T_H_W_ 5 345 3390 JEWETT S 345 1
Open 967 GIBCRK B 345 44500 OBRIEN 5 345 1
3489.1 3441.4 47.8 L: 1690 VALLEY 345 1692 PARIS SS 345 1 454.1 1050.4 1052.0 0.17089
C:Open 1692 PARIS SS 345 1695 MOSES 345 1
3501.5 3523.1 -21.6 L: 3414 TEMP SS 345 3429 SANDOW 345 1 90.6 957.1 956.0 0.24747
C:Open 3413 TEMPSSLT 345 3414 TEMP SS 345 1
3226.0 3524.3 -298.4 L: 7202 HICROS13 138 9147 HICRSMB2 138 1 216.0 477.5 480.0 0.08106
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
3894.0 3566.3 327.7 L: 967 GIBCRK B 345 44500 OBRIEN 5 345 1 362.0 1086.9 1088.0 0.18614
C:Open 45500 T_H_W_ 5 345 3390 JEWETT S 345 1
Open 46500 TOMBAL 5 345 3391 JEWETT N 345 1
4071.7 3588.2 483.5 L: 3390 JEWETT S 345 45500 T_H_W_ 5 345 1 236.4 956.1 956.0 0.17677
C:Open 40600 FRONTR 345 40900 KING 5 345 &1
Open 46500 TOMBAL 5 345 3391 JEWETT N 345 1
3483.7 3650.0 -166.2 L: 3415 TEMP SS 138 3675 ROGERS 138 1 104.3 184.8 186.0 0.02309
C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
Open 3414 TEMP SS 345 3429 SANDOW 345 1
3443.7 3729.9 -286.2 L: 7202 HICROS13 138 7500 TURNER13 138 1 157.1 437.2 440.0 0.08134
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
3641.5 3736.1 -94.6 L: 7040 AUSTRO34 345 7045 ZORN 34 345 1 330.0 1100.1 1100.0 0.21148
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
3863.7 3906.1 -42.4 L: 3414 TEMP SS 345 3429 SANDOW 345 1 200.1 956.1 956.0 0.19568
C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
3731.1 3913.9 -182.9 L: 9074 LYTTON 345 7042 ZORN 34 345 1 341.2 1101.2 1100.0 0.20370
C:Open 7040 AUSTRO34 345 7048 GARFIE34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
4501.8 4014.6 487.2 L:46500 TOMBAL 5 345 3391 JEWETT N 345 1 134.4 951.6 956.0 0.18151
C:Open 967 GIBCRK B 345 40600 FRONTR 345 1
Open 967 GIBCRK B 345 44500 OBRIEN 5 345 1
4173.2 4229.6 -56.4 L: 3409 LAKE CRK 345 3414 TEMP SS 345 1 220.8 957.0 956.0 0.17642
Base Case
4242.6 4314.5 -71.9 L: 3413 TEMPSSLT 345 3429 SANDOW 345 1 200.2 1068.2 1072.0 0.20460
C:Open 3414 TEMP SS 345 3429 SANDOW 345 1
4385.9 4372.9 13.0 L: 7040 AUSTRO34 345 7048 GARFIE34 345 1 323.5 1098.8 1100.0 0.17678
C:Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
4548.5 4444.9 103.6 L:46100 N_BELT 5 345 40900 KING 5 345 97 524.0 1087.6 1091.0 0.12391
C:Open 45500 T_H_W_ 5 345 3390 JEWETT S 345 1
Open 967 GIBCRK B 345 44500 OBRIEN 5 345 1
4004.7 4476.5 -471.8 L: 1692 PARIS SS 345 1695 MOSES 345 1 305.3 968.3 1052.0 0.16555
NotConv C:Open 1690 VALLEY 345 1692 PARIS SS 345 1
4657.6 4488.2 169.5 L: 3390 JEWETT S 345 45500 T_H_W_ 5 345 1 88.3 890.4 956.0 0.17222
NotConv C:Open 967 GIBCRK B 345 40600 FRONTR 345 1
Open 967 GIBCRK B 345 44500 OBRIEN 5 345 1
4477.8 4563.6 -85.7 L: 2428 WATMILLE 345 2432 TRICORN 345 1 172.5 1074.7 1072.0 0.20148
C:Open 3380 BIGBRN 345 3390 JEWETT S 345 1
Open 3380 BIGBRN 345 3391 JEWETT N 345 1
4606.7 4703.5 -96.8 L: 3429 SANDOW 345 3430 SANDOW 138 1 79.8 449.8 448.0 0.08032
C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
Open 3414 TEMP SS 345 3429 SANDOW 345 1
4705.1 4705.1 0.0 L: 3429 SANDOW 345 7040 AUSTRO34 345 1 97.4 717.9 716.0 0.13188
Base Case
4698.1 4756.8 -58.7 L: 9040 AUSTROP 345 7040 AUSTRO34 345 1 274.8 1125.7 1125.0 0.18112
C:Open 7040 AUSTRO34 345 7048 GARFIE34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
4257.2 4783.1 -525.9 L: 3429 SANDOW 345 3430 SANDOW 138 1 151.9 419.9 448.0 0.06296
NotConv C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
4758.7 4830.1 -71.4 L: 3405 T HOUSE 345 3414 TEMP SS 345 1 207.4 958.1 956.0 0.15775
Base Case
4772.3 4879.4 -107.1 L: 1690 VALLEY 345 1692 PARIS SS 345 1 552.5 1043.9 1052.0 0.10296
NotConv Base Case
4743.3 4930.2 -186.9 L: 3405 T HOUSE 345 3409 LAKE CRK 345 2 228.2 937.0 956.0 0.14943
NotConv C:Open 3405 T HOUSE 345 3414 TEMP SS 345 1
4113.4 5110.7 -997.3 L: 2428 WATMILLE 345 2432 TRICORN 345 1 104.8 933.1 1072.0 0.20137
NotConv C:Open 3123 TRINDAD1 345 3133 RICHLND1 345 1
Open 3124 TRINDAD2 345 3134 RICHLND2 345 1
4717.1 5117.2 -400.1 L: 3380 BIGBRN 345 3390 JEWETT S 345 1 233.8 830.5 956.0 0.12650
NotConv C:Open 3380 BIGBRN 345 3391 JEWETT N 345 1
4769.2 5133.0 -363.8 L: 3429 SANDOW 345 7040 AUSTRO34 345 2 97.4 730.1 789.0 0.13267
NotConv Base Case
4788.0 5144.2 -356.3 L: 967 GIBCRK B 345 44500 OBRIEN 5 345 1 281.3 807.1 906.0 0.10982
NotConv Base Case
3683.8 5188.3 -1504.5 L: 3116 TNSKGATE 345 3124 TRINDAD2 345 1 82.3 959.0 1072.0 0.23798
NotConv C:Open 3100 MARTINLK 345 3116 TNSKGATE 345 1
4752.5 5352.9 -600.3 L: 3413 TEMPSSLT 345 3414 TEMP SS 345 1 200.8 991.9 1072.0 0.16647
NotConv Base Case
4541.5 5413.4 -871.9 L:45972 KUYDAL 5 345 40600 FRONTR 345 75 546.6 1422.8 1662.0 0.19294
NotConv C:Open 45500 T_H_W_ 5 345 3390 JEWETT S 345 1
Open 967 GIBCRK B 345 44500 OBRIEN 5 345 1
4784.2 5445.0 -660.8 L:46500 TOMBAL 5 345 3391 JEWETT N 345 1 187.5 725.1 906.0 0.11236
NotConv Base Case
4778.4 5486.8 -708.4 L: 7042 ZORN 34 345 7045 ZORN 34 345 1 224.9 1010.2 1100.0 0.16433
NotConv C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
3675.0 5513.7 -1838.7 L: 3119 NACOG SE 345 3120 NACOG SE 138 1 65.9 399.6 512.0 0.09080
NotConv C:Open 3100 MARTINLK 345 3116 TNSKGATE 345 1
4531.7 5544.0 -1012.3 L:45972 KUYDAL 5 345 40900 KING 5 345 75 522.1 1395.3 1662.0 0.19269
NotConv C:Open 45500 T_H_W_ 5 345 3390 JEWETT S 345 1
Open 967 GIBCRK B 345 44500 OBRIEN 5 345 1
Study transfer. From NORTH2001 To WEST2001 . Transfer level - 20000.0 MW
AC DC Delta L: Limiting constraint PreShft PostShf AC_TDF
FCITC FCITC FCITC C: Contingency description Ncon MVA/MW MVA/MW Rating
828.9 872.4 -43.5 L: 1869 BENB A T 345 1873 BENBRK 345 1 858.4 1052.0 1052.0 0.23357
C:Open 1436 PARKER 345 1900 COM PEAK 345 1
1070.7 1008.5 62.2 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 32.6 84.5 84.0 0.04846
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1119.6 1057.8 61.9 L: 1624 LEON 138 1640 LNGLVL M 138 1 36.1 85.1 84.0 0.04377
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
897.2 1126.0 -228.7 L: 1029 ODEHV 2T 345 1030 MRGN CRK 345 1 262.6 526.4 526.0 0.29401
C:Open 1028 ODEHV 1T 345 1030 MRGN CRK 345 1
898.4 1127.6 -229.2 L: 1028 ODEHV 1T 345 1030 MRGN CRK 345 1 262.4 526.4 526.0 0.29382
C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1369.1 1172.3 196.8 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 23.7 85.1 84.0 0.04480
Base Case
992.2 1174.5 -182.3 L: 1026 ODES EHV 345 1028 ODEHV 1T 345 1 192.4 526.3 526.0 0.33648
C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1073.7 1214.6 -140.9 L: 1029 ODEHV 2T 345 1030 MRGN CRK 345 1 196.2 526.8 526.0 0.30792
C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1116.6 1247.8 -131.3 L: 1026 ODES EHV 345 1028 ODEHV 1T 345 1 101.2 526.7 526.0 0.38105
C:Open 1020 EHV TIET 345 1029 ODEHV 2T 345 1
1008.3 1271.9 -263.6 L: 1028 ODEHV 1T 345 1030 MRGN CRK 345 1 269.7 529.8 526.0 0.25786
C:Open 1021 MIDL E T 345 1025 FS COGEN 345 1
1464.6 1280.1 184.5 L: 1624 LEON 138 1640 LNGLVL M 138 1 18.4 85.0 84.0 0.04542
Base Case
1259.7 1879.7 -620.0 L: 1020 EHV TIET 345 1029 ODEHV 2T 345 1 1.1 895.0 1195.0 0.70958
NotConv C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1624.9 1879.7 -254.9 L: 1020 EHV TIET 345 1026 ODES EHV 345 1 1.1 1198.3 1195.0 0.73675
C:Open 1020 EHV TIET 345 1029 ODEHV 2T 345 1
1510.3 1918.2 -407.8 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 230.0 612.5 717.0 0.25324
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1611.5 1923.2 -311.7 L: 1029 ODEHV 2T 345 1030 MRGN CRK 345 1 191.6 528.6 526.0 0.20909
Base Case
1565.8 1926.2 -360.4 L: 1020 EHV TIET 345 1026 ODES EHV 345 1 170.2 1198.0 1195.0 0.65645
C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1617.5 1931.3 -313.8 L: 1028 ODEHV 1T 345 1030 MRGN CRK 345 1 191.3 528.6 526.0 0.20852
Base Case
1695.6 2009.7 -314.1 L: 1026 ODES EHV 345 1028 ODEHV 1T 345 1 106.9 523.7 526.0 0.24583
Base Case
1359.7 2028.9 -669.3 L: 1571 ORAN 138 1596 GRAHAMSS 138 1 109.9 108.8 186.0 -0.00079
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1929.8 2084.2 -154.4 L: 1371 MURRAY M 138 1431 GRAHAM P 138 1 8.6 97.4 96.0 0.04601
Base Case
1905.8 2220.2 -314.5 L: 1869 BENB A T 345 1873 BENBRK 345 1 839.7 1050.5 1052.0 0.11058
C:Open 1870 BENB B T 345 1873 BENBRK 345 1
1723.8 2239.3 -515.6 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 374.5 556.2 717.0 0.10542
NotConv C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1887.6 2271.2 -383.6 L: 1027 ODES EHV 138 1028 ODEHV 1T 345 1 146.0 350.1 350.0 0.10814
C:Open 1026 ODES EHV 345 1028 ODEHV 1T 345 1
1903.9 2344.8 -440.9 L: 1030 MRGN CRK 345 1420 ENCOGEN 345 1 100.5 671.2 717.0 0.29979
NotConv C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
1672.8 2345.9 -673.1 L: 1025 FS COGEN 345 1030 MRGN CRK 345 1 100.8 472.4 526.0 0.22214
NotConv C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1674.4 2348.0 -673.6 L: 1025 FS COGEN 345 1030 MRGN CRK 345 1 100.8 472.4 526.0 0.22190
NotConv C:Open 1028 ODEHV 1T 345 1030 MRGN CRK 345 1
1848.0 2369.0 -521.0 L: 1030 MRGN CRK 345 1420 ENCOGEN 345 1 107.4 652.1 717.0 0.29479
NotConv C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
2003.8 2411.8 -408.1 L: 1869 BENB A T 345 1436 PARKER 345 1 444.7 1025.8 1052.0 0.29001
NotConv C:Open 1436 PARKER 345 1900 COM PEAK 345 1
1977.3 2432.1 -454.8 L: 1886 EV EAST 345 1422 BOWMAN 345 1 342.3 748.0 789.0 0.20515
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1782.1 2487.6 -705.5 L: 1027 ODES EHV 138 1028 ODEHV 1T 345 1 91.6 307.4 350.0 0.12110
NotConv C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1780.2 2511.1 -730.9 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 227.1 550.4 717.0 0.18161
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
1777.7 2677.6 -899.9 L: 6230 ABMULCE7 345 1430 GRAHAM 345 1 65.8 533.5 717.0 0.26306
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
1778.8 2679.2 -900.4 L: 1027 ODES EHV 138 1029 ODEHV 2T 345 1 187.9 510.9 680.0 0.18158
NotConv C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1895.1 2718.8 -823.7 L: 1020 EHV TIET 345 1029 ODEHV 2T 345 1 70.8 1102.6 1195.0 0.54444
NotConv C:Open 1026 ODES EHV 345 1028 ODEHV 1T 345 1
1970.7 2779.8 -809.1 L: 1596 GRAHAMSS 138 1601 GRAHAM E 138 1 141.3 189.1 251.0 0.02425
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1916.6 2802.0 -885.4 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 307.0 487.8 717.0 0.09435
NotConv C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
1992.2 2918.8 -926.5 L: 1601 GRAHAM E 138 1431 GRAHAM P 138 1 160.4 178.8 251.0 0.00923
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1900.0 2968.1 -1068.1 L: 6230 ABMULCE7 345 1430 GRAHAM 345 1 105.6 484.9 717.0 0.19961
NotConv C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
2019.4 2969.2 -949.8 L: 1030 MRGN CRK 345 1420 ENCOGEN 345 1 110.1 588.3 717.0 0.23683
NotConv Base Case
2014.6 3068.2 -1053.6 L: 1430 GRAHAM 345 1436 PARKER 345 2 425.9 672.9 1052.0 0.12259
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
2021.4 3070.0 -1048.6 L: 1430 GRAHAM 345 1436 PARKER 345 1 425.9 677.5 1052.0 0.12447
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 2
1505.8 3114.7 -1608.8 L: 1032 MRGN CRK 138 1341 SWTRDT T 138 1 87.6 51.3 186.0 -0.02411
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1508.0 3119.1 -1611.1 L: 1339 ESKOTA 138 1341 SWTRDT T 138 1 61.9 79.4 214.0 0.01164
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1684.0 3150.9 -1466.9 L: 1021 MIDL E T 345 1025 FS COGEN 345 1 307.5 740.8 896.0 0.25727
NotConv C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1685.5 3153.5 -1468.0 L: 1021 MIDL E T 345 1025 FS COGEN 345 1 307.5 740.6 896.0 0.25697
NotConv C:Open 1028 ODEHV 1T 345 1030 MRGN CRK 345 1
2023.6 3168.0 -1144.4 L: 1020 EHV TIET 345 1026 ODES EHV 345 1 32.4 988.9 1195.0 0.47271
NotConv Base Case
1848.6 3181.8 -1333.1 L: 1420 ENCOGEN 345 1430 GRAHAM 345 1 274.6 360.9 717.0 0.04666
NotConv C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1884.2 3189.5 -1305.3 L: 1420 ENCOGEN 345 1430 GRAHAM 345 1 239.9 373.8 717.0 0.07106
NotConv C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
2017.7 3262.2 -1244.5 L: 1869 BENB A T 345 1873 BENBRK 345 1 522.3 897.4 1052.0 0.18591
NotConv Base Case
2022.7 3291.4 -1268.7 L: 6169 TCRK2 4 138 1371 MURRAY M 138 1 11.4 103.9 155.0 0.04576
NotConv Base Case
1734.6 3415.6 -1681.0 L: 1032 MRGN CRK 138 1341 SWTRDT T 138 1 112.6 43.4 186.0 -0.03991
NotConv C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1727.6 3420.0 -1692.4 L: 1339 ESKOTA 138 1341 SWTRDT T 138 1 87.1 72.3 214.0 -0.00855
NotConv C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
2041.4 3422.3 -1380.9 L: 1690 VALLEY 345 1692 PARIS SS 345 1 454.1 800.9 1052.0 0.16987
NotConv C:Open 1692 PARIS SS 345 1695 MOSES 345 1
1981.9 3447.3 -1465.4 L: 1430 GRAHAM 345 1431 GRAHAM P 138 1 190.6 170.5 350.0 -0.01014
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
2020.2 3500.2 -1480.0 L: 1917 SHERRY T 345 2420 C HILL 345 1 179.7 668.9 925.0 0.24219
NotConv C:Open 1882 EV WEST 345 1906 VENUS S 345 1
Open 1886 EV EAST 345 1907 VENUS N 345 1
1517.2 3560.8 -2043.6 L: 6230 ABMULCE7 345 6232 ABMULCK4 138 1 33.3 151.6 284.9 0.07803
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
2024.0 3596.8 -1572.8 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 252.5 386.5 717.0 0.06621
NotConv Base Case
1681.2 3618.6 -1937.4 L: 1021 MIDL E T 345 1022 MIDLND E 345 1 78.7 429.3 717.0 0.20850
NotConv C:Open 1028 ODEHV 1T 345 1030 MRGN CRK 345 1
1682.0 3619.6 -1937.6 L: 1021 MIDL E T 345 1022 MIDLND E 345 1 78.6 432.9 717.0 0.21065
NotConv C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
2022.6 3710.3 -1687.7 L: 1571 ORAN 138 1596 GRAHAMSS 138 1 36.1 103.1 186.0 0.03312
NotConv Base Case
Study transfer. From SOUTH2001 To WEST2001 . Transfer level - 20000.0 MW
AC DC Delta L: Limiting constraint PreShft PostShf AC_TDF
FCITC FCITC FCITC C: Contingency description Ncon MVA/MW MVA/MW Rating
332.4 426.3 -93.9 L: 1906 VENUS S 345 2420 C HILL 345 1 1018.0 1072.1 1072.0 0.16265
C:Open 1882 EV WEST 345 1906 VENUS S 345 1
Open 1886 EV EAST 345 1907 VENUS N 345 1
726.4 736.3 -9.9 L: 1869 BENB A T 345 1873 BENBRK 345 1 858.4 1056.6 1052.0 0.27291
C:Open 1436 PARKER 345 1900 COM PEAK 345 1
655.3 743.8 -88.6 L: 1906 VENUS S 345 2420 C HILL 345 1 974.9 1074.0 1072.0 0.15123
C:Open 1882 EV WEST 345 1906 VENUS S 345 1
1117.6 1059.8 57.7 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 32.6 83.9 84.0 0.04590
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1111.6 1111.6 0.0 L: 1624 LEON 138 1640 LNGLVL M 138 1 36.1 79.1 84.0 0.03870
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
907.9 1145.4 -237.5 L: 1029 ODEHV 2T 345 1030 MRGN CRK 345 1 262.6 526.5 526.0 0.29069
C:Open 1028 ODEHV 1T 345 1030 MRGN CRK 345 1
909.1 1147.1 -238.0 L: 1028 ODEHV 1T 345 1030 MRGN CRK 345 1 262.4 526.5 526.0 0.29051
C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1131.8 1167.0 -35.2 L: 3415 TEMP SS 138 3675 ROGERS 138 1 104.3 189.7 186.0 0.07546
C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
Open 3414 TEMP SS 345 3429 SANDOW 345 1
998.9 1187.1 -188.3 L: 1026 ODES EHV 345 1028 ODEHV 1T 345 1 192.4 526.3 526.0 0.33426
C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1082.1 1229.3 -147.1 L: 1029 ODEHV 2T 345 1030 MRGN CRK 345 1 196.2 526.9 526.0 0.30563
C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1118.2 1251.5 -133.2 L: 1026 ODES EHV 345 1028 ODEHV 1T 345 1 101.2 526.5 526.0 0.38037
C:Open 1020 EHV TIET 345 1029 ODEHV 2T 345 1
1019.8 1295.1 -275.3 L: 1028 ODEHV 1T 345 1030 MRGN CRK 345 1 269.7 529.7 526.0 0.25496
C:Open 1021 MIDL E T 345 1025 FS COGEN 345 1
1622.8 1812.4 -189.7 L: 1869 BENB A T 345 1873 BENBRK 345 1 839.7 1050.1 1052.0 0.12965
C:Open 1870 BENB B T 345 1873 BENBRK 345 1
1638.0 1879.7 -241.7 L: 1020 EHV TIET 345 1026 ODES EHV 345 1 1.1 1195.0 1195.0 0.72885
C:Open 1020 EHV TIET 345 1029 ODEHV 2T 345 1
1259.7 1879.7 -620.0 L: 1020 EHV TIET 345 1029 ODEHV 2T 345 1 1.1 894.9 1195.0 0.70950
NotConv C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1571.5 1941.0 -369.5 L: 1020 EHV TIET 345 1026 ODES EHV 345 1 170.2 1198.1 1195.0 0.65415
C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1624.2 1956.4 -332.2 L: 1029 ODEHV 2T 345 1030 MRGN CRK 345 1 191.6 527.9 526.0 0.20700
Base Case
1630.8 1964.6 -333.9 L: 1028 ODEHV 1T 345 1030 MRGN CRK 345 1 191.3 528.2 526.0 0.20656
Base Case
1496.8 1964.9 -468.1 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 230.0 581.1 717.0 0.23459
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1713.0 2024.7 -311.7 L: 1026 ODES EHV 345 1028 ODEHV 1T 345 1 106.9 522.9 526.0 0.24283
Base Case
1956.4 2125.9 -169.4 L: 3429 SANDOW 345 7040 AUSTRO34 345 1 157.5 714.3 716.0 0.28458
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 2
1892.8 2145.2 -252.4 L: 1869 BENB A T 345 1436 PARKER 345 1 444.7 1050.6 1052.0 0.32011
C:Open 1436 PARKER 345 1900 COM PEAK 345 1
2013.4 2266.3 -253.0 L: 1906 VENUS S 345 3405 T HOUSE 345 1 499.0 953.0 956.0 0.22547
C:Open 1907 VENUS N 345 3405 T HOUSE 345 1
1730.7 2293.9 -563.2 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 374.5 550.2 717.0 0.10152
NotConv C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1897.9 2329.3 -431.4 L: 1571 ORAN 138 1596 GRAHAMSS 138 1 109.9 187.2 186.0 0.04072
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1879.0 2329.9 -450.9 L: 1027 ODES EHV 138 1028 ODEHV 1T 345 1 146.0 348.1 350.0 0.10756
C:Open 1026 ODES EHV 345 1028 ODEHV 1T 345 1
1682.4 2393.9 -711.5 L: 1025 FS COGEN 345 1030 MRGN CRK 345 1 100.8 480.2 526.0 0.22551
NotConv C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1683.9 2396.0 -712.1 L: 1025 FS COGEN 345 1030 MRGN CRK 345 1 100.8 480.1 526.0 0.22524
NotConv C:Open 1028 ODEHV 1T 345 1030 MRGN CRK 345 1
2013.8 2399.3 -385.5 L: 3429 SANDOW 345 7040 AUSTRO34 345 2 157.5 735.1 789.0 0.28679
NotConv C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
1848.6 2426.7 -578.1 L: 1030 MRGN CRK 345 1420 ENCOGEN 345 1 107.4 647.0 717.0 0.29190
NotConv C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1906.3 2441.1 -534.8 L: 1030 MRGN CRK 345 1420 ENCOGEN 345 1 100.5 655.6 717.0 0.29120
NotConv C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
2022.5 2441.2 -418.7 L: 7132 GILLES13 138 6390 MASON4 138 1 21.7 140.3 147.0 0.05865
NotConv Base Case
2012.1 2454.0 -441.8 L: 7334 MCNEIL13 138 9079 MCNEILN 138 1 58.1 283.4 304.0 0.11197
NotConv C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
1959.8 2512.4 -552.6 L: 1886 EV EAST 345 1422 BOWMAN 345 1 342.3 743.0 789.0 0.20443
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1781.5 2513.0 -731.4 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 227.1 540.5 717.0 0.17592
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
2022.5 2514.2 -491.7 L: 9040 AUSTROP 345 7040 AUSTRO34 345 1 532.9 1057.5 1125.0 0.25939
NotConv C:Open 9074 LYTTON 345 7048 GARFIE34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
1772.5 2539.2 -766.7 L: 1027 ODES EHV 138 1028 ODEHV 1T 345 1 91.6 304.4 350.0 0.12002
NotConv C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1997.8 2594.3 -596.6 L: 2427 WATMILLW 345 2420 C HILL 345 1 450.5 942.3 956.0 0.24614
NotConv C:Open 1906 VENUS S 345 3405 T HOUSE 345 1
Open 1907 VENUS N 345 3405 T HOUSE 345 1
2020.5 2632.9 -612.4 L: 1907 VENUS N 345 3405 T HOUSE 345 1 518.6 996.4 1072.0 0.23648
NotConv C:Open 1906 VENUS S 345 3405 T HOUSE 345 1
1782.4 2643.0 -860.6 L: 1027 ODES EHV 138 1029 ODEHV 2T 345 1 187.9 509.9 680.0 0.18065
NotConv C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1994.4 2671.6 -677.2 L: 3380 BIGBRN 345 3390 JEWETT S 345 1 470.2 934.3 956.0 0.23270
NotConv C:Open 46020 LIMEST 5 345 2428 WATMILLE 345 1
Open 46020 LIMEST 5 345 2435 WATMLLDB 345 2
1899.5 2720.4 -820.9 L: 1020 EHV TIET 345 1029 ODEHV 2T 345 1 70.8 1102.9 1195.0 0.54338
NotConv C:Open 1026 ODES EHV 345 1028 ODEHV 1T 345 1
2005.0 2721.1 -716.1 L: 7332 ELGIN 13 138 3650 ELGIN SS 138 1 17.9 172.1 214.0 0.07687
NotConv C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
2024.0 2752.4 -728.4 L: 1869 BENB A T 345 1873 BENBRK 345 1 522.3 965.8 1052.0 0.21912
NotConv Base Case
1909.6 2801.6 -892.0 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 307.0 486.4 717.0 0.09396
NotConv C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
1999.5 2845.2 -845.7 L: 3380 BIGBRN 345 3391 JEWETT N 345 1 511.0 1029.2 1072.0 0.25915
NotConv C:Open 46020 LIMEST 5 345 2428 WATMILLE 345 1
Open 46020 LIMEST 5 345 2435 WATMLLDB 345 2
2015.2 2887.6 -872.5 L: 1917 SHERRY T 345 2420 C HILL 345 1 179.7 779.7 925.0 0.29776
NotConv C:Open 1882 EV WEST 345 1906 VENUS S 345 1
Open 1886 EV EAST 345 1907 VENUS N 345 1
1783.3 2913.4 -1130.1 L: 6230 ABMULCE7 345 1430 GRAHAM 345 1 65.8 502.2 717.0 0.24471
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
1976.9 2942.3 -965.4 L: 3380 BIGBRN 345 3390 JEWETT S 345 1 355.6 873.2 956.0 0.26182
NotConv C:Open 1906 VENUS S 345 3405 T HOUSE 345 1
Open 1907 VENUS N 345 3405 T HOUSE 345 1
2028.5 2959.6 -931.1 L: 3414 TEMP SS 345 3429 SANDOW 345 1 200.1 769.2 956.0 0.28055
NotConv C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
2024.4 3091.1 -1066.7 L: 1030 MRGN CRK 345 1420 ENCOGEN 345 1 110.1 574.0 717.0 0.22918
NotConv Base Case
1511.5 3105.5 -1594.0 L: 1032 MRGN CRK 138 1341 SWTRDT T 138 1 87.6 52.8 186.0 -0.02303
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1503.5 3109.9 -1606.4 L: 1339 ESKOTA 138 1341 SWTRDT T 138 1 61.9 80.6 214.0 0.01243
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
2021.3 3137.9 -1116.7 L: 6375 MENARD 4 138 6480 SAPS1 4 138 1 23.8 101.5 147.0 0.03845
NotConv Base Case
2017.7 3176.8 -1159.1 L: 1020 EHV TIET 345 1026 ODES EHV 345 1 32.4 974.7 1195.0 0.46703
NotConv Base Case
1969.2 3179.2 -1209.9 L: 1596 GRAHAMSS 138 1601 GRAHAM E 138 1 141.3 164.7 251.0 0.01191
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1670.6 3215.3 -1544.6 L: 1021 MIDL E T 345 1025 FS COGEN 345 1 307.5 719.7 896.0 0.24673
NotConv C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1672.2 3218.0 -1545.8 L: 1021 MIDL E T 345 1025 FS COGEN 345 1 307.5 719.7 896.0 0.24648
NotConv C:Open 1028 ODEHV 1T 345 1030 MRGN CRK 345 1
1909.8 3232.8 -1323.0 L: 6230 ABMULCE7 345 1430 GRAHAM 345 1 105.6 459.2 717.0 0.18516
NotConv C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
2016.8 3243.3 -1226.4 L: 1430 GRAHAM 345 1436 PARKER 345 2 425.9 645.1 1052.0 0.10869
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1

## RateB South to West
Study transfer. From SOUTH2001 To WEST2001 . Transfer level - 20000.0 MW
AC DC Delta L: Limiting constraint PreShft PostShf AC_TDF
FCITC FCITC FCITC C: Contingency description Ncon MVA/MW MVA/MW Rating
332.4 426.3 -93.9 L: 1906 VENUS S 345 2420 C HILL 345 1 1018.0 1072.1 1072.0 0.16265
C:Open 1882 EV WEST 345 1906 VENUS S 345 1
Open 1886 EV EAST 345 1907 VENUS N 345 1
726.4 736.3 -9.9 L: 1869 BENB A T 345 1873 BENBRK 345 1 858.4 1056.6 1052.0 0.27291
C:Open 1436 PARKER 345 1900 COM PEAK 345 1
655.3 743.8 -88.6 L: 1906 VENUS S 345 2420 C HILL 345 1 974.9 1074.0 1072.0 0.15123
C:Open 1882 EV WEST 345 1906 VENUS S 345 1
1117.6 1059.8 57.7 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 32.6 83.9 84.0 0.04590
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1111.6 1111.6 0.0 L: 1624 LEON 138 1640 LNGLVL M 138 1 36.1 79.1 84.0 0.03870
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
907.9 1145.4 -237.5 L: 1029 ODEHV 2T 345 1030 MRGN CRK 345 1 262.6 526.5 526.0 0.29069
C:Open 1028 ODEHV 1T 345 1030 MRGN CRK 345 1
909.1 1147.1 -238.0 L: 1028 ODEHV 1T 345 1030 MRGN CRK 345 1 262.4 526.5 526.0 0.29051
C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1131.8 1167.0 -35.2 L: 3415 TEMP SS 138 3675 ROGERS 138 1 104.3 189.7 186.0 0.07546
C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
Open 3414 TEMP SS 345 3429 SANDOW 345 1
998.9 1187.1 -188.3 L: 1026 ODES EHV 345 1028 ODEHV 1T 345 1 192.4 526.3 526.0 0.33426
C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1082.1 1229.3 -147.1 L: 1029 ODEHV 2T 345 1030 MRGN CRK 345 1 196.2 526.9 526.0 0.30563
C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1118.2 1251.5 -133.2 L: 1026 ODES EHV 345 1028 ODEHV 1T 345 1 101.2 526.5 526.0 0.38037
C:Open 1020 EHV TIET 345 1029 ODEHV 2T 345 1
1019.8 1295.1 -275.3 L: 1028 ODEHV 1T 345 1030 MRGN CRK 345 1 269.7 529.7 526.0 0.25496
C:Open 1021 MIDL E T 345 1025 FS COGEN 345 1
1622.8 1812.4 -189.7 L: 1869 BENB A T 345 1873 BENBRK 345 1 839.7 1050.1 1052.0 0.12965
C:Open 1870 BENB B T 345 1873 BENBRK 345 1
1638.0 1879.7 -241.7 L: 1020 EHV TIET 345 1026 ODES EHV 345 1 1.1 1195.0 1195.0 0.72885
C:Open 1020 EHV TIET 345 1029 ODEHV 2T 345 1
1259.7 1879.7 -620.0 L: 1020 EHV TIET 345 1029 ODEHV 2T 345 1 1.1 894.9 1195.0 0.70950
NotConv C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1571.5 1941.0 -369.5 L: 1020 EHV TIET 345 1026 ODES EHV 345 1 170.2 1198.1 1195.0 0.65415
C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1624.2 1956.4 -332.2 L: 1029 ODEHV 2T 345 1030 MRGN CRK 345 1 191.6 527.9 526.0 0.20700
Base Case
1630.8 1964.6 -333.9 L: 1028 ODEHV 1T 345 1030 MRGN CRK 345 1 191.3 528.2 526.0 0.20656
Base Case
1496.8 1964.9 -468.1 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 230.0 581.1 717.0 0.23459
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1713.0 2024.7 -311.7 L: 1026 ODES EHV 345 1028 ODEHV 1T 345 1 106.9 522.9 526.0 0.24283
Base Case
1956.4 2125.9 -169.4 L: 3429 SANDOW 345 7040 AUSTRO34 345 1 157.5 714.3 716.0 0.28458
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 2
1892.8 2145.2 -252.4 L: 1869 BENB A T 345 1436 PARKER 345 1 444.7 1050.6 1052.0 0.32011
C:Open 1436 PARKER 345 1900 COM PEAK 345 1
2013.4 2266.3 -253.0 L: 1906 VENUS S 345 3405 T HOUSE 345 1 499.0 953.0 956.0 0.22547
C:Open 1907 VENUS N 345 3405 T HOUSE 345 1
1730.7 2293.9 -563.2 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 374.5 550.2 717.0 0.10152
NotConv C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1897.9 2329.3 -431.4 L: 1571 ORAN 138 1596 GRAHAMSS 138 1 109.9 187.2 186.0 0.04072
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1879.0 2329.9 -450.9 L: 1027 ODES EHV 138 1028 ODEHV 1T 345 1 146.0 348.1 350.0 0.10756
C:Open 1026 ODES EHV 345 1028 ODEHV 1T 345 1
1682.4 2393.9 -711.5 L: 1025 FS COGEN 345 1030 MRGN CRK 345 1 100.8 480.2 526.0 0.22551
NotConv C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1683.9 2396.0 -712.1 L: 1025 FS COGEN 345 1030 MRGN CRK 345 1 100.8 480.1 526.0 0.22524
NotConv C:Open 1028 ODEHV 1T 345 1030 MRGN CRK 345 1
2013.8 2399.3 -385.5 L: 3429 SANDOW 345 7040 AUSTRO34 345 2 157.5 735.1 789.0 0.28679
NotConv C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
1848.6 2426.7 -578.1 L: 1030 MRGN CRK 345 1420 ENCOGEN 345 1 107.4 647.0 717.0 0.29190
NotConv C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1906.3 2441.1 -534.8 L: 1030 MRGN CRK 345 1420 ENCOGEN 345 1 100.5 655.6 717.0 0.29120
NotConv C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
2022.5 2441.2 -418.7 L: 7132 GILLES13 138 6390 MASON4 138 1 21.7 140.3 147.0 0.05865
NotConv Base Case
2012.1 2454.0 -441.8 L: 7334 MCNEIL13 138 9079 MCNEILN 138 1 58.1 283.4 304.0 0.11197
NotConv C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
1959.8 2512.4 -552.6 L: 1886 EV EAST 345 1422 BOWMAN 345 1 342.3 743.0 789.0 0.20443
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1781.5 2513.0 -731.4 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 227.1 540.5 717.0 0.17592
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
2022.5 2514.2 -491.7 L: 9040 AUSTROP 345 7040 AUSTRO34 345 1 532.9 1057.5 1125.0 0.25939
NotConv C:Open 9074 LYTTON 345 7048 GARFIE34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
1772.5 2539.2 -766.7 L: 1027 ODES EHV 138 1028 ODEHV 1T 345 1 91.6 304.4 350.0 0.12002
NotConv C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1997.8 2594.3 -596.6 L: 2427 WATMILLW 345 2420 C HILL 345 1 450.5 942.3 956.0 0.24614
NotConv C:Open 1906 VENUS S 345 3405 T HOUSE 345 1
Open 1907 VENUS N 345 3405 T HOUSE 345 1
2020.5 2632.9 -612.4 L: 1907 VENUS N 345 3405 T HOUSE 345 1 518.6 996.4 1072.0 0.23648
NotConv C:Open 1906 VENUS S 345 3405 T HOUSE 345 1
1782.4 2643.0 -860.6 L: 1027 ODES EHV 138 1029 ODEHV 2T 345 1 187.9 509.9 680.0 0.18065
NotConv C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1994.4 2671.6 -677.2 L: 3380 BIGBRN 345 3390 JEWETT S 345 1 470.2 934.3 956.0 0.23270
NotConv C:Open 46020 LIMEST 5 345 2428 WATMILLE 345 1
Open 46020 LIMEST 5 345 2435 WATMLLDB 345 2
1899.5 2720.4 -820.9 L: 1020 EHV TIET 345 1029 ODEHV 2T 345 1 70.8 1102.9 1195.0 0.54338
NotConv C:Open 1026 ODES EHV 345 1028 ODEHV 1T 345 1
2005.0 2721.1 -716.1 L: 7332 ELGIN 13 138 3650 ELGIN SS 138 1 17.9 172.1 214.0 0.07687
NotConv C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
2024.0 2752.4 -728.4 L: 1869 BENB A T 345 1873 BENBRK 345 1 522.3 965.8 1052.0 0.21912
NotConv Base Case
1909.6 2801.6 -892.0 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 307.0 486.4 717.0 0.09396
NotConv C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
1999.5 2845.2 -845.7 L: 3380 BIGBRN 345 3391 JEWETT N 345 1 511.0 1029.2 1072.0 0.25915
NotConv C:Open 46020 LIMEST 5 345 2428 WATMILLE 345 1
Open 46020 LIMEST 5 345 2435 WATMLLDB 345 2
2015.2 2887.6 -872.5 L: 1917 SHERRY T 345 2420 C HILL 345 1 179.7 779.7 925.0 0.29776
NotConv C:Open 1882 EV WEST 345 1906 VENUS S 345 1
Open 1886 EV EAST 345 1907 VENUS N 345 1
1783.3 2913.4 -1130.1 L: 6230 ABMULCE7 345 1430 GRAHAM 345 1 65.8 502.2 717.0 0.24471
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
1976.9 2942.3 -965.4 L: 3380 BIGBRN 345 3390 JEWETT S 345 1 355.6 873.2 956.0 0.26182
NotConv C:Open 1906 VENUS S 345 3405 T HOUSE 345 1
Open 1907 VENUS N 345 3405 T HOUSE 345 1
2028.5 2959.6 -931.1 L: 3414 TEMP SS 345 3429 SANDOW 345 1 200.1 769.2 956.0 0.28055
NotConv C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
2024.4 3091.1 -1066.7 L: 1030 MRGN CRK 345 1420 ENCOGEN 345 1 110.1 574.0 717.0 0.22918
NotConv Base Case
1511.5 3105.5 -1594.0 L: 1032 MRGN CRK 138 1341 SWTRDT T 138 1 87.6 52.8 186.0 -0.02303
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1503.5 3109.9 -1606.4 L: 1339 ESKOTA 138 1341 SWTRDT T 138 1 61.9 80.6 214.0 0.01243
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
2021.3 3137.9 -1116.7 L: 6375 MENARD 4 138 6480 SAPS1 4 138 1 23.8 101.5 147.0 0.03845
NotConv Base Case
2017.7 3176.8 -1159.1 L: 1020 EHV TIET 345 1026 ODES EHV 345 1 32.4 974.7 1195.0 0.46703
NotConv Base Case
1969.2 3179.2 -1209.9 L: 1596 GRAHAMSS 138 1601 GRAHAM E 138 1 141.3 164.7 251.0 0.01191
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1670.6 3215.3 -1544.6 L: 1021 MIDL E T 345 1025 FS COGEN 345 1 307.5 719.7 896.0 0.24673
NotConv C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1672.2 3218.0 -1545.8 L: 1021 MIDL E T 345 1025 FS COGEN 345 1 307.5 719.7 896.0 0.24648
NotConv C:Open 1028 ODEHV 1T 345 1030 MRGN CRK 345 1
1909.8 3232.8 -1323.0 L: 6230 ABMULCE7 345 1430 GRAHAM 345 1 105.6 459.2 717.0 0.18516
NotConv C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
2016.8 3243.3 -1226.4 L: 1430 GRAHAM 345 1436 PARKER 345 2 425.9 645.1 1052.0 0.10869
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1

## Rate B North to West
Study transfer. From NORTH2001 To WEST2001 . Transfer level - 20000.0 MW
AC DC Delta L: Limiting constraint PreShft PostShf AC_TDF
FCITC FCITC FCITC C: Contingency description Ncon MVA/MW MVA/MW Rating
828.9 872.4 -43.5 L: 1869 BENB A T 345 1873 BENBRK 345 1 858.4 1052.0 1052.0 0.23357
C:Open 1436 PARKER 345 1900 COM PEAK 345 1
1070.7 1008.5 62.2 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 32.6 84.5 84.0 0.04846
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1119.6 1057.8 61.9 L: 1624 LEON 138 1640 LNGLVL M 138 1 36.1 85.1 84.0 0.04377
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
897.2 1126.0 -228.7 L: 1029 ODEHV 2T 345 1030 MRGN CRK 345 1 262.6 526.4 526.0 0.29401
C:Open 1028 ODEHV 1T 345 1030 MRGN CRK 345 1
898.4 1127.6 -229.2 L: 1028 ODEHV 1T 345 1030 MRGN CRK 345 1 262.4 526.4 526.0 0.29382
C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1369.1 1172.3 196.8 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 23.7 85.1 84.0 0.04480
Base Case
992.2 1174.5 -182.3 L: 1026 ODES EHV 345 1028 ODEHV 1T 345 1 192.4 526.3 526.0 0.33648
C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1073.7 1214.6 -140.9 L: 1029 ODEHV 2T 345 1030 MRGN CRK 345 1 196.2 526.8 526.0 0.30792
C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1116.6 1247.8 -131.3 L: 1026 ODES EHV 345 1028 ODEHV 1T 345 1 101.2 526.7 526.0 0.38105
C:Open 1020 EHV TIET 345 1029 ODEHV 2T 345 1
1008.3 1271.9 -263.6 L: 1028 ODEHV 1T 345 1030 MRGN CRK 345 1 269.7 529.8 526.0 0.25786
C:Open 1021 MIDL E T 345 1025 FS COGEN 345 1
1464.6 1280.1 184.5 L: 1624 LEON 138 1640 LNGLVL M 138 1 18.4 85.0 84.0 0.04542
Base Case
1259.7 1879.7 -620.0 L: 1020 EHV TIET 345 1029 ODEHV 2T 345 1 1.1 895.0 1195.0 0.70958
NotConv C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1624.9 1879.7 -254.9 L: 1020 EHV TIET 345 1026 ODES EHV 345 1 1.1 1198.3 1195.0 0.73675
C:Open 1020 EHV TIET 345 1029 ODEHV 2T 345 1
1510.3 1918.2 -407.8 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 230.0 612.5 717.0 0.25324
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1611.5 1923.2 -311.7 L: 1029 ODEHV 2T 345 1030 MRGN CRK 345 1 191.6 528.6 526.0 0.20909
Base Case
1565.8 1926.2 -360.4 L: 1020 EHV TIET 345 1026 ODES EHV 345 1 170.2 1198.0 1195.0 0.65645
C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1617.5 1931.3 -313.8 L: 1028 ODEHV 1T 345 1030 MRGN CRK 345 1 191.3 528.6 526.0 0.20852
Base Case
1695.6 2009.7 -314.1 L: 1026 ODES EHV 345 1028 ODEHV 1T 345 1 106.9 523.7 526.0 0.24583
Base Case
1359.7 2028.9 -669.3 L: 1571 ORAN 138 1596 GRAHAMSS 138 1 109.9 108.8 186.0 -0.00079
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1929.8 2084.2 -154.4 L: 1371 MURRAY M 138 1431 GRAHAM P 138 1 8.6 97.4 96.0 0.04601
Base Case
1905.8 2220.2 -314.5 L: 1869 BENB A T 345 1873 BENBRK 345 1 839.7 1050.5 1052.0 0.11058
C:Open 1870 BENB B T 345 1873 BENBRK 345 1
1723.8 2239.3 -515.6 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 374.5 556.2 717.0 0.10542
NotConv C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1887.6 2271.2 -383.6 L: 1027 ODES EHV 138 1028 ODEHV 1T 345 1 146.0 350.1 350.0 0.10814
C:Open 1026 ODES EHV 345 1028 ODEHV 1T 345 1
1903.9 2344.8 -440.9 L: 1030 MRGN CRK 345 1420 ENCOGEN 345 1 100.5 671.2 717.0 0.29979
NotConv C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
1672.8 2345.9 -673.1 L: 1025 FS COGEN 345 1030 MRGN CRK 345 1 100.8 472.4 526.0 0.22214
NotConv C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1674.4 2348.0 -673.6 L: 1025 FS COGEN 345 1030 MRGN CRK 345 1 100.8 472.4 526.0 0.22190
NotConv C:Open 1028 ODEHV 1T 345 1030 MRGN CRK 345 1
1848.0 2369.0 -521.0 L: 1030 MRGN CRK 345 1420 ENCOGEN 345 1 107.4 652.1 717.0 0.29479
NotConv C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
2003.8 2411.8 -408.1 L: 1869 BENB A T 345 1436 PARKER 345 1 444.7 1025.8 1052.0 0.29001
NotConv C:Open 1436 PARKER 345 1900 COM PEAK 345 1
1977.3 2432.1 -454.8 L: 1886 EV EAST 345 1422 BOWMAN 345 1 342.3 748.0 789.0 0.20515
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1782.1 2487.6 -705.5 L: 1027 ODES EHV 138 1028 ODEHV 1T 345 1 91.6 307.4 350.0 0.12110
NotConv C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1780.2 2511.1 -730.9 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 227.1 550.4 717.0 0.18161
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
1777.7 2677.6 -899.9 L: 6230 ABMULCE7 345 1430 GRAHAM 345 1 65.8 533.5 717.0 0.26306
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
1778.8 2679.2 -900.4 L: 1027 ODES EHV 138 1029 ODEHV 2T 345 1 187.9 510.9 680.0 0.18158
NotConv C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1895.1 2718.8 -823.7 L: 1020 EHV TIET 345 1029 ODEHV 2T 345 1 70.8 1102.6 1195.0 0.54444
NotConv C:Open 1026 ODES EHV 345 1028 ODEHV 1T 345 1
1970.7 2779.8 -809.1 L: 1596 GRAHAMSS 138 1601 GRAHAM E 138 1 141.3 189.1 251.0 0.02425
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1916.6 2802.0 -885.4 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 307.0 487.8 717.0 0.09435
NotConv C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
1992.2 2918.8 -926.5 L: 1601 GRAHAM E 138 1431 GRAHAM P 138 1 160.4 178.8 251.0 0.00923
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1900.0 2968.1 -1068.1 L: 6230 ABMULCE7 345 1430 GRAHAM 345 1 105.6 484.9 717.0 0.19961
NotConv C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
2019.4 2969.2 -949.8 L: 1030 MRGN CRK 345 1420 ENCOGEN 345 1 110.1 588.3 717.0 0.23683
NotConv Base Case
2014.6 3068.2 -1053.6 L: 1430 GRAHAM 345 1436 PARKER 345 2 425.9 672.9 1052.0 0.12259
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
2021.4 3070.0 -1048.6 L: 1430 GRAHAM 345 1436 PARKER 345 1 425.9 677.5 1052.0 0.12447
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 2
1505.8 3114.7 -1608.8 L: 1032 MRGN CRK 138 1341 SWTRDT T 138 1 87.6 51.3 186.0 -0.02411
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1508.0 3119.1 -1611.1 L: 1339 ESKOTA 138 1341 SWTRDT T 138 1 61.9 79.4 214.0 0.01164
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1684.0 3150.9 -1466.9 L: 1021 MIDL E T 345 1025 FS COGEN 345 1 307.5 740.8 896.0 0.25727
NotConv C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1685.5 3153.5 -1468.0 L: 1021 MIDL E T 345 1025 FS COGEN 345 1 307.5 740.6 896.0 0.25697
NotConv C:Open 1028 ODEHV 1T 345 1030 MRGN CRK 345 1
2023.6 3168.0 -1144.4 L: 1020 EHV TIET 345 1026 ODES EHV 345 1 32.4 988.9 1195.0 0.47271
NotConv Base Case
1848.6 3181.8 -1333.1 L: 1420 ENCOGEN 345 1430 GRAHAM 345 1 274.6 360.9 717.0 0.04666
NotConv C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1884.2 3189.5 -1305.3 L: 1420 ENCOGEN 345 1430 GRAHAM 345 1 239.9 373.8 717.0 0.07106
NotConv C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
2017.7 3262.2 -1244.5 L: 1869 BENB A T 345 1873 BENBRK 345 1 522.3 897.4 1052.0 0.18591
NotConv Base Case
2022.7 3291.4 -1268.7 L: 6169 TCRK2 4 138 1371 MURRAY M 138 1 11.4 103.9 155.0 0.04576
NotConv Base Case
1734.6 3415.6 -1681.0 L: 1032 MRGN CRK 138 1341 SWTRDT T 138 1 112.6 43.4 186.0 -0.03991
NotConv C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1727.6 3420.0 -1692.4 L: 1339 ESKOTA 138 1341 SWTRDT T 138 1 87.1 72.3 214.0 -0.00855
NotConv C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
2041.4 3422.3 -1380.9 L: 1690 VALLEY 345 1692 PARIS SS 345 1 454.1 800.9 1052.0 0.16987
NotConv C:Open 1692 PARIS SS 345 1695 MOSES 345 1
1981.9 3447.3 -1465.4 L: 1430 GRAHAM 345 1431 GRAHAM P 138 1 190.6 170.5 350.0 -0.01014
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
2020.2 3500.2 -1480.0 L: 1917 SHERRY T 345 2420 C HILL 345 1 179.7 668.9 925.0 0.24219
NotConv C:Open 1882 EV WEST 345 1906 VENUS S 345 1
Open 1886 EV EAST 345 1907 VENUS N 345 1
1517.2 3560.8 -2043.6 L: 6230 ABMULCE7 345 6232 ABMULCK4 138 1 33.3 151.6 284.9 0.07803
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
2024.0 3596.8 -1572.8 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 252.5 386.5 717.0 0.06621
NotConv Base Case
1681.2 3618.6 -1937.4 L: 1021 MIDL E T 345 1022 MIDLND E 345 1 78.7 429.3 717.0 0.20850
NotConv C:Open 1028 ODEHV 1T 345 1030 MRGN CRK 345 1
1682.0 3619.6 -1937.6 L: 1021 MIDL E T 345 1022 MIDLND E 345 1 78.6 432.9 717.0 0.21065
NotConv C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
2022.6 3710.3 -1687.7 L: 1571 ORAN 138 1596 GRAHAMSS 138 1 36.1 103.1 186.0 0.03312
NotConv Base Case

## RateB North to South
Study transfer. From NORTH2001 To SOUTH2001 . Transfer level - 20000.0 MW
AC DC Delta L: Limiting constraint PreShft PostShf AC_TDF
FCITC FCITC FCITC C: Contingency description Ncon MVA/MW MVA/MW Rating
1034.9 1046.8 -11.9 L: 3410 LAKE CRK 138 3415 TEMP SS 138 1 109.8 187.9 186.0 0.07548
C:Open 3409 LAKE CRK 345 3414 TEMP SS 345 1
Open 3405 T HOUSE 345 3414 TEMP SS 345 1
1557.2 1544.5 12.7 L: 3661 SALTY M 138 3430 SANDOW 138 1 103.6 212.4 214.0 0.06988
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
1562.1 1583.7 -21.6 L: 7500 TURNER13 138 7501 GOFORT13 138 1 98.7 223.8 220.0 0.08011
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
1600.3 1595.6 4.6 L: 3659 THORNDAL 138 3661 SALTY M 138 1 100.5 212.4 214.0 0.06990
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
1669.5 1673.7 -4.2 L: 3658 TAYLOR 138 3659 THORNDAL 138 1 95.6 212.3 214.0 0.06991
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
1650.3 1677.0 -26.8 L: 7501 GOFORT13 138 7515 ROHR 13 138 1 91.8 223.8 220.0 0.07999
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
1721.5 1753.7 -32.2 L: 7200 CANYON13 138 7515 ROHR 13 138 1 86.3 223.8 220.0 0.07990
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
2084.4 2067.7 16.7 L: 3650 ELGIN SS 138 3430 SANDOW 138 1 65.8 214.6 214.0 0.07137
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
1936.5 2123.5 -187.0 L: 7192 SANMAR13 138 7200 CANYON13 138 1 62.6 217.5 220.0 0.07999
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
2159.7 2155.3 4.4 L: 3409 LAKE CRK 345 3414 TEMP SS 345 1 355.3 956.2 956.0 0.27823
C:Open 3405 T HOUSE 345 3414 TEMP SS 345 1
2210.1 2207.4 2.7 L: 3409 LAKE CRK 345 3414 TEMP SS 345 1 348.0 956.2 956.0 0.27521
C:Open 3405 T HOUSE 345 3409 LAKE CRK 345 1
Open 3405 T HOUSE 345 3414 TEMP SS 345 1
2252.1 2218.6 33.5 L: 3405 T HOUSE 345 3409 LAKE CRK 345 2 391.8 956.9 956.0 0.25095
C:Open 3405 T HOUSE 345 3409 LAKE CRK 345 1
Open 3405 T HOUSE 345 3414 TEMP SS 345 1
2333.1 2274.2 58.9 L: 7332 ELGIN 13 138 3650 ELGIN SS 138 1 17.9 215.0 214.0 0.08446
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
2321.7 2320.8 1.0 L: 3405 T HOUSE 345 3414 TEMP SS 345 1 341.4 956.3 956.0 0.26485
C:Open 3409 LAKE CRK 345 3414 TEMP SS 345 1
2710.7 2488.0 222.8 L: 967 GIBCRK B 345 44500 OBRIEN 5 345 1 525.0 1085.3 1088.0 0.20671
C:Open 40600 FRONTR 345 40900 KING 5 345 &1
Open 46500 TOMBAL 5 345 3391 JEWETT N 345 1
2223.0 2611.7 -388.7 L: 3409 LAKE CRK 345 3410 LAKE CRK 138 1 331.5 536.7 537.0 0.09227
C:Open 3409 LAKE CRK 345 3414 TEMP SS 345 1
Open 3405 T HOUSE 345 3414 TEMP SS 345 1
2985.7 2955.9 29.8 L: 3429 SANDOW 345 7040 AUSTRO34 345 1 157.5 717.0 716.0 0.18737
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 2
2937.1 3034.9 -97.8 L: 7334 MCNEIL13 138 7336 GILLEL13 138 1 18.0 219.9 220.0 0.06876
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
3219.4 3062.8 156.7 L: 7334 MCNEIL13 138 9079 MCNEILN 138 1 58.1 302.8 304.0 0.07603
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
2919.7 3085.3 -165.6 L: 3414 TEMP SS 345 3415 TEMP SS 138 1 264.2 543.4 543.0 0.09565
C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
Open 3414 TEMP SS 345 3429 SANDOW 345 1
3074.7 3140.9 -66.2 L: 9074 LYTTON 345 7042 ZORN 34 345 1 389.2 1100.2 1100.0 0.23122
C:Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
3233.0 3205.5 27.4 L: 3429 SANDOW 345 7040 AUSTRO34 345 2 157.5 788.2 789.0 0.19508
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
3302.7 3308.0 -5.3 L: 3413 TEMPSSLT 345 3414 TEMP SS 345 1 147.2 1071.2 1072.0 0.27978
C:Open 3414 TEMP SS 345 3429 SANDOW 345 1
3724.8 3363.8 361.0 L:46500 TOMBAL 5 345 3391 JEWETT N 345 1 274.5 952.4 956.0 0.18199
C:Open 45500 T_H_W_ 5 345 3390 JEWETT S 345 1
Open 967 GIBCRK B 345 44500 OBRIEN 5 345 1
3489.1 3441.4 47.8 L: 1690 VALLEY 345 1692 PARIS SS 345 1 454.1 1050.4 1052.0 0.17089
C:Open 1692 PARIS SS 345 1695 MOSES 345 1
3501.5 3523.1 -21.6 L: 3414 TEMP SS 345 3429 SANDOW 345 1 90.6 957.1 956.0 0.24747
C:Open 3413 TEMPSSLT 345 3414 TEMP SS 345 1
3226.0 3524.3 -298.4 L: 7202 HICROS13 138 9147 HICRSMB2 138 1 216.0 477.5 480.0 0.08106
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
3894.0 3566.3 327.7 L: 967 GIBCRK B 345 44500 OBRIEN 5 345 1 362.0 1086.9 1088.0 0.18614
C:Open 45500 T_H_W_ 5 345 3390 JEWETT S 345 1
Open 46500 TOMBAL 5 345 3391 JEWETT N 345 1
4071.7 3588.2 483.5 L: 3390 JEWETT S 345 45500 T_H_W_ 5 345 1 236.4 956.1 956.0 0.17677
C:Open 40600 FRONTR 345 40900 KING 5 345 &1
Open 46500 TOMBAL 5 345 3391 JEWETT N 345 1
3483.7 3650.0 -166.2 L: 3415 TEMP SS 138 3675 ROGERS 138 1 104.3 184.8 186.0 0.02309
C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
Open 3414 TEMP SS 345 3429 SANDOW 345 1
3443.7 3729.9 -286.2 L: 7202 HICROS13 138 7500 TURNER13 138 1 157.1 437.2 440.0 0.08134
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
3641.5 3736.1 -94.6 L: 7040 AUSTRO34 345 7045 ZORN 34 345 1 330.0 1100.1 1100.0 0.21148
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
3863.7 3906.1 -42.4 L: 3414 TEMP SS 345 3429 SANDOW 345 1 200.1 956.1 956.0 0.19568
C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
3731.1 3913.9 -182.9 L: 9074 LYTTON 345 7042 ZORN 34 345 1 341.2 1101.2 1100.0 0.20370
C:Open 7040 AUSTRO34 345 7048 GARFIE34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
4501.8 4014.6 487.2 L:46500 TOMBAL 5 345 3391 JEWETT N 345 1 134.4 951.6 956.0 0.18151
C:Open 967 GIBCRK B 345 40600 FRONTR 345 1
Open 967 GIBCRK B 345 44500 OBRIEN 5 345 1
4173.2 4229.6 -56.4 L: 3409 LAKE CRK 345 3414 TEMP SS 345 1 220.8 957.0 956.0 0.17642
Base Case
4242.6 4314.5 -71.9 L: 3413 TEMPSSLT 345 3429 SANDOW 345 1 200.2 1068.2 1072.0 0.20460
C:Open 3414 TEMP SS 345 3429 SANDOW 345 1
4385.9 4372.9 13.0 L: 7040 AUSTRO34 345 7048 GARFIE34 345 1 323.5 1098.8 1100.0 0.17678
C:Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
4548.5 4444.9 103.6 L:46100 N_BELT 5 345 40900 KING 5 345 97 524.0 1087.6 1091.0 0.12391
C:Open 45500 T_H_W_ 5 345 3390 JEWETT S 345 1
Open 967 GIBCRK B 345 44500 OBRIEN 5 345 1
4004.7 4476.5 -471.8 L: 1692 PARIS SS 345 1695 MOSES 345 1 305.3 968.3 1052.0 0.16555
NotConv C:Open 1690 VALLEY 345 1692 PARIS SS 345 1
4657.6 4488.2 169.5 L: 3390 JEWETT S 345 45500 T_H_W_ 5 345 1 88.3 890.4 956.0 0.17222
NotConv C:Open 967 GIBCRK B 345 40600 FRONTR 345 1
Open 967 GIBCRK B 345 44500 OBRIEN 5 345 1
4477.8 4563.6 -85.7 L: 2428 WATMILLE 345 2432 TRICORN 345 1 172.5 1074.7 1072.0 0.20148
C:Open 3380 BIGBRN 345 3390 JEWETT S 345 1
Open 3380 BIGBRN 345 3391 JEWETT N 345 1
4606.7 4703.5 -96.8 L: 3429 SANDOW 345 3430 SANDOW 138 1 79.8 449.8 448.0 0.08032
C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
Open 3414 TEMP SS 345 3429 SANDOW 345 1
4705.1 4705.1 0.0 L: 3429 SANDOW 345 7040 AUSTRO34 345 1 97.4 717.9 716.0 0.13188
Base Case
4698.1 4756.8 -58.7 L: 9040 AUSTROP 345 7040 AUSTRO34 345 1 274.8 1125.7 1125.0 0.18112
C:Open 7040 AUSTRO34 345 7048 GARFIE34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
4257.2 4783.1 -525.9 L: 3429 SANDOW 345 3430 SANDOW 138 1 151.9 419.9 448.0 0.06296
NotConv C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
4758.7 4830.1 -71.4 L: 3405 T HOUSE 345 3414 TEMP SS 345 1 207.4 958.1 956.0 0.15775
Base Case
4772.3 4879.4 -107.1 L: 1690 VALLEY 345 1692 PARIS SS 345 1 552.5 1043.9 1052.0 0.10296
NotConv Base Case
4743.3 4930.2 -186.9 L: 3405 T HOUSE 345 3409 LAKE CRK 345 2 228.2 937.0 956.0 0.14943
NotConv C:Open 3405 T HOUSE 345 3414 TEMP SS 345 1
4113.4 5110.7 -997.3 L: 2428 WATMILLE 345 2432 TRICORN 345 1 104.8 933.1 1072.0 0.20137
NotConv C:Open 3123 TRINDAD1 345 3133 RICHLND1 345 1
Open 3124 TRINDAD2 345 3134 RICHLND2 345 1
4717.1 5117.2 -400.1 L: 3380 BIGBRN 345 3390 JEWETT S 345 1 233.8 830.5 956.0 0.12650
NotConv C:Open 3380 BIGBRN 345 3391 JEWETT N 345 1
4769.2 5133.0 -363.8 L: 3429 SANDOW 345 7040 AUSTRO34 345 2 97.4 730.1 789.0 0.13267
NotConv Base Case
4788.0 5144.2 -356.3 L: 967 GIBCRK B 345 44500 OBRIEN 5 345 1 281.3 807.1 906.0 0.10982
NotConv Base Case
3683.8 5188.3 -1504.5 L: 3116 TNSKGATE 345 3124 TRINDAD2 345 1 82.3 959.0 1072.0 0.23798
NotConv C:Open 3100 MARTINLK 345 3116 TNSKGATE 345 1
4752.5 5352.9 -600.3 L: 3413 TEMPSSLT 345 3414 TEMP SS 345 1 200.8 991.9 1072.0 0.16647
NotConv Base Case
4541.5 5413.4 -871.9 L:45972 KUYDAL 5 345 40600 FRONTR 345 75 546.6 1422.8 1662.0 0.19294
NotConv C:Open 45500 T_H_W_ 5 345 3390 JEWETT S 345 1
Open 967 GIBCRK B 345 44500 OBRIEN 5 345 1
4784.2 5445.0 -660.8 L:46500 TOMBAL 5 345 3391 JEWETT N 345 1 187.5 725.1 906.0 0.11236
NotConv Base Case
4778.4 5486.8 -708.4 L: 7042 ZORN 34 345 7045 ZORN 34 345 1 224.9 1010.2 1100.0 0.16433
NotConv C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
3675.0 5513.7 -1838.7 L: 3119 NACOG SE 345 3120 NACOG SE 138 1 65.9 399.6 512.0 0.09080
NotConv C:Open 3100 MARTINLK 345 3116 TNSKGATE 345 1
4531.7 5544.0 -1012.3 L:45972 KUYDAL 5 345 40900 KING 5 345 75 522.1 1395.3 1662.0 0.19269
NotConv C:Open 45500 T_H_W_ 5 345 3390 JEWETT S 345 1
Open 967 GIBCRK B 345 44500 OBRIEN 5 345 1

## RateB West to South
Study transfer. From WEST2001 To SOUTH2001 . Transfer level - 20000.0 MW
AC DC Delta L: Limiting constraint PreShft PostShf AC_TDF
FCITC FCITC FCITC C: Contingency description Ncon MVA/MW MVA/MW Rating
525.8 452.3 73.5 L: 1624 LEON 138 1640 LNGLVL M 138 1 36.1 84.0 84.0 0.09117
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
571.4 504.1 67.3 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 32.6 84.4 84.0 0.09060
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
599.7 601.6 -1.8 L: 1571 ORAN 138 1596 GRAHAMSS 138 1 109.9 186.1 186.0 0.12717
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
733.3 723.7 9.6 L: 1601 GRAHAM E 138 1431 GRAHAM P 138 1 160.4 251.6 251.0 0.12444
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
745.9 724.2 21.7 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 374.5 716.5 717.0 0.45850
C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
826.4 784.3 42.1 L: 1032 MRGN CRK 138 1341 SWTRDT T 138 1 112.6 189.2 186.0 0.09263
C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
887.7 882.6 5.1 L: 1596 GRAHAMSS 138 1601 GRAHAM E 138 1 141.3 252.6 251.0 0.12544
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1033.5 988.4 45.0 L: 1886 EV EAST 345 1422 BOWMAN 345 1 342.3 788.2 789.0 0.43147
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1040.6 1035.7 4.8 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 339.6 717.1 717.0 0.36283
C:Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1062.6 1053.2 9.4 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 230.0 716.2 717.0 0.45757
C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1107.8 1084.3 23.5 L: 1032 MRGN CRK 138 1341 SWTRDT T 138 1 87.6 189.2 186.0 0.09165
C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1170.8 1155.6 15.3 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 307.0 717.4 717.0 0.35049
C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
1063.2 1217.0 -153.8 L: 1430 GRAHAM 345 1431 GRAHAM P 138 1 190.6 350.6 350.0 0.15053
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1296.6 1265.8 30.7 L: 6100 OKLAEHV7 345 1425 FISHRDSS 345 1 408.2 716.9 717.0 0.23804
C:Open 6230 ABMULCE7 345 1430 GRAHAM 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1272.7 1399.0 -126.4 L: 1026 ODES EHV 345 1028 ODEHV 1T 345 1 101.2 528.7 526.0 0.33591
C:Open 1020 EHV TIET 345 1029 ODEHV 2T 345 1
1492.6 1402.6 90.0 L: 1430 GRAHAM 345 1436 PARKER 345 1 425.9 1054.3 1052.0 0.42101
C:Open 1430 GRAHAM 345 1436 PARKER 345 2
1492.6 1404.6 88.0 L: 1430 GRAHAM 345 1436 PARKER 345 2 425.9 1054.3 1052.0 0.42101
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
1197.1 1410.6 -213.5 L: 1339 ESKOTA 138 1341 SWTRDT T 138 1 87.1 217.5 214.0 0.10897
C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1448.3 1435.7 12.6 L: 1420 ENCOGEN 345 1430 GRAHAM 345 1 274.6 715.1 717.0 0.30411
C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1687.8 1638.3 49.5 L: 1420 ENCOGEN 345 1430 GRAHAM 345 1 239.9 715.0 717.0 0.28152
C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
1578.1 1651.2 -73.1 L: 1859 EAGLE MT 345 1436 PARKER 345 1 959.5 1192.7 1195.0 0.14782
C:Open 1436 PARKER 345 1853 ROANOKE 345 1
1362.0 1710.6 -348.6 L: 1339 ESKOTA 138 1341 SWTRDT T 138 1 61.9 204.7 214.0 0.10484
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1617.0 1728.6 -111.6 L: 7500 TURNER13 138 7501 GOFORT13 138 1 98.7 219.5 220.0 0.07473
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
1741.6 1760.9 -19.3 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 252.5 716.5 717.0 0.26644
Base Case
1489.1 1777.3 -288.3 L: 1026 ODES EHV 345 1028 ODEHV 1T 345 1 192.4 522.7 526.0 0.22182
C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1699.3 1830.5 -131.1 L: 7501 GOFORT13 138 7515 ROHR 13 138 1 91.8 219.6 220.0 0.07517
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
1699.7 1879.7 -180.0 L: 1020 EHV TIET 345 1029 ODEHV 2T 345 1 1.1 1192.9 1195.0 0.70118
C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1712.4 1879.7 -167.3 L: 1020 EHV TIET 345 1026 ODES EHV 345 1 1.1 1196.0 1195.0 0.69776
C:Open 1020 EHV TIET 345 1029 ODEHV 2T 345 1
1858.7 1886.1 -27.4 L: 1027 ODES EHV 138 1029 ODEHV 2T 345 1 187.9 681.0 680.0 0.26526
C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1472.0 1893.2 -421.2 L: 1422 BOWMAN 345 1430 GRAHAM 345 1 419.2 936.4 1072.0 0.35135
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1655.1 1906.8 -251.7 L: 1029 ODEHV 2T 345 1030 MRGN CRK 345 1 196.2 529.6 526.0 0.20146
C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1764.9 1914.1 -149.2 L: 7200 CANYON13 138 7515 ROHR 13 138 1 86.3 219.6 220.0 0.07553
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
1981.8 2093.8 -112.0 L: 6100 OKLAEHV7 345 1425 FISHRDSS 345 1 354.0 718.1 717.0 0.18372
C:Open 6230 ABMULCE7 345 1430 GRAHAM 345 1
1410.1 2104.2 -694.1 L: 1029 ODEHV 2T 345 1030 MRGN CRK 345 1 262.6 424.8 526.0 0.11508
NotConv C:Open 1028 ODEHV 1T 345 1030 MRGN CRK 345 1
1411.4 2106.2 -694.7 L: 1028 ODEHV 1T 345 1030 MRGN CRK 345 1 262.4 424.9 526.0 0.11515
NotConv C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
2117.0 2157.9 -41.0 L: 3405 T HOUSE 345 3409 LAKE CRK 345 2 391.8 893.9 956.0 0.23721
NotConv C:Open 3405 T HOUSE 345 3409 LAKE CRK 345 1
Open 3405 T HOUSE 345 3414 TEMP SS 345 1
1867.8 2160.9 -293.1 L: 6230 ABMULCE7 345 1430 GRAHAM 345 1 209.5 701.1 717.0 0.26321
NotConv C:Open 6100 OKLAEHV7 345 1425 FISHRDSS 345 1
2048.3 2232.2 -183.9 L: 1430 GRAHAM 345 1436 PARKER 345 1 302.3 998.1 1052.0 0.33970
NotConv C:Open 1422 BOWMAN 345 1886 EV EAST 345 1
1496.6 2233.3 -736.7 L: 1028 ODEHV 1T 345 1030 MRGN CRK 345 1 188.4 402.3 526.0 0.14291
NotConv C:Open 1020 EHV TIET 345 1029 ODEHV 2T 345 1
2048.3 2239.1 -190.8 L: 1430 GRAHAM 345 1436 PARKER 345 2 302.3 998.1 1052.0 0.33970
NotConv C:Open 1422 BOWMAN 345 1886 EV EAST 345 1
1730.9 2268.3 -537.4 L: 1030 MRGN CRK 345 1420 ENCOGEN 345 1 107.4 585.6 717.0 0.27627
NotConv C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1663.6 2269.7 -606.1 L: 1422 BOWMAN 345 1425 FISHRDSS 345 1 221.8 592.9 717.0 0.22308
NotConv C:Open 6230 ABMULCE7 345 1430 GRAHAM 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
2093.9 2280.9 -186.9 L: 6375 MENARD 4 138 6480 SAPS1 4 138 1 23.8 123.5 147.0 0.04765
NotConv Base Case
1842.2 2300.3 -458.2 L: 6230 ABMULCE7 345 1430 GRAHAM 345 1 126.5 600.0 717.0 0.25701
NotConv C:Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
2064.8 2322.9 -258.1 L: 7192 SANMAR13 138 7200 CANYON13 138 1 62.6 223.2 220.0 0.07775
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
2104.6 2363.2 -258.6 L: 3409 LAKE CRK 345 3414 TEMP SS 345 1 355.3 876.7 956.0 0.24774
NotConv C:Open 3405 T HOUSE 345 3414 TEMP SS 345 1
1969.7 2377.3 -407.6 L: 1020 EHV TIET 345 1026 ODES EHV 345 1 170.2 1222.1 1195.0 0.53406
NotConv C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
2028.4 2392.6 -364.2 L: 1027 ODES EHV 138 1028 ODEHV 1T 345 1 91.6 320.7 350.0 0.11296
NotConv C:Open 1020 EHV TIET 345 1029 ODEHV 2T 345 1
2089.9 2424.6 -334.8 L: 3409 LAKE CRK 345 3414 TEMP SS 345 1 348.0 856.8 956.0 0.24347
NotConv C:Open 3405 T HOUSE 345 3409 LAKE CRK 345 1
Open 3405 T HOUSE 345 3414 TEMP SS 345 1
2039.8 2429.8 -390.0 L: 1026 ODES EHV 345 1028 ODEHV 1T 345 1 106.9 527.9 526.0 0.20641
Base Case
2125.9 2443.9 -317.9 L: 1420 ENCOGEN 345 1430 GRAHAM 345 1 194.5 671.4 717.0 0.22432
NotConv Base Case
1877.0 2517.7 -640.7 L: 1030 MRGN CRK 345 1420 ENCOGEN 345 1 100.5 548.1 717.0 0.23851
NotConv C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
2082.2 2520.3 -438.1 L: 7332 ELGIN 13 138 3650 ELGIN SS 138 1 17.9 172.9 214.0 0.07444
NotConv C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
2119.0 2532.7 -413.7 L: 3405 T HOUSE 345 3414 TEMP SS 345 1 341.4 840.6 956.0 0.23557
NotConv C:Open 3409 LAKE CRK 345 3414 TEMP SS 345 1
2122.1 2619.2 -497.2 L: 1855 ALLIANCE 345 1859 EAGLE MT 345 1 830.1 1098.0 1195.0 0.12622
NotConv C:Open 1436 PARKER 345 1853 ROANOKE 345 1
2002.5 2620.4 -617.9 L: 1025 FS COGEN 345 1030 MRGN CRK 345 1 100.8 467.8 526.0 0.18326
NotConv C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
2003.9 2622.2 -618.3 L: 1025 FS COGEN 345 1030 MRGN CRK 345 1 100.8 467.9 526.0 0.18317
NotConv C:Open 1028 ODEHV 1T 345 1030 MRGN CRK 345 1
2016.2 2645.9 -629.7 L: 6230 ABMULCE7 345 6232 ABMULCK4 138 1 68.9 228.2 284.9 0.07905
NotConv C:Open 6230 ABMULCE7 345 6235 ABMULCW7 345 1
2056.4 2734.5 -678.1 L: 1020 EHV TIET 345 1029 ODEHV 2T 345 1 70.8 1097.9 1195.0 0.49947
NotConv C:Open 1026 ODES EHV 345 1028 ODEHV 1T 345 1
-2036.7 2736.3 -4773.0 L: 967 GIBCRK B 345 44500 OBRIEN 5 345 1 525.0 54.1 1088.0 0.23119
-NotConv C:Open 40600 FRONTR 345 40900 KING 5 345 &1
Open 46500 TOMBAL 5 345 3391 JEWETT N 345 1

## RateB West to North
Study transfer. From WEST2001 To NORTH2001 . Transfer level - 20000.0 MW
AC DC Delta L: Limiting constraint PreShft PostShf AC_TDF
FCITC FCITC FCITC C: Contingency description Ncon MVA/MW MVA/MW Rating
498.3 430.4 67.9 L: 1624 LEON 138 1640 LNGLVL M 138 1 36.1 83.9 84.0 0.09613
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
541.5 479.6 61.9 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 32.6 84.3 84.0 0.09551
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
522.4 524.0 -1.6 L: 1571 ORAN 138 1596 GRAHAMSS 138 1 109.9 186.1 186.0 0.14591
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
641.2 632.8 8.4 L: 1601 GRAHAM E 138 1431 GRAHAM P 138 1 160.4 252.2 251.0 0.14322
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
730.4 707.0 23.4 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 374.5 716.6 717.0 0.46840
C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
744.5 738.7 5.9 L: 1464 S WFALLS 138 1467 NORTHSTR 138 1 125.1 183.4 186.0 0.07827
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
776.2 771.8 4.4 L: 1596 GRAHAMSS 138 1601 GRAHAM E 138 1 141.3 252.5 251.0 0.14328
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
775.6 771.9 3.7 L: 1467 NORTHSTR 138 1468 AROWHEAD 138 1 122.6 183.2 186.0 0.07816
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
828.9 786.6 42.2 L: 1032 MRGN CRK 138 1341 SWTRDT T 138 1 112.6 189.0 186.0 0.09219
C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
794.5 792.6 2.0 L: 1468 AROWHEAD 138 1470 NEWPRT M 138 1 121.0 183.0 186.0 0.07805
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
814.5 831.4 -16.9 L: 1469 SUNSET 138 1470 NEWPRT M 138 1 119.4 183.0 186.0 0.07816
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
999.6 956.8 42.8 L: 1886 EV EAST 345 1422 BOWMAN 345 1 342.3 787.9 789.0 0.44569
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1040.6 1028.1 12.5 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 230.0 716.2 717.0 0.46725
C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1040.8 1035.0 5.9 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 339.6 717.3 717.0 0.36288
C:Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1111.1 1087.5 23.6 L: 1032 MRGN CRK 138 1341 SWTRDT T 138 1 87.6 188.9 186.0 0.09116
C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
970.1 1103.5 -133.4 L: 1430 GRAHAM 345 1431 GRAHAM P 138 1 190.6 351.2 350.0 0.16560
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1172.8 1155.8 17.0 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 307.0 717.9 717.0 0.35041
C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
1206.2 1177.6 28.6 L: 6100 OKLAEHV7 345 1425 FISHRDSS 345 1 408.2 718.5 717.0 0.25721
C:Open 6230 ABMULCE7 345 1430 GRAHAM 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1143.5 1249.0 -105.4 L: 1859 EAGLE MT 345 1436 PARKER 345 1 959.5 1194.3 1195.0 0.20532
C:Open 1436 PARKER 345 1853 ROANOKE 345 1
1406.0 1326.9 79.1 L: 1430 GRAHAM 345 1436 PARKER 345 1 425.9 1053.2 1052.0 0.44614
C:Open 1430 GRAHAM 345 1436 PARKER 345 2
1406.0 1328.8 77.3 L: 1430 GRAHAM 345 1436 PARKER 345 2 425.9 1053.2 1052.0 0.44614
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
1274.1 1395.0 -120.9 L: 1026 ODES EHV 345 1028 ODEHV 1T 345 1 101.2 530.8 526.0 0.33719
C:Open 1020 EHV TIET 345 1029 ODEHV 2T 345 1
1413.8 1401.5 12.3 L: 1420 ENCOGEN 345 1430 GRAHAM 345 1 274.6 713.0 717.0 0.31006
C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1201.7 1414.8 -213.0 L: 1339 ESKOTA 138 1341 SWTRDT T 138 1 87.1 218.3 214.0 0.10921
C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1632.4 1573.7 58.7 L: 1420 ENCOGEN 345 1430 GRAHAM 345 1 239.9 715.3 717.0 0.29126
C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
1369.6 1715.7 -346.1 L: 1339 ESKOTA 138 1341 SWTRDT T 138 1 61.9 205.0 214.0 0.10450
NotConv C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1738.9 1736.3 2.5 L: 1371 MURRAY M 138 1431 GRAHAM P 138 1 8.6 97.2 96.0 0.05095
Base Case
1485.5 1758.4 -272.9 L: 1026 ODES EHV 345 1028 ODEHV 1T 345 1 192.4 523.7 526.0 0.22305
C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1765.0 1786.2 -21.2 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 252.5 717.9 717.0 0.26369
Base Case
1503.8 1816.1 -312.3 L: 1422 BOWMAN 345 1430 GRAHAM 345 1 419.2 973.3 1072.0 0.36845
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1698.8 1879.7 -180.9 L: 1020 EHV TIET 345 1029 ODEHV 2T 345 1 1.1 1193.4 1195.0 0.70182
C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1705.6 1879.7 -174.2 L: 1020 EHV TIET 345 1026 ODES EHV 345 1 1.1 1196.4 1195.0 0.70078
C:Open 1020 EHV TIET 345 1029 ODEHV 2T 345 1
1634.5 1884.0 -249.6 L: 1029 ODEHV 2T 345 1030 MRGN CRK 345 1 196.2 529.1 526.0 0.20369
C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1834.8 1911.9 -77.2 L: 1027 ODES EHV 138 1029 ODEHV 2T 345 1 187.9 681.4 680.0 0.26893
C:Open 1020 EHV TIET 345 1026 ODES EHV 345 1
1887.3 1931.9 -44.6 L: 6100 OKLAEHV7 345 1425 FISHRDSS 345 1 354.0 714.9 717.0 0.19120
C:Open 6230 ABMULCE7 345 1430 GRAHAM 345 1
1863.0 1965.0 -102.0 L: 6230 ABMULCE7 345 1430 GRAHAM 345 1 209.5 721.6 717.0 0.27491
C:Open 6100 OKLAEHV7 345 1425 FISHRDSS 345 1
2077.1 1976.3 100.8 L: 1624 LEON 138 1640 LNGLVL M 138 1 18.4 79.9 84.0 0.02959
Base Case
2133.7 2031.7 102.1 L: 1855 ALLIANCE 345 1859 EAGLE MT 345 1 830.1 1187.3 1195.0 0.16738
NotConv C:Open 1436 PARKER 345 1853 ROANOKE 345 1
1386.2 2068.5 -682.3 L: 1029 ODEHV 2T 345 1030 MRGN CRK 345 1 262.6 422.1 526.0 0.11511
NotConv C:Open 1028 ODEHV 1T 345 1030 MRGN CRK 345 1
1387.5 2070.4 -683.0 L: 1028 ODEHV 1T 345 1030 MRGN CRK 345 1 262.4 422.1 526.0 0.11514
NotConv C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
2138.5 2084.2 54.3 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 23.7 80.3 84.0 0.02644
Base Case
1824.6 2114.1 -289.6 L: 6230 ABMULCE7 345 1430 GRAHAM 345 1 126.5 615.1 717.0 0.26778
NotConv C:Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1699.6 2132.0 -432.5 L: 1422 BOWMAN 345 1425 FISHRDSS 345 1 221.8 627.8 717.0 0.23886
NotConv C:Open 6230 ABMULCE7 345 1430 GRAHAM 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
2082.5 2135.5 -52.9 L: 1430 GRAHAM 345 1436 PARKER 345 1 302.3 1021.1 1052.0 0.34516
NotConv C:Open 1422 BOWMAN 345 1886 EV EAST 345 1
2082.5 2142.1 -59.5 L: 1430 GRAHAM 345 1436 PARKER 345 2 302.3 1021.1 1052.0 0.34516
NotConv C:Open 1422 BOWMAN 345 1886 EV EAST 345 1
1478.2 2205.8 -727.6 L: 1028 ODEHV 1T 345 1030 MRGN CRK 345 1 188.4 400.1 526.0 0.14320
NotConv C:Open 1020 EHV TIET 345 1029 ODEHV 2T 345 1
1758.2 2214.3 -456.1 L: 1030 MRGN CRK 345 1420 ENCOGEN 345 1 107.4 602.3 717.0 0.28152
NotConv C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
2164.9 2347.5 -182.5 L: 1420 ENCOGEN 345 1430 GRAHAM 345 1 194.5 693.5 717.0 0.23050
NotConv Base Case
1970.9 2359.2 -388.4 L: 1020 EHV TIET 345 1026 ODES EHV 345 1 170.2 1216.8 1195.0 0.53105
NotConv C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
1972.6 2411.8 -439.2 L: 1026 ODES EHV 345 1028 ODEHV 1T 345 1 106.9 496.0 526.0 0.19726
NotConv Base Case
1915.9 2418.3 -502.4 L: 1030 MRGN CRK 345 1420 ENCOGEN 345 1 100.5 570.5 717.0 0.24531
NotConv C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
2051.5 2440.4 -388.9 L: 1027 ODES EHV 138 1028 ODEHV 1T 345 1 91.6 326.7 350.0 0.11461
NotConv C:Open 1020 EHV TIET 345 1029 ODEHV 2T 345 1
2167.3 2548.3 -381.0 L: 1571 ORAN 138 1596 GRAHAMSS 138 1 36.1 162.4 186.0 0.05829
NotConv Base Case
2040.7 2567.9 -527.2 L: 1025 FS COGEN 345 1030 MRGN CRK 345 1 100.8 484.4 526.0 0.18798
NotConv C:Open 1029 ODEHV 2T 345 1030 MRGN CRK 345 1
2042.1 2569.6 -527.6 L: 1025 FS COGEN 345 1030 MRGN CRK 345 1 100.8 484.4 526.0 0.18783
NotConv C:Open 1028 ODEHV 1T 345 1030 MRGN CRK 345 1
2159.7 2647.2 -487.5 L: 3134 RICHLND2 345 3380 BIGBRN 345 1 591.0 932.8 956.0 0.15827
NotConv C:Open 3100 MARTINLK 345 3116 TNSKGATE 345 1
2169.4 2654.7 -485.3 L: 3124 TRINDAD2 345 3134 RICHLND2 345 1 591.4 937.4 956.0 0.15948
NotConv C:Open 3100 MARTINLK 345 3116 TNSKGATE 345 1
2055.0 2696.7 -641.8 L: 6230 ABMULCE7 345 6232 ABMULCK4 138 1 68.9 231.0 284.9 0.07889
NotConv C:Open 6230 ABMULCE7 345 6235 ABMULCW7 345 1
2148.7 2700.7 -552.1 L: 1430 GRAHAM 345 1436 PARKER 345 1 273.9 882.1 1052.0 0.28307
NotConv Base Case
2148.7 2708.7 -560.1 L: 1430 GRAHAM 345 1436 PARKER 345 2 273.9 882.1 1052.0 0.28307
NotConv Base Case

## RateB South to North
Study transfer. From SOUTH2001 To NORTH2001 . Transfer level - 20000.0 MW
AC DC Delta L: Limiting constraint PreShft PostShf AC_TDF
FCITC FCITC FCITC C: Contingency description Ncon MVA/MW MVA/MW Rating
419.5 538.0 -118.5 L: 1906 VENUS S 345 2420 C HILL 345 1 1018.0 1072.3 1072.0 0.12943
C:Open 1882 EV WEST 345 1906 VENUS S 345 1
Open 1886 EV EAST 345 1907 VENUS N 345 1
582.7 659.9 -77.2 L: 1882 EV WEST 345 1906 VENUS S 345 1 884.8 956.5 956.0 0.12305
C:Open 1906 VENUS S 345 2420 C HILL 345 1
1035.6 1067.8 -32.2 L: 3415 TEMP SS 138 3675 ROGERS 138 1 104.3 188.0 186.0 0.08082
C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
Open 3414 TEMP SS 345 3429 SANDOW 345 1
1909.8 1941.1 -31.3 L: 3429 SANDOW 345 7040 AUSTRO34 345 1 157.5 718.6 716.0 0.29380
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 2
2159.4 2190.7 -31.3 L: 3429 SANDOW 345 7040 AUSTRO34 345 2 157.5 793.7 789.0 0.29462
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
2045.3 2237.8 -192.5 L: 3380 BIGBRN 345 3390 JEWETT S 345 1 470.2 958.5 956.0 0.23877
C:Open 46020 LIMEST 5 345 2428 WATMILLE 345 1
Open 46020 LIMEST 5 345 2435 WATMLLDB 345 2
2301.8 2324.3 -22.6 L: 1906 VENUS S 345 3405 T HOUSE 345 1 499.0 957.1 956.0 0.19904
C:Open 1907 VENUS N 345 3405 T HOUSE 345 1
2275.2 2331.2 -56.1 L: 9040 AUSTROP 345 7040 AUSTRO34 345 1 532.9 1126.3 1125.0 0.26079
C:Open 9074 LYTTON 345 7048 GARFIE34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
2292.5 2369.9 -77.5 L: 7334 MCNEIL13 138 9079 MCNEILN 138 1 58.1 304.1 304.0 0.10734
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
2384.0 2455.3 -71.4 L: 7332 ELGIN 13 138 3650 ELGIN SS 138 1 17.9 214.9 214.0 0.08263
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
2206.3 2478.2 -271.9 L: 3380 BIGBRN 345 3391 JEWETT N 345 1 511.0 1068.9 1072.0 0.25285
C:Open 46020 LIMEST 5 345 2428 WATMILLE 345 1
Open 46020 LIMEST 5 345 2435 WATMLLDB 345 2
2312.5 2610.2 -297.6 L: 3380 BIGBRN 345 3390 JEWETT S 345 1 355.6 952.6 956.0 0.25815
C:Open 1906 VENUS S 345 3405 T HOUSE 345 1
Open 1907 VENUS N 345 3405 T HOUSE 345 1
2613.9 2705.5 -91.5 L: 3414 TEMP SS 345 3429 SANDOW 345 1 200.1 956.6 956.0 0.28940
C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
2681.8 2765.6 -83.8 L: 1907 VENUS N 345 3405 T HOUSE 345 1 518.6 1075.2 1072.0 0.20754
C:Open 1906 VENUS S 345 3405 T HOUSE 345 1
2645.3 2861.6 -216.3 L: 1906 VENUS S 345 3405 T HOUSE 345 1 408.9 955.1 956.0 0.20645
C:Open 3380 BIGBRN 345 3390 JEWETT S 345 1
Open 3380 BIGBRN 345 3391 JEWETT N 345 1
2885.2 2985.3 -100.1 L: 9040 AUSTROP 345 7040 AUSTRO34 345 1 274.8 1125.7 1125.0 0.29495
C:Open 7040 AUSTRO34 345 7048 GARFIE34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
2958.0 3096.9 -138.9 L: 3134 RICHLND2 345 3380 BIGBRN 345 1 476.1 955.1 956.0 0.16195
Base Case
2958.2 3103.4 -145.2 L: 3124 TRINDAD2 345 3134 RICHLND2 345 1 477.1 955.5 956.0 0.16172
Base Case
2980.7 3110.5 -129.8 L: 3413 TEMPSSLT 345 3429 SANDOW 345 1 200.2 1073.6 1072.0 0.29302
C:Open 3414 TEMP SS 345 3429 SANDOW 345 1
2751.1 3146.1 -394.9 L: 1907 VENUS N 345 1911 WEBB 1 345 1 887.3 1070.7 1072.0 0.06666
Base Case
3082.0 3201.2 -119.2 L: 7334 MCNEIL13 138 7336 GILLEL13 138 1 18.0 220.3 220.0 0.06566
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
2933.2 3201.9 -268.8 L: 3429 SANDOW 345 3430 SANDOW 138 1 151.9 449.8 448.0 0.10156
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
2933.5 3248.1 -314.7 L: 1907 VENUS N 345 3405 T HOUSE 345 1 435.4 1070.1 1072.0 0.21636
C:Open 3380 BIGBRN 345 3390 JEWETT S 345 1
Open 3380 BIGBRN 345 3391 JEWETT N 345 1
3213.6 3290.9 -77.3 L: 7192 SANMAR13 138 7200 CANYON13 138 1 62.6 219.6 220.0 0.04884
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
3430.3 3406.4 23.9 L: 3414 TEMP SS 345 3415 TEMP SS 138 1 180.7 544.8 543.0 0.10614
C:Open 3409 LAKE CRK 345 3414 TEMP SS 345 1
Open 3405 T HOUSE 345 3414 TEMP SS 345 1
3002.6 3609.0 -606.4 L:40000 CEDARP 5 345 40255 CHAMBR 5 345 97 621.2 901.7 906.0 0.09342
Base Case
3227.7 3619.7 -392.0 L: 3380 BIGBRN 345 3391 JEWETT N 345 1 228.5 1070.2 1072.0 0.26076
C:Open 3380 BIGBRN 345 3390 JEWETT S 345 1
3459.7 3635.8 -176.2 L: 3414 TEMP SS 345 3429 SANDOW 345 1 90.6 959.7 956.0 0.25120
C:Open 3413 TEMPSSLT 345 3414 TEMP SS 345 1
3515.0 3690.3 -175.3 L: 3429 SANDOW 345 7040 AUSTRO34 345 1 97.4 715.1 716.0 0.17573
Base Case
3360.2 3718.1 -358.0 L: 5915 SO TEX 5 345 44000 W_A_P_ 5 345 39 539.8 1007.1 1088.0 0.13906
NotConv C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
Open 3414 TEMP SS 345 3429 SANDOW 345 1
3535.4 3762.4 -227.0 L: 5915 SO TEX 5 345 44000 W_A_P_ 5 345 39 534.5 1018.4 1088.0 0.13688
NotConv C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
3520.6 3779.2 -258.6 L: 2432 TRICORN 345 2433 SGVL SS 345 1 634.1 1076.6 1072.0 0.12570
Base Case
3766.2 3911.0 -144.9 L: 7200 CANYON13 138 7515 ROHR 13 138 1 86.3 218.5 220.0 0.03510
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
3570.8 3952.1 -381.3 L: 3650 ELGIN SS 138 3430 SANDOW 138 1 65.8 211.2 214.0 0.04073
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
3807.2 3987.7 -180.5 L: 7501 GOFORT13 138 7515 ROHR 13 138 1 91.8 216.2 220.0 0.03267
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
3694.3 4007.6 -313.4 L: 3410 LAKE CRK 138 3415 TEMP SS 138 1 109.8 188.9 186.0 0.02139
C:Open 3409 LAKE CRK 345 3414 TEMP SS 345 1
Open 3405 T HOUSE 345 3414 TEMP SS 345 1
3896.3 4081.0 -184.7 L: 7500 TURNER13 138 7501 GOFORT13 138 1 98.7 217.4 220.0 0.03046
C:Open 9074 LYTTON 345 7042 ZORN 34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
3876.8 4118.2 -241.4 L: 3429 SANDOW 345 7040 AUSTRO34 345 2 97.4 787.7 789.0 0.17807
Base Case
3375.5 4132.0 -756.4 L: 3429 SANDOW 345 3430 SANDOW 138 1 79.8 406.2 448.0 0.09669
NotConv C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
Open 3414 TEMP SS 345 3429 SANDOW 345 1
3803.0 4160.5 -357.4 L: 3413 TEMPSSLT 345 3414 TEMP SS 345 1 147.2 1046.6 1072.0 0.23650
NotConv C:Open 3414 TEMP SS 345 3429 SANDOW 345 1
3566.4 4206.5 -640.1 L: 9076 MCNEILW 138 9079 MCNEILN 138 1 130.6 458.6 480.0 0.09197
NotConv C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
3780.2 4212.8 -432.6 L: 9040 AUSTROP 345 7040 AUSTRO34 345 1 591.4 1013.9 1010.0 0.11175
Base Case
3862.2 4216.0 -353.8 L: 5915 SO TEX 5 345 44000 W_A_P_ 5 345 39 507.3 831.7 906.0 0.08399
NotConv Base Case
3772.9 4280.6 -507.7 L: 2410 NORWOODT 345 2420 C HILL 345 1 823.8 1137.7 1133.0 0.08319
Base Case
3885.9 4306.6 -420.7 L: 1906 VENUS S 345 3405 T HOUSE 345 1 359.2 939.1 956.0 0.14923
NotConv Base Case
3560.8 4314.4 -753.6 L: 1911 WEBB 1 345 1916 LIG2 T 345 1 818.4 1075.8 1072.0 0.07230
Base Case
3546.6 4362.4 -815.8 L: 3658 TAYLOR 138 3659 THORNDAL 138 1 95.6 179.6 214.0 0.02367
NotConv C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
3545.1 4440.6 -895.4 L: 3659 THORNDAL 138 3661 SALTY M 138 1 100.5 174.4 214.0 0.02084
NotConv C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
3611.0 4460.5 -849.5 L: 967 GIBCRK B 345 40600 FRONTR 345 1 336.9 1186.8 1195.0 0.23536
NotConv C:Open 45500 T_H_W_ 5 345 3390 JEWETT S 345 1
Open 46500 TOMBAL 5 345 3391 JEWETT N 345 1
3536.7 4491.7 -955.0 L: 3661 SALTY M 138 3430 SANDOW 138 1 103.6 170.0 214.0 0.01878
NotConv C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
3712.6 4555.8 -843.2 L: 967 GIBCRK B 345 40600 FRONTR 345 1 260.9 1184.8 1195.0 0.24885
NotConv C:Open 45500 T_H_W_ 5 345 3390 JEWETT S 345 1
Open 967 GIBCRK B 345 44500 OBRIEN 5 345 1
3837.9 4586.6 -748.7 L: 3409 LAKE CRK 345 3414 TEMP SS 345 1 355.3 821.0 956.0 0.12132
NotConv C:Open 3405 T HOUSE 345 3414 TEMP SS 345 1
3840.8 4630.5 -789.8 L: 3409 LAKE CRK 345 3414 TEMP SS 345 1 348.0 810.2 956.0 0.12034
NotConv C:Open 3405 T HOUSE 345 3409 LAKE CRK 345 1
Open 3405 T HOUSE 345 3414 TEMP SS 345 1
3242.5 4700.4 -1457.9 L: 2428 WATMILLE 345 2432 TRICORN 345 1 107.4 890.9 1072.0 0.24164
NotConv C:Open 3133 RICHLND1 345 3380 BIGBRN 345 1
Open 3134 RICHLND2 345 3380 BIGBRN 345 1
3234.0 4702.8 -1468.9 L: 2428 WATMILLE 345 2432 TRICORN 345 1 104.8 886.4 1072.0 0.24170
NotConv C:Open 3123 TRINDAD1 345 3133 RICHLND1 345 1
Open 3124 TRINDAD2 345 3134 RICHLND2 345 1
2701.8 4750.5 -2048.7 L: 3116 TNSKGATE 345 3124 TRINDAD2 345 1 82.3 842.5 1072.0 0.28137
NotConv C:Open 3100 MARTINLK 345 3116 TNSKGATE 345 1
3894.2 4750.6 -856.4 L: 1907 VENUS N 345 3405 T HOUSE 345 1 386.8 1001.5 1072.0 0.15785
NotConv Base Case
3880.1 4772.6 -892.6 L: 3405 T HOUSE 345 3414 TEMP SS 345 1 341.4 792.7 956.0 0.11631
NotConv C:Open 3409 LAKE CRK 345 3414 TEMP SS 345 1
3932.7 4798.4 -865.7 L: 1906 VENUS S 345 2420 C HILL 345 1 719.0 1050.1 1072.0 0.08417
NotConv Base Case
3232.5 4913.4 -1680.8 L: 1907 VENUS N 345 3380 BIGBRN 345 1 510.2 890.9 956.0 0.11778
NotConv C:Open 3133 RICHLND1 345 3380 BIGBRN 345 1
Open 3134 RICHLND2 345 3380 BIGBRN 345 1