## AC FCITC Summary
AC FCITC Multiple Transfers Report
*** MUST 4.00 *** WED, APR 25 2001 15:37 ***
01SUM1N - 2001 SUMMER ON-PEAK BASE CASE - ERCOT ESC SSTF
PASS 8 - 12/01/00 - ERCOT
Subsys.File D:\ATC_3zones_01\Gens_2csc_3z_sans_offline.sub
Monit.File D:\allmon_.mon
Contin.File D:\Wichita\All_contingencies.con
Exclud.File D:\Wichita\excludefile.exc
Study transfer. From NORTH2001 To SOUTH2001 . Transfer level - 2500.0 MW
AC DC Delta L: Limiting constraint PreShft PostShf AC_TDF
FCITC FCITC FCITC C: Contingency description Ncon MVA/MW MVA/MW Rating
2262.2 2223.7 38.4 L: 3405 T HOUSE 345 3409 LAKE CRK 345 2 391.8 956.9 956.0 0.24981
C:Open 3405 T HOUSE 345 3409 LAKE CRK 345 1
Open 3405 T HOUSE 345 3414 TEMP SS 345 1
2399.5 2268.6 130.9 L: 967 GIBCRK B 345 44500 OBRIEN 5 345 1 525.0 1087.6 1088.0 0.23446
C:Open 40600 FRONTR 345 40900 KING 5 345 &1
Open 46500 TOMBAL 5 345 3391 JEWETT N 345 1
Study transfer. From NORTH2001 To WEST2001 . Transfer level - 2500.0 MW
AC DC Delta L: Limiting constraint PreShft PostShf AC_TDF
FCITC FCITC FCITC C: Contingency description Ncon MVA/MW MVA/MW Rating
824.9 836.1 -11.2 L: 1869 BENB A T 345 1873 BENBRK 345 1 858.4 1050.3 1052.0 0.23269
C:Open 1436 PARKER 345 1900 COM PEAK 345 1
1071.4 971.4 100.0 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 32.6 83.6 84.0 0.04761
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1123.9 1018.9 105.0 L: 1624 LEON 138 1640 LNGLVL M 138 1 36.1 83.3 84.0 0.04202
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1306.7 1081.2 225.5 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 23.7 84.4 84.0 0.04643
Base Case
1408.4 1180.7 227.7 L: 1624 LEON 138 1640 LNGLVL M 138 1 18.4 85.0 84.0 0.04728
Base Case
1738.6 1864.9 -126.3 L: 1571 ORAN 138 1596 GRAHAMSS 138 1 109.9 188.7 186.0 0.04535
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
2079.9 2020.2 59.7 L: 1574 PALOPNTO 138 1578 PALOPT M 138 1 208.2 325.6 326.0 0.05647
Base Case
1917.3 2044.1 -126.8 L: 1869 BENB A T 345 1873 BENBRK 345 1 839.7 1050.7 1052.0 0.11002
C:Open 1870 BENB B T 345 1873 BENBRK 345 1
2096.5 2056.9 39.6 L: 1574 PALOPNTO 138 1576 MINWLJCT 138 1 207.2 325.6 326.0 0.05646
Base Case
2142.0 2278.0 -135.9 L: 1869 BENB A T 345 1436 PARKER 345 1 444.7 1056.9 1052.0 0.28580
C:Open 1436 PARKER 345 1900 COM PEAK 345 1
2352.8 2338.7 14.2 L: 1575 MINWL W 138 1576 MINWLJCT 138 1 102.1 252.6 249.0 0.06396
Base Case
2189.8 2467.1 -277.3 L: 1886 EV EAST 345 1422 BOWMAN 345 1 342.3 797.2 789.0 0.20772
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
2295.4 2480.4 -185.1 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 230.0 718.5 717.0 0.21283
C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
Study transfer. From SOUTH2001 To NORTH2001 . Transfer level - 2500.0 MW
AC DC Delta L: Limiting constraint PreShft PostShf AC_TDF
FCITC FCITC FCITC C: Contingency description Ncon MVA/MW MVA/MW Rating
446.5 572.6 -126.2 L: 1906 VENUS S 345 2420 C HILL 345 1 1018.0 1073.4 1072.0 0.12419
C:Open 1882 EV WEST 345 1906 VENUS S 345 1
Open 1886 EV EAST 345 1907 VENUS N 345 1
850.2 965.2 -115.0 L: 1906 VENUS S 345 2420 C HILL 345 1 974.9 1075.2 1072.0 0.11793
C:Open 1882 EV WEST 345 1906 VENUS S 345 1
1204.6 1242.0 -37.5 L: 3415 TEMP SS 138 3675 ROGERS 138 1 104.3 188.2 186.0 0.06964
C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
Open 3414 TEMP SS 345 3429 SANDOW 345 1
2247.6 2309.9 -62.3 L: 3429 SANDOW 345 7040 AUSTRO34 345 1 157.5 716.6 716.0 0.24876
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 2
2082.2 2317.8 -235.6 L: 3380 BIGBRN 345 3390 JEWETT S 345 1 470.2 955.6 956.0 0.23316
C:Open 46020 LIMEST 5 345 2428 WATMILLE 345 1
Open 46020 LIMEST 5 345 2435 WATMLLDB 345 2
2374.3 2439.6 -65.3 L: 1906 VENUS S 345 3405 T HOUSE 345 1 499.0 958.5 956.0 0.19355
C:Open 1907 VENUS N 345 3405 T HOUSE 345 1
2179.1 2441.2 -262.1 L: 3380 BIGBRN 345 3391 JEWETT N 345 1 511.0 1069.1 1072.0 0.25609
C:Open 46020 LIMEST 5 345 2428 WATMILLE 345 1
Open 46020 LIMEST 5 345 2435 WATMLLDB 345 2
Study transfer. From SOUTH2001 To WEST2001 . Transfer level - 2500.0 MW
AC DC Delta L: Limiting constraint PreShft PostShf AC_TDF
FCITC FCITC FCITC C: Contingency description Ncon MVA/MW MVA/MW Rating
337.2 432.5 -95.3 L: 1906 VENUS S 345 2420 C HILL 345 1 1018.0 1070.7 1072.0 0.15637
C:Open 1882 EV WEST 345 1906 VENUS S 345 1
Open 1886 EV EAST 345 1907 VENUS N 345 1
715.9 725.6 -9.7 L: 1869 BENB A T 345 1873 BENBRK 345 1 858.4 1049.6 1052.0 0.26721
C:Open 1436 PARKER 345 1900 COM PEAK 345 1
665.4 755.4 -90.0 L: 1906 VENUS S 345 2420 C HILL 345 1 974.9 1071.2 1072.0 0.14461
C:Open 1882 EV WEST 345 1906 VENUS S 345 1
1144.1 1039.9 104.1 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 32.6 83.7 84.0 0.04461
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1199.3 1090.8 108.5 L: 1624 LEON 138 1640 LNGLVL M 138 1 36.1 83.4 84.0 0.03946
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1454.6 1201.6 253.0 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 23.7 85.1 84.0 0.04220
Base Case
1558.5 1312.1 246.4 L: 1624 LEON 138 1640 LNGLVL M 138 1 18.4 85.0 84.0 0.04271
Base Case
1684.6 1796.1 -111.4 L: 1869 BENB A T 345 1873 BENBRK 345 1 839.7 1049.2 1052.0 0.12433
C:Open 1870 BENB B T 345 1873 BENBRK 345 1
1985.6 2112.0 -126.4 L: 1869 BENB A T 345 1436 PARKER 345 1 444.7 1054.8 1052.0 0.30726
C:Open 1436 PARKER 345 1900 COM PEAK 345 1
1997.5 2214.2 -216.8 L: 1571 ORAN 138 1596 GRAHAMSS 138 1 109.9 190.0 186.0 0.04010
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
2233.9 2394.5 -160.6 L: 1906 VENUS S 345 3405 T HOUSE 345 1 499.0 952.9 956.0 0.20319
C:Open 1907 VENUS N 345 3405 T HOUSE 345 1
2223.5 2446.9 -223.4 L: 2427 WATMILLW 345 2420 C HILL 345 1 491.9 960.0 956.0 0.21052
C:Open 1906 VENUS S 345 3380 BIGBRN 345 1
Open 1907 VENUS N 345 3380 BIGBRN 345 1
1667.4 2488.1 -820.7 L: 1886 EV EAST 345 1422 BOWMAN 345 1 342.3 484.1 789.0 0.08506
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
Study transfer. From WEST2001 To NORTH2001 . Transfer level - 2500.0 MW
AC DC Delta L: Limiting constraint PreShft PostShf AC_TDF
FCITC FCITC FCITC C: Contingency description Ncon MVA/MW MVA/MW Rating
487.5 414.6 72.9 L: 1624 LEON 138 1640 LNGLVL M 138 1 36.1 83.7 84.0 0.09784
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
529.9 462.0 67.8 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 32.6 84.1 84.0 0.09719
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
480.2 481.6 -1.5 L: 1571 ORAN 138 1596 GRAHAMSS 138 1 109.9 184.7 186.0 0.15585
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
586.1 578.5 7.7 L: 1601 GRAHAM E 138 1431 GRAHAM P 138 1 160.4 250.3 251.0 0.15345
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
709.5 705.5 4.1 L: 1596 GRAHAMSS 138 1601 GRAHAM E 138 1 141.3 250.4 251.0 0.15372
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
751.7 745.8 5.9 L: 1464 S WFALLS 138 1467 NORTHSTR 138 1 125.1 182.3 186.0 0.07606
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
783.1 779.3 3.7 L: 1467 NORTHSTR 138 1468 AROWHEAD 138 1 122.6 182.1 186.0 0.07609
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
802.2 800.2 2.0 L: 1468 AROWHEAD 138 1470 NEWPRT M 138 1 121.0 182.0 186.0 0.07598
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
822.4 839.4 -17.0 L: 1469 SUNSET 138 1470 NEWPRT M 138 1 119.4 181.9 186.0 0.07603
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
974.5 914.2 60.3 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 374.5 715.1 717.0 0.34958
C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1032.3 970.6 61.7 L: 1886 EV EAST 345 1422 BOWMAN 345 1 342.3 791.0 789.0 0.43467
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1107.5 1180.6 -73.1 L: 1019 MOSS 138 1292 ECTR HRP 138 1 133.8 189.5 191.0 0.05030
Base Case
1123.4 1248.3 -124.9 L: 1430 GRAHAM 345 1431 GRAHAM P 138 1 190.6 350.8 350.0 0.14258
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1221.0 1319.8 -98.8 L: 1859 EAGLE MT 345 1436 PARKER 345 1 959.5 1193.0 1195.0 0.19128
C:Open 1436 PARKER 345 1853 ROANOKE 345 1
1421.9 1327.8 94.2 L: 1430 GRAHAM 345 1436 PARKER 345 1 425.9 1052.7 1052.0 0.44079
C:Open 1430 GRAHAM 345 1436 PARKER 345 2
1382.3 1329.5 52.8 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 230.0 721.2 717.0 0.35531
C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1421.9 1329.6 92.3 L: 1430 GRAHAM 345 1436 PARKER 345 2 425.9 1052.7 1052.0 0.44079
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
1409.4 1365.0 44.3 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 339.6 716.5 717.0 0.26742
C:Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1381.6 1376.1 5.5 L: 1010 PERMIANB 138 1292 ECTR HRP 138 1 138.6 208.1 210.0 0.05028
Base Case
1464.6 1429.9 34.7 L: 6100 OKLAEHV7 345 1425 FISHRDSS 345 1 408.2 713.4 717.0 0.20838
C:Open 6230 ABMULCE7 345 1430 GRAHAM 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1582.6 1525.5 57.1 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 307.0 718.6 717.0 0.26008
C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
1543.7 1750.6 -206.9 L: 1422 BOWMAN 345 1430 GRAHAM 345 1 419.2 999.2 1072.0 0.37569
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1871.6 1812.4 59.2 L: 1420 ENCOGEN 345 1430 GRAHAM 345 1 274.6 718.2 717.0 0.23701
C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
2074.6 1822.9 251.7 L: 1624 LEON 138 1640 LNGLVL M 138 1 18.4 84.8 84.0 0.03199
Base Case
2134.6 1922.3 212.3 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 23.7 84.5 84.0 0.02844
Base Case
2110.9 2008.3 102.6 L: 1420 ENCOGEN 345 1430 GRAHAM 345 1 239.9 714.9 717.0 0.22505
C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
2145.2 2094.7 50.4 L: 1571 ORAN 138 1596 GRAHAMSS 138 1 36.1 186.4 186.0 0.07005
Base Case
2204.4 2150.9 53.4 L: 1430 GRAHAM 345 1436 PARKER 345 1 302.3 1047.5 1052.0 0.33806
C:Open 1422 BOWMAN 345 1886 EV EAST 345 1
2204.4 2157.6 46.8 L: 1430 GRAHAM 345 1436 PARKER 345 2 302.3 1047.5 1052.0 0.33806
C:Open 1422 BOWMAN 345 1886 EV EAST 345 1
2150.0 2181.5 -31.6 L: 1030 MRGN CRK 345 1032 MRGN CRK 138 2 33.1 340.5 341.0 0.14294
C:Open 1030 MRGN CRK 345 1032 MRGN CRK 138 1
2164.3 2197.8 -33.5 L: 1030 MRGN CRK 345 1032 MRGN CRK 138 1 33.9 348.1 349.0 0.14515
C:Open 1030 MRGN CRK 345 1032 MRGN CRK 138 2
2370.5 2335.1 35.4 L: 1601 GRAHAM E 138 1431 GRAHAM P 138 1 85.3 255.2 251.0 0.07168
Base Case
2330.5 2387.2 -56.7 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 252.5 720.3 717.0 0.20075
Base Case
2409.4 2454.1 -44.7 L: 1855 ALLIANCE 345 1859 EAGLE MT 345 1 830.1 1153.0 1195.0 0.13401
NotConv C:Open 1436 PARKER 345 1853 ROANOKE 345 1
Study transfer. From WEST2001 To SOUTH2001 . Transfer level - 2500.0 MW
AC DC Delta L: Limiting constraint PreShft PostShf AC_TDF
FCITC FCITC FCITC C: Contingency description Ncon MVA/MW MVA/MW Rating
524.9 443.8 81.1 L: 1624 LEON 138 1640 LNGLVL M 138 1 36.1 83.8 84.0 0.09093
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
570.5 494.6 75.9 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 32.6 84.2 84.0 0.09035
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
570.1 571.8 -1.7 L: 1571 ORAN 138 1596 GRAHAMSS 138 1 109.9 184.4 186.0 0.13071
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
691.4 682.3 9.1 L: 1601 GRAHAM E 138 1431 GRAHAM P 138 1 160.4 250.3 251.0 0.13011
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
836.9 832.1 4.8 L: 1596 GRAHAMSS 138 1601 GRAHAM E 138 1 141.3 249.8 251.0 0.12964
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
994.7 938.5 56.2 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 374.5 715.1 717.0 0.34242
C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1043.9 978.9 65.0 L: 1886 EV EAST 345 1422 BOWMAN 345 1 342.3 790.2 789.0 0.42901
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1125.3 1199.6 -74.3 L: 1019 MOSS 138 1292 ECTR HRP 138 1 133.8 189.5 191.0 0.04953
Base Case
1410.8 1364.9 45.9 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 230.0 720.5 717.0 0.34769
C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1409.7 1366.2 43.5 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 339.6 717.4 717.0 0.26797
C:Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1479.3 1375.4 104.0 L: 1430 GRAHAM 345 1436 PARKER 345 1 425.9 1053.2 1052.0 0.42408
C:Open 1430 GRAHAM 345 1436 PARKER 345 2
1479.3 1377.3 102.1 L: 1430 GRAHAM 345 1436 PARKER 345 2 425.9 1053.2 1052.0 0.42408
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
1403.8 1398.2 5.6 L: 1010 PERMIANB 138 1292 ECTR HRP 138 1 138.6 208.3 210.0 0.04968
Base Case
1292.6 1440.0 -147.4 L: 1430 GRAHAM 345 1431 GRAHAM P 138 1 190.6 350.4 350.0 0.12362
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1583.7 1525.3 58.4 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 307.0 715.7 717.0 0.25806
C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
1573.3 1536.0 37.3 L: 6100 OKLAEHV7 345 1425 FISHRDSS 345 1 408.2 712.8 717.0 0.19356
C:Open 6230 ABMULCE7 345 1430 GRAHAM 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1536.5 1607.8 -71.4 L: 1859 EAGLE MT 345 1436 PARKER 345 1 959.5 1192.6 1195.0 0.15174
C:Open 1436 PARKER 345 1853 ROANOKE 345 1
1526.2 1788.1 -261.9 L: 1422 BOWMAN 345 1430 GRAHAM 345 1 419.2 983.2 1072.0 0.36951
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1876.9 1860.6 16.3 L: 1420 ENCOGEN 345 1430 GRAHAM 345 1 274.6 712.7 717.0 0.23337
C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
2275.9 2025.7 250.2 L: 1624 LEON 138 1640 LNGLVL M 138 1 18.4 84.9 84.0 0.02918
Base Case
2095.5 2097.1 -1.6 L: 1420 ENCOGEN 345 1430 GRAHAM 345 1 239.9 696.5 717.0 0.21793
NotConv C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
2347.0 2136.2 210.8 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 23.7 85.1 84.0 0.02614
Base Case
2247.4 2199.4 48.0 L: 1430 GRAHAM 345 1436 PARKER 345 1 302.3 1056.0 1052.0 0.33537
C:Open 1422 BOWMAN 345 1886 EV EAST 345 1
2172.8 2204.7 -31.9 L: 1030 MRGN CRK 345 1032 MRGN CRK 138 2 33.1 340.3 341.0 0.14137
C:Open 1030 MRGN CRK 345 1032 MRGN CRK 138 1
2247.4 2206.2 41.2 L: 1430 GRAHAM 345 1436 PARKER 345 2 302.3 1056.0 1052.0 0.33537
C:Open 1422 BOWMAN 345 1886 EV EAST 345 1
2187.3 2221.2 -33.9 L: 1030 MRGN CRK 345 1032 MRGN CRK 138 1 33.9 348.0 349.0 0.14356
C:Open 1030 MRGN CRK 345 1032 MRGN CRK 138 2
2301.5 2346.0 -44.5 L: 3405 T HOUSE 345 3409 LAKE CRK 345 2 391.8 878.8 956.0 0.21164
NotConv C:Open 3405 T HOUSE 345 3409 LAKE CRK 345 1
Open 3405 T HOUSE 345 3414 TEMP SS 345 1
2293.4 2349.1 -55.8 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 252.5 719.6 717.0 0.20368
Base Case
2318.5 2407.8 -89.3 L: 967 GIBCRK B 345 44500 OBRIEN 5 345 1 525.0 945.6 1088.0 0.18139
NotConv C:Open 40600 FRONTR 345 40900 KING 5 345 &1
Open 46500 TOMBAL 5 345 3391 JEWETT N 345 1

## systems
List of Available subsystems
Not shown sub index | Subsystem Name | # Buses | #Part Bus | Adjustment Type | Total Gen | Net Intrchng | MaxImport | MaxExport | Change
1 | ERCOT_GENS | 362 | 210 | ExportSpec | 40801.5 | 40648.5 | 0 | 6295.3
2 | NORTH2001 | 85 | 57 | ExportSpec | 11296.2 | 11263.9 | 0 | 1408.6
3 | SOUTH2001 | 226 | 132 | ExportSpec | 25643.3 | 25547.1 | 0 | 4645.6
4 | WEST2001 | 51 | 21 | ExportSpec | 3862 | 3837.6 | 144.6 | 241

## North to South
Study transfer. From NORTH2001 To SOUTH2001 . Transfer level - 10000.0 MW
AC DC Delta L: Limiting constraint PreShft PostShf AC_TDF
FCITC FCITC FCITC C: Contingency description Ncon MVA/MW MVA/MW Rating
2262.2 2223.7 38.4 L: 3405 T HOUSE 345 3409 LAKE CRK 345 2 391.8 956.9 956.0 0.24981
C:Open 3405 T HOUSE 345 3409 LAKE CRK 345 1
Open 3405 T HOUSE 345 3414 TEMP SS 345 1
2399.5 2268.6 130.9 L: 967 GIBCRK B 345 44500 OBRIEN 5 345 1 525.0 1087.6 1088.0 0.23446
C:Open 40600 FRONTR 345 40900 KING 5 345 &1
Open 46500 TOMBAL 5 345 3391 JEWETT N 345 1
2566.0 2548.7 17.3 L: 3409 LAKE CRK 345 3414 TEMP SS 345 1 355.3 956.3 956.0 0.23420
C:Open 3405 T HOUSE 345 3414 TEMP SS 345 1
2632.5 2616.9 15.6 L: 3409 LAKE CRK 345 3414 TEMP SS 345 1 348.0 956.2 956.0 0.23103
C:Open 3405 T HOUSE 345 3409 LAKE CRK 345 1
Open 3405 T HOUSE 345 3414 TEMP SS 345 1
2779.0 2697.7 81.3 L: 7332 ELGIN 13 138 3650 ELGIN SS 138 1 17.9 215.1 214.0 0.07095
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
2740.6 2726.3 14.3 L: 3405 T HOUSE 345 3414 TEMP SS 345 1 341.4 956.2 956.0 0.22435
C:Open 3409 LAKE CRK 345 3414 TEMP SS 345 1
3227.7 3038.7 189.0 L:46500 TOMBAL 5 345 3391 JEWETT N 345 1 274.5 955.3 956.0 0.21091
C:Open 45500 T_H_W_ 5 345 3390 JEWETT S 345 1
Open 967 GIBCRK B 345 44500 OBRIEN 5 345 1
2614.9 3060.5 -445.6 L: 3409 LAKE CRK 345 3410 LAKE CRK 138 1 331.5 536.7 537.0 0.07847
C:Open 3409 LAKE CRK 345 3414 TEMP SS 345 1
Open 3405 T HOUSE 345 3414 TEMP SS 345 1
3444.8 3206.4 238.4 L: 3390 JEWETT S 345 45500 T_H_W_ 5 345 1 236.4 954.9 956.0 0.20859
C:Open 40600 FRONTR 345 40900 KING 5 345 &1
Open 46500 TOMBAL 5 345 3391 JEWETT N 345 1
3458.3 3288.3 170.0 L: 967 GIBCRK B 345 44500 OBRIEN 5 345 1 362.0 1088.3 1088.0 0.20999
C:Open 45500 T_H_W_ 5 345 3390 JEWETT S 345 1
Open 46500 TOMBAL 5 345 3391 JEWETT N 345 1
3562.8 3517.5 45.3 L: 3429 SANDOW 345 7040 AUSTRO34 345 1 157.5 715.6 716.0 0.15664
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 2
3764.3 3557.4 206.9 L: 7334 MCNEIL13 138 9079 MCNEILN 138 1 58.1 302.8 304.0 0.06501
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
3856.4 3610.7 245.7 L:46500 TOMBAL 5 345 3391 JEWETT N 345 1 134.4 956.0 956.0 0.21305
C:Open 967 GIBCRK B 345 40600 FRONTR 345 1
Open 967 GIBCRK B 345 44500 OBRIEN 5 345 1
3455.8 3634.2 -178.4 L: 3414 TEMP SS 345 3415 TEMP SS 138 1 264.2 543.3 543.0 0.08078
C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
Open 3414 TEMP SS 345 3429 SANDOW 345 1
3859.5 3814.5 45.0 L: 3429 SANDOW 345 7040 AUSTRO34 345 2 157.5 788.2 789.0 0.16341
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
3912.7 3899.1 13.6 L: 3413 TEMPSSLT 345 3414 TEMP SS 345 1 147.2 1071.1 1072.0 0.23614
C:Open 3414 TEMP SS 345 3429 SANDOW 345 1
4317.8 4039.9 278.0 L: 3390 JEWETT S 345 45500 T_H_W_ 5 345 1 88.3 957.4 956.0 0.20129
C:Open 967 GIBCRK B 345 40600 FRONTR 345 1
Open 967 GIBCRK B 345 44500 OBRIEN 5 345 1
4142.8 4148.2 -5.4 L: 3414 TEMP SS 345 3429 SANDOW 345 1 90.6 957.0 956.0 0.20913
C:Open 3413 TEMPSSLT 345 3414 TEMP SS 345 1
4151.7 4151.7 0.0 L:42500 DOW345 5 345 42515 DOW_A_ 138 A4 88.2 501.1 500.0 0.09947
C:Open 42500 DOW345 5 345 42515 DOW_A_ 138 A3
4151.7 4151.7 0.0 L:42500 DOW345 5 345 42515 DOW_A_ 138 A3 88.2 501.2 500.0 0.09947
C:Open 42500 DOW345 5 345 42515 DOW_A_ 138 A4
4083.0 4245.4 -162.4 L: 3415 TEMP SS 138 3675 ROGERS 138 1 104.3 185.2 186.0 0.01980
C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
Open 3414 TEMP SS 345 3429 SANDOW 345 1
4602.2 4525.5 76.8 L:46100 N_BELT 5 345 40900 KING 5 345 97 524.0 1088.7 1091.0 0.12271
C:Open 45500 T_H_W_ 5 345 3390 JEWETT S 345 1
Open 967 GIBCRK B 345 44500 OBRIEN 5 345 1
4590.6 4590.6 0.0 L: 3414 TEMP SS 345 3429 SANDOW 345 1 200.1 960.6 956.0 0.16566
C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
4726.8 4806.1 -79.2 L: 3405 T HOUSE 345 3409 LAKE CRK 345 2 240.9 914.0 956.0 0.14239
NotConv C:Open 3405 T HOUSE 345 3409 LAKE CRK 345 1
4716.6 4831.6 -115.0 L: 967 GIBCRK B 345 44500 OBRIEN 5 345 1 281.3 850.1 906.0 0.12060
NotConv Base Case
4685.0 4832.2 -147.2 L:45972 KUYDAL 5 345 40600 FRONTR 345 75 546.6 1605.3 1662.0 0.22598
NotConv C:Open 45500 T_H_W_ 5 345 3390 JEWETT S 345 1
Open 967 GIBCRK B 345 44500 OBRIEN 5 345 1
4730.0 4890.0 -160.0 L:46500 TOMBAL 5 345 3391 JEWETT N 345 1 187.5 813.1 906.0 0.13227
NotConv Base Case
4690.0 4948.8 -258.8 L:45972 KUYDAL 5 345 40900 KING 5 345 75 522.1 1579.4 1662.0 0.22544
NotConv C:Open 45500 T_H_W_ 5 345 3390 JEWETT S 345 1
Open 967 GIBCRK B 345 44500 OBRIEN 5 345 1
4718.6 5046.5 -327.9 L: 3405 T HOUSE 345 3409 LAKE CRK 345 1 231.3 879.1 956.0 0.13729
NotConv C:Open 3405 T HOUSE 345 3409 LAKE CRK 345 2
4722.5 5063.3 -340.7 L: 3409 LAKE CRK 345 3414 TEMP SS 345 1 220.8 910.1 956.0 0.14598
NotConv Base Case
4723.5 5070.5 -347.0 L: 3413 TEMPSSLT 345 3429 SANDOW 345 1 200.2 989.2 1072.0 0.16704
NotConv C:Open 3414 TEMP SS 345 3429 SANDOW 345 1
4730.0 5370.9 -641.0 L: 3380 BIGBRN 345 3390 JEWETT S 345 1 233.8 773.1 956.0 0.11403
NotConv C:Open 3380 BIGBRN 345 3391 JEWETT N 345 1
4724.6 5379.6 -655.0 L: 9074 LYTTON 345 7042 ZORN 34 345 1 389.2 1017.9 1100.0 0.13307
NotConv C:Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
4693.8 5456.3 -762.5 L:45972 KUYDAL 5 345 40600 FRONTR 345 75 471.0 1444.9 1662.0 0.20749
NotConv C:Open 45500 T_H_W_ 5 345 3390 JEWETT S 345 1
Open 46500 TOMBAL 5 345 3391 JEWETT N 345 1
4702.3 5483.7 -781.5 L: 3429 SANDOW 345 3430 SANDOW 138 1 151.9 397.4 448.0 0.05221
NotConv C:Open 7040 AUSTRO34 345 3429 SANDOW 345 1
Open 7040 AUSTRO34 345 3429 SANDOW 345 2
4730.1 5516.2 -786.1 L: 9040 AUSTROP 345 7040 AUSTRO34 345 1 274.8 920.3 1125.0 0.13647
NotConv C:Open 7040 AUSTRO34 345 7048 GARFIE34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
4734.0 5542.2 -808.1 L: 3390 JEWETT S 345 45500 T_H_W_ 5 345 1 111.6 724.2 906.0 0.12939
NotConv Base Case
4689.6 5579.2 -889.6 L:45972 KUYDAL 5 345 40900 KING 5 345 75 447.0 1417.9 1662.0 0.20704
NotConv C:Open 45500 T_H_W_ 5 345 3390 JEWETT S 345 1
Open 46500 TOMBAL 5 345 3391 JEWETT N 345 1
4735.1 5599.0 -863.9 L: 3429 SANDOW 345 7040 AUSTRO34 345 1 97.4 584.8 716.0 0.10294
NotConv Base Case
4730.0 5599.3 -869.4 L: 3405 T HOUSE 345 3414 TEMP SS 345 1 207.4 837.7 956.0 0.13327
NotConv Base Case
4732.2 5761.8 -1029.5 L: 3380 BIGBRN 345 3391 JEWETT N 345 1 228.5 789.4 1072.0 0.11852
NotConv C:Open 3380 BIGBRN 345 3390 JEWETT S 345 1
4696.7 5768.4 -1071.7 L: 3429 SANDOW 345 3430 SANDOW 138 1 79.8 362.1 448.0 0.06012
NotConv C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
Open 3414 TEMP SS 345 3429 SANDOW 345 1
4701.3 5845.1 -1143.8 L:46100 N_BELT 5 345 45500 T_H_W_ 5 345 97 106.1 727.0 1091.0 0.13207
NotConv C:Open 40600 FRONTR 345 40900 KING 5 345 &1
Open 46500 TOMBAL 5 345 3391 JEWETT N 345 1
4717.7 6047.8 -1330.1 L: 3380 BIGBRN 345 3390 JEWETT S 345 1 355.6 648.6 956.0 0.06212
NotConv C:Open 1906 VENUS S 345 3405 T HOUSE 345 1
Open 1907 VENUS N 345 3405 T HOUSE 345 1
4735.0 6108.2 -1373.2 L: 3429 SANDOW 345 7040 AUSTRO34 345 2 97.4 584.9 789.0 0.10296
NotConv Base Case
4728.6 6323.3 -1594.8 L: 3413 TEMPSSLT 345 3414 TEMP SS 345 1 200.8 853.1 1072.0 0.13795
NotConv Base Case
4699.1 6422.2 -1723.1 L: 967 GIBCRK B 345 40600 FRONTR 345 1 260.9 757.9 1195.0 0.10576
NotConv C:Open 45500 T_H_W_ 5 345 3390 JEWETT S 345 1
Open 967 GIBCRK B 345 44500 OBRIEN 5 345 1
4728.1 6704.1 -1976.0 L:45500 T_H_W_ 5 345 45600 ADICKS 5 345 71 283.0 840.4 1088.0 0.11790
NotConv C:Open 44500 OBRIEN 5 345 45500 T_H_W_ 5 345 98
Open 967 GIBCRK B 345 44500 OBRIEN 5 345 1
4729.9 6873.8 -2143.9 L: 3380 BIGBRN 345 3391 JEWETT N 345 1 511.0 526.8 1072.0 0.00334
NotConv C:Open 46020 LIMEST 5 345 2428 WATMILLE 345 1
Open 46020 LIMEST 5 345 2435 WATMLLDB 345 2
4696.6 7133.0 -2436.4 L: 967 GIBCRK B 345 40600 FRONTR 345 1 336.9 570.9 1195.0 0.04982
NotConv C:Open 45500 T_H_W_ 5 345 3390 JEWETT S 345 1
Open 46500 TOMBAL 5 345 3391 JEWETT N 345 1
4731.1 7314.0 -2582.9 L: 3414 TEMP SS 345 3429 SANDOW 345 1 124.2 581.9 956.0 0.09674
NotConv Base Case
4726.2 7383.7 -2657.5 L: 2428 WATMILLE 345 2432 TRICORN 345 1 172.5 721.0 1072.0 0.11604
NotConv C:Open 3380 BIGBRN 345 3390 JEWETT S 345 1
Open 3380 BIGBRN 345 3391 JEWETT N 345 1
4731.6 7493.0 -2761.3 L: 9040 AUSTROP 345 7040 AUSTRO34 345 1 532.9 548.4 1125.0 0.00327
NotConv C:Open 9074 LYTTON 345 7048 GARFIE34 345 1
Open 7040 AUSTRO34 345 7045 ZORN 34 345 1
4735.0 7686.9 -2951.9 L: 7040 AUSTRO34 345 7048 GARFIE34 345 1 146.1 615.9 1100.0 0.09922
NotConv C:Open 9040 AUSTROP 345 7040 AUSTRO34 345 1
4731.6 7709.7 -2978.0 L:42500 DOW345 5 345 42515 DOW_A_ 138 A3 47.7 290.8 500.0 0.05139
NotConv Base Case
4733.7 7713.0 -2979.3 L: 3380 BIGBRN 345 3390 JEWETT S 345 1 162.1 502.9 956.0 0.07198
NotConv Base Case
4731.6 7716.5 -2984.8 L:42500 DOW345 5 345 42515 DOW_A_ 138 A4 47.6 290.6 500.0 0.05134
NotConv Base Case
4733.6 7830.4 -3096.8 L: 3380 BIGBRN 345 3391 JEWETT N 345 1 155.9 547.2 1072.0 0.08266
NotConv Base Case
4731.1 7878.0 -3146.9 L: 1906 VENUS S 345 3405 T HOUSE 345 1 499.0 402.3 956.0 -0.02045
NotConv C:Open 1907 VENUS N 345 3405 T HOUSE 345 1
4631.9 8091.0 -3459.1 L: 3414 TEMP SS 345 3415 TEMP SS 138 1 180.7 296.5 543.0 0.02501
NotConv C:Open 3409 LAKE CRK 345 3414 TEMP SS 345 1
Open 3405 T HOUSE 345 3414 TEMP SS 345 1

## North to West
Study transfer. From NORTH2001 To WEST2001 . Transfer level - 2500.0 MW
AC DC Delta L: Limiting constraint PreShft PostShf AC_TDF
FCITC FCITC FCITC C: Contingency description Ncon MVA/MW MVA/MW Rating
824.9 836.1 -11.2 L: 1869 BENB A T 345 1873 BENBRK 345 1 858.4 1050.3 1052.0 0.23269
C:Open 1436 PARKER 345 1900 COM PEAK 345 1
1071.4 971.4 100.0 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 32.6 83.6 84.0 0.04761
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1123.9 1018.9 105.0 L: 1624 LEON 138 1640 LNGLVL M 138 1 36.1 83.3 84.0 0.04202
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1306.7 1081.2 225.5 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 23.7 84.4 84.0 0.04643
Base Case
1408.4 1180.7 227.7 L: 1624 LEON 138 1640 LNGLVL M 138 1 18.4 85.0 84.0 0.04728
Base Case
1738.6 1864.9 -126.3 L: 1571 ORAN 138 1596 GRAHAMSS 138 1 109.9 188.7 186.0 0.04535
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
2079.9 2020.2 59.7 L: 1574 PALOPNTO 138 1578 PALOPT M 138 1 208.2 325.6 326.0 0.05647
Base Case
1917.3 2044.1 -126.8 L: 1869 BENB A T 345 1873 BENBRK 345 1 839.7 1050.7 1052.0 0.11002
C:Open 1870 BENB B T 345 1873 BENBRK 345 1
2096.5 2056.9 39.6 L: 1574 PALOPNTO 138 1576 MINWLJCT 138 1 207.2 325.6 326.0 0.05646
Base Case
2142.0 2278.0 -135.9 L: 1869 BENB A T 345 1436 PARKER 345 1 444.7 1056.9 1052.0 0.28580
C:Open 1436 PARKER 345 1900 COM PEAK 345 1
2352.8 2338.7 14.2 L: 1575 MINWL W 138 1576 MINWLJCT 138 1 102.1 252.6 249.0 0.06396
Base Case
2189.8 2467.1 -277.3 L: 1886 EV EAST 345 1422 BOWMAN 345 1 342.3 797.2 789.0 0.20772
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
2295.4 2480.4 -185.1 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 230.0 718.5 717.0 0.21283
C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1

## South to North
Study transfer. From SOUTH2001 To NORTH2001 . Transfer level - 2500.0 MW
AC DC Delta L: Limiting constraint PreShft PostShf AC_TDF
FCITC FCITC FCITC C: Contingency description Ncon MVA/MW MVA/MW Rating
446.5 572.6 -126.2 L: 1906 VENUS S 345 2420 C HILL 345 1 1018.0 1073.4 1072.0 0.12419
C:Open 1882 EV WEST 345 1906 VENUS S 345 1
Open 1886 EV EAST 345 1907 VENUS N 345 1
850.2 965.2 -115.0 L: 1906 VENUS S 345 2420 C HILL 345 1 974.9 1075.2 1072.0 0.11793
C:Open 1882 EV WEST 345 1906 VENUS S 345 1
1204.6 1242.0 -37.5 L: 3415 TEMP SS 138 3675 ROGERS 138 1 104.3 188.2 186.0 0.06964
C:Open 3413 TEMPSSLT 345 3429 SANDOW 345 1
Open 3414 TEMP SS 345 3429 SANDOW 345 1
2247.6 2309.9 -62.3 L: 3429 SANDOW 345 7040 AUSTRO34 345 1 157.5 716.6 716.0 0.24876
C:Open 7040 AUSTRO34 345 3429 SANDOW 345 2
2082.2 2317.8 -235.6 L: 3380 BIGBRN 345 3390 JEWETT S 345 1 470.2 955.6 956.0 0.23316
C:Open 46020 LIMEST 5 345 2428 WATMILLE 345 1
Open 46020 LIMEST 5 345 2435 WATMLLDB 345 2
2374.3 2439.6 -65.3 L: 1906 VENUS S 345 3405 T HOUSE 345 1 499.0 958.5 956.0 0.19355
C:Open 1907 VENUS N 345 3405 T HOUSE 345 1
2179.1 2441.2 -262.1 L: 3380 BIGBRN 345 3391 JEWETT N 345 1 511.0 1069.1 1072.0 0.25609
C:Open 46020 LIMEST 5 345 2428 WATMILLE 345 1
Open 46020 LIMEST 5 345 2435 WATMLLDB 345 2

## South to West
Study transfer. From SOUTH2001 To WEST2001 . Transfer level - 2500.0 MW
AC DC Delta L: Limiting constraint PreShft PostShf AC_TDF
FCITC FCITC FCITC C: Contingency description Ncon MVA/MW MVA/MW Rating
337.2 432.5 -95.3 L: 1906 VENUS S 345 2420 C HILL 345 1 1018.0 1070.7 1072.0 0.15637
C:Open 1882 EV WEST 345 1906 VENUS S 345 1
Open 1886 EV EAST 345 1907 VENUS N 345 1
715.9 725.6 -9.7 L: 1869 BENB A T 345 1873 BENBRK 345 1 858.4 1049.6 1052.0 0.26721
C:Open 1436 PARKER 345 1900 COM PEAK 345 1
665.4 755.4 -90.0 L: 1906 VENUS S 345 2420 C HILL 345 1 974.9 1071.2 1072.0 0.14461
C:Open 1882 EV WEST 345 1906 VENUS S 345 1
1144.1 1039.9 104.1 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 32.6 83.7 84.0 0.04461
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1199.3 1090.8 108.5 L: 1624 LEON 138 1640 LNGLVL M 138 1 36.1 83.4 84.0 0.03946
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1454.6 1201.6 253.0 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 23.7 85.1 84.0 0.04220
Base Case
1558.5 1312.1 246.4 L: 1624 LEON 138 1640 LNGLVL M 138 1 18.4 85.0 84.0 0.04271
Base Case
1684.6 1796.1 -111.4 L: 1869 BENB A T 345 1873 BENBRK 345 1 839.7 1049.2 1052.0 0.12433
C:Open 1870 BENB B T 345 1873 BENBRK 345 1
1985.6 2112.0 -126.4 L: 1869 BENB A T 345 1436 PARKER 345 1 444.7 1054.8 1052.0 0.30726
C:Open 1436 PARKER 345 1900 COM PEAK 345 1
1997.5 2214.2 -216.8 L: 1571 ORAN 138 1596 GRAHAMSS 138 1 109.9 190.0 186.0 0.04010
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
2233.9 2394.5 -160.6 L: 1906 VENUS S 345 3405 T HOUSE 345 1 499.0 952.9 956.0 0.20319
C:Open 1907 VENUS N 345 3405 T HOUSE 345 1
2223.5 2446.9 -223.4 L: 2427 WATMILLW 345 2420 C HILL 345 1 491.9 960.0 956.0 0.21052
C:Open 1906 VENUS S 345 3380 BIGBRN 345 1
Open 1907 VENUS N 345 3380 BIGBRN 345 1
1667.4 2488.1 -820.7 L: 1886 EV EAST 345 1422 BOWMAN 345 1 342.3 484.1 789.0 0.08506
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2

## West to North
Study transfer. From WEST2001 To NORTH2001 . Transfer level - 2500.0 MW
AC DC Delta L: Limiting constraint PreShft PostShf AC_TDF
FCITC FCITC FCITC C: Contingency description Ncon MVA/MW MVA/MW Rating
487.5 414.6 72.9 L: 1624 LEON 138 1640 LNGLVL M 138 1 36.1 83.7 84.0 0.09784
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
529.9 462.0 67.8 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 32.6 84.1 84.0 0.09719
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
480.2 481.6 -1.5 L: 1571 ORAN 138 1596 GRAHAMSS 138 1 109.9 184.7 186.0 0.15585
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
586.1 578.5 7.7 L: 1601 GRAHAM E 138 1431 GRAHAM P 138 1 160.4 250.3 251.0 0.15345
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
709.5 705.5 4.1 L: 1596 GRAHAMSS 138 1601 GRAHAM E 138 1 141.3 250.4 251.0 0.15372
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
751.7 745.8 5.9 L: 1464 S WFALLS 138 1467 NORTHSTR 138 1 125.1 182.3 186.0 0.07606
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
783.1 779.3 3.7 L: 1467 NORTHSTR 138 1468 AROWHEAD 138 1 122.6 182.1 186.0 0.07609
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
802.2 800.2 2.0 L: 1468 AROWHEAD 138 1470 NEWPRT M 138 1 121.0 182.0 186.0 0.07598
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
822.4 839.4 -17.0 L: 1469 SUNSET 138 1470 NEWPRT M 138 1 119.4 181.9 186.0 0.07603
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
974.5 914.2 60.3 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 374.5 715.1 717.0 0.34958
C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1032.3 970.6 61.7 L: 1886 EV EAST 345 1422 BOWMAN 345 1 342.3 791.0 789.0 0.43467
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1107.5 1180.6 -73.1 L: 1019 MOSS 138 1292 ECTR HRP 138 1 133.8 189.5 191.0 0.05030
Base Case
1123.4 1248.3 -124.9 L: 1430 GRAHAM 345 1431 GRAHAM P 138 1 190.6 350.8 350.0 0.14258
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1221.0 1319.8 -98.8 L: 1859 EAGLE MT 345 1436 PARKER 345 1 959.5 1193.0 1195.0 0.19128
C:Open 1436 PARKER 345 1853 ROANOKE 345 1
1421.9 1327.8 94.2 L: 1430 GRAHAM 345 1436 PARKER 345 1 425.9 1052.7 1052.0 0.44079
C:Open 1430 GRAHAM 345 1436 PARKER 345 2
1382.3 1329.5 52.8 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 230.0 721.2 717.0 0.35531
C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1421.9 1329.6 92.3 L: 1430 GRAHAM 345 1436 PARKER 345 2 425.9 1052.7 1052.0 0.44079
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
1409.4 1365.0 44.3 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 339.6 716.5 717.0 0.26742
C:Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1381.6 1376.1 5.5 L: 1010 PERMIANB 138 1292 ECTR HRP 138 1 138.6 208.1 210.0 0.05028
Base Case
1464.6 1429.9 34.7 L: 6100 OKLAEHV7 345 1425 FISHRDSS 345 1 408.2 713.4 717.0 0.20838
C:Open 6230 ABMULCE7 345 1430 GRAHAM 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1582.6 1525.5 57.1 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 307.0 718.6 717.0 0.26008
C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
1543.7 1750.6 -206.9 L: 1422 BOWMAN 345 1430 GRAHAM 345 1 419.2 999.2 1072.0 0.37569
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1871.6 1812.4 59.2 L: 1420 ENCOGEN 345 1430 GRAHAM 345 1 274.6 718.2 717.0 0.23701
C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
2074.6 1822.9 251.7 L: 1624 LEON 138 1640 LNGLVL M 138 1 18.4 84.8 84.0 0.03199
Base Case
2134.6 1922.3 212.3 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 23.7 84.5 84.0 0.02844
Base Case
2110.9 2008.3 102.6 L: 1420 ENCOGEN 345 1430 GRAHAM 345 1 239.9 714.9 717.0 0.22505
C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
2145.2 2094.7 50.4 L: 1571 ORAN 138 1596 GRAHAMSS 138 1 36.1 186.4 186.0 0.07005
Base Case
2204.4 2150.9 53.4 L: 1430 GRAHAM 345 1436 PARKER 345 1 302.3 1047.5 1052.0 0.33806
C:Open 1422 BOWMAN 345 1886 EV EAST 345 1
2204.4 2157.6 46.8 L: 1430 GRAHAM 345 1436 PARKER 345 2 302.3 1047.5 1052.0 0.33806
C:Open 1422 BOWMAN 345 1886 EV EAST 345 1
2150.0 2181.5 -31.6 L: 1030 MRGN CRK 345 1032 MRGN CRK 138 2 33.1 340.5 341.0 0.14294
C:Open 1030 MRGN CRK 345 1032 MRGN CRK 138 1
2164.3 2197.8 -33.5 L: 1030 MRGN CRK 345 1032 MRGN CRK 138 1 33.9 348.1 349.0 0.14515
C:Open 1030 MRGN CRK 345 1032 MRGN CRK 138 2
2370.5 2335.1 35.4 L: 1601 GRAHAM E 138 1431 GRAHAM P 138 1 85.3 255.2 251.0 0.07168
Base Case
2330.5 2387.2 -56.7 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 252.5 720.3 717.0 0.20075
Base Case
2409.4 2454.1 -44.7 L: 1855 ALLIANCE 345 1859 EAGLE MT 345 1 830.1 1153.0 1195.0 0.13401
NotConv C:Open 1436 PARKER 345 1853 ROANOKE 345 1

## West to South
Study transfer. From WEST2001 To SOUTH2001 . Transfer level - 2500.0 MW
AC DC Delta L: Limiting constraint PreShft PostShf AC_TDF
FCITC FCITC FCITC C: Contingency description Ncon MVA/MW MVA/MW Rating
524.9 443.8 81.1 L: 1624 LEON 138 1640 LNGLVL M 138 1 36.1 83.8 84.0 0.09093
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
570.5 494.6 75.9 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 32.6 84.2 84.0 0.09035
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
570.1 571.8 -1.7 L: 1571 ORAN 138 1596 GRAHAMSS 138 1 109.9 184.4 186.0 0.13071
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
691.4 682.3 9.1 L: 1601 GRAHAM E 138 1431 GRAHAM P 138 1 160.4 250.3 251.0 0.13011
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
836.9 832.1 4.8 L: 1596 GRAHAMSS 138 1601 GRAHAM E 138 1 141.3 249.8 251.0 0.12964
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
994.7 938.5 56.2 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 374.5 715.1 717.0 0.34242
C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1043.9 978.9 65.0 L: 1886 EV EAST 345 1422 BOWMAN 345 1 342.3 790.2 789.0 0.42901
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1125.3 1199.6 -74.3 L: 1019 MOSS 138 1292 ECTR HRP 138 1 133.8 189.5 191.0 0.04953
Base Case
1410.8 1364.9 45.9 L: 1030 MRGN CRK 345 1430 GRAHAM 345 1 230.0 720.5 717.0 0.34769
C:Open 1030 MRGN CRK 345 1420 ENCOGEN 345 1
Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
1409.7 1366.2 43.5 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 339.6 717.4 717.0 0.26797
C:Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1479.3 1375.4 104.0 L: 1430 GRAHAM 345 1436 PARKER 345 1 425.9 1053.2 1052.0 0.42408
C:Open 1430 GRAHAM 345 1436 PARKER 345 2
1479.3 1377.3 102.1 L: 1430 GRAHAM 345 1436 PARKER 345 2 425.9 1053.2 1052.0 0.42408
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
1403.8 1398.2 5.6 L: 1010 PERMIANB 138 1292 ECTR HRP 138 1 138.6 208.3 210.0 0.04968
Base Case
1292.6 1440.0 -147.4 L: 1430 GRAHAM 345 1431 GRAHAM P 138 1 190.6 350.4 350.0 0.12362
C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1583.7 1525.3 58.4 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 307.0 715.7 717.0 0.25806
C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
1573.3 1536.0 37.3 L: 6100 OKLAEHV7 345 1425 FISHRDSS 345 1 408.2 712.8 717.0 0.19356
C:Open 6230 ABMULCE7 345 1430 GRAHAM 345 1
Open 1420 ENCOGEN 345 1430 GRAHAM 345 1
1536.5 1607.8 -71.4 L: 1859 EAGLE MT 345 1436 PARKER 345 1 959.5 1192.6 1195.0 0.15174
C:Open 1436 PARKER 345 1853 ROANOKE 345 1
1526.2 1788.1 -261.9 L: 1422 BOWMAN 345 1430 GRAHAM 345 1 419.2 983.2 1072.0 0.36951
NotConv C:Open 1430 GRAHAM 345 1436 PARKER 345 1
Open 1430 GRAHAM 345 1436 PARKER 345 2
1876.9 1860.6 16.3 L: 1420 ENCOGEN 345 1430 GRAHAM 345 1 274.6 712.7 717.0 0.23337
C:Open 6235 ABMULCW7 345 1030 MRGN CRK 345 1
2275.9 2025.7 250.2 L: 1624 LEON 138 1640 LNGLVL M 138 1 18.4 84.9 84.0 0.02918
Base Case
2095.5 2097.1 -1.6 L: 1420 ENCOGEN 345 1430 GRAHAM 345 1 239.9 696.5 717.0 0.21793
NotConv C:Open 1030 MRGN CRK 345 1430 GRAHAM 345 1
2347.0 2136.2 210.8 L: 1640 LNGLVL M 138 1641 STPHVIL 138 1 23.7 85.1 84.0 0.02614
Base Case
2247.4 2199.4 48.0 L: 1430 GRAHAM 345 1436 PARKER 345 1 302.3 1056.0 1052.0 0.33537
C:Open 1422 BOWMAN 345 1886 EV EAST 345 1
2172.8 2204.7 -31.9 L: 1030 MRGN CRK 345 1032 MRGN CRK 138 2 33.1 340.3 341.0 0.14137
C:Open 1030 MRGN CRK 345 1032 MRGN CRK 138 1
2247.4 2206.2 41.2 L: 1430 GRAHAM 345 1436 PARKER 345 2 302.3 1056.0 1052.0 0.33537
C:Open 1422 BOWMAN 345 1886 EV EAST 345 1
2187.3 2221.2 -33.9 L: 1030 MRGN CRK 345 1032 MRGN CRK 138 1 33.9 348.0 349.0 0.14356
C:Open 1030 MRGN CRK 345 1032 MRGN CRK 138 2
2301.5 2346.0 -44.5 L: 3405 T HOUSE 345 3409 LAKE CRK 345 2 391.8 878.8 956.0 0.21164
NotConv C:Open 3405 T HOUSE 345 3409 LAKE CRK 345 1
Open 3405 T HOUSE 345 3414 TEMP SS 345 1
2293.4 2349.1 -55.8 L: 6235 ABMULCW7 345 1030 MRGN CRK 345 1 252.5 719.6 717.0 0.20368
Base Case
2318.5 2407.8 -89.3 L: 967 GIBCRK B 345 44500 OBRIEN 5 345 1 525.0 945.6 1088.0 0.18139
NotConv C:Open 40600 FRONTR 345 40900 KING 5 345 &1
Open 46500 TOMBAL 5 345 3391 JEWETT N 345 1