## Asset Schedule
CPU UNITS
| Unit 9 | Unit 8/6 | Unit 7
Unit Type | STAG Combined Cycle | Simple Cycle/CC | Conventional 400lb Steam
Min Capacity | 12 | 5/8 | 4
Max Capacity | 22 | 12.7/6.8 | 7.5
Min Heat Rate | 12500 | 21,000/13,100
Max Heat Rate | 11500 | 17,300/11,900 | 19500
Preferred Min Run Time | 16 | 16 | 120
Acceptable Min Run Time | 12 | 12 | 60
Min Off Time
Cold Start Time | 2 | 3 | 12
Warm Start Time | 1 | 2 | 8
Hot Start Time | 0.5 | 1 | 2
Ramp MW/min | 2 | 1.5 | 0.5
Weekly Starts | 7 | 5 | 1
Monthly Starts | 28 | 20 | 4
Yearly Starts | 96 | 48 | 20
Start Costs
VOM | 2 | 2 | 2
Dual Fuel? | Yes | Yes | No
2nd Fuel | LS #2 | LS #2 | --
Dual Fuel Heat Rate |  |  | --
Dual Fuel VOM | 2 | 2 | --
Yazoo City UNITS
| Unit # CT1 | Unit # ST2 | Unit # ST3 | Unit # CT1/ST3 | TOTAL
Unit Type | SIMPLE CYCLE | 400 LB STEAM | 600 LB STEAM | COMBINED CYCLE | SYSTEM
Min Capacity | 3 | 2 | 6 | 15
Max Capacity | 14.5 | 5 | 12 | 23 | 32
Min Heat Rate | ? | ? | ? | 12000
Max Heat Rate | 17000 | 16000 | 15000 | 10700 | 12000
Preferred Min Run Time |  | 16 | 120 | 16
Acceptable Min Run Time |  | 12 | 60 | 12
Min Off Time
Cold Start Time | 0.17 | 1 | 6 | .17/2.00
Warm Start Time | 0.17 | 0.5 | 1 | .17/.50
Hot Start Time | 0.17 | 0.1 | 0.5 | .17/.10
Ramp MW/min | 2 | 1 | 1 | 2.00/1.00
Weekly Starts | 14 | 7 | 1 | 7
Monthly Starts | 31 | 31 | 4 | 31
Yearly Starts
Start Costs
VOM | 2 | 2 | 2 | 2
Dual Fuel? | YES | NO | NO | YES
2nd Fuel | LS #2 |  |  | LS #2
Dual Fuel Heat Rate
Dual Fuel VOM | 2 |  |  | 2
HRSG is rated at 95,000 lbs./hr and conventional boiler is rated at 120,000 lbs./hr. The two steam turbines are supplied from a common header
off these two boilers. ST2 can not be operated by its self.