## Sheet1
Enron Wind 1.5 Downtime Allocation Document
| Availability |  |  | Survey Time
| System Ok Time | SOT |  | ST = SOT+DT+LOT+WOT+EST+MT+RT
| Down Time | DT
| Weather Out Time | WOT |  | Machine Availability:
| External Stop Time | EST |  | MA [%] = SOT/ST*100%
| Repair Time | RT
| Survey Time, measured | ST |  | Operational Availability
| Survey Time, total possible | TO |  | OA [%] = OT/ST*100%
| Maintenance Time | MT
| Prorated MT for period | Mtprorated |  | Line Availability
LA [%] = (ST - LOT)/ST * 100%
| The terms Mt and Mtprorated |  |  | Enron Availability: displayed on SCADA screen. Not corrected.
| implement the OOH contractual |  |  | EA [ %] = (SOT+LOT+WOT+EST)/(SOT+DT+LOT+WOT+EST+MT+RT)*100%
term.
| Mtprorated is computed by |  |  | Existing Contractual Availability. Corrected for Force Majeure
| prorating the MT annual credit |  |  | CA[%] = (TO - DT - RT - LOT - MT)/(TO - LOT - Mtprorated) * 100%
to the survey period.
Preferred Contractual Availability: Easy to compute, understand, & explain
CA[%] = (TO - DT - RT - MT)/(TO - Mtprorated) * 100%
Operator will still report force majeure, line out, and extreme weather events.
Operational Policies
1) The rotary service switch must be set to "repair" before any repair.
2) The rotary service switch must be set to "maintenance" before all maintenance tasks.
3) The down time clock should be incremented if the turbine is braked due to a malfunction. The WTG is not safe to operate.
4) The System OK time clock should be incremented in one of three scenarios. First, if the turbine has a minor malfunction
that needs correcting but is not serious enough to require turbine braking. Second, the turbine is automatically changing
state as per approved design. The turbine may not produce power during this scecario but the duration is short.
Third, a technician pauses or stops a turbine, that is safe to operate, for a short time duration for inspection or testing.
Beyond this short duration the technician will either manually induce a fault to increment Down time,
will set the rotary switch to "repair", or will set the rotary switch to "maintenance".
List of Messages: For status messages indicated with "A" in the Auto Reset Column, a restart automatically follows resolution of the cause of error. When a number is given, an automatic restart follows resolution of the cause of error; however, if this number of disturbances is exceeded, the turbine remains braked.
Status No. | Description | Braking Procedure | No. of Auto Resets | Error Identification | Status Times EW 1.5 | Responsibility
1 | program start PLC | 2 | A | PLC was freshly started | system OK time | Noone
2 | no error | - |  | turbine free of error | system OK time | Noone
3 | manual stop | 2 |  | manual stop from switching box key or turbine PC (general control function or DI1.13=0 (Bvb-1) or DI11.11=0 (BvB=1)) | system OK time | Noone
4 | remote stop | 2 |  | manual stop from remote PC (general control function) | system OK time | Noone
5 | remote start | - |  | turbine start from remote PC (general control function) | system OK time | Noone
6 | system OK | - |  | no error and no manual stop | system OK time | Noone
7 | storm shutdown | 2 | A | wind P6.5 time averaged P6.6 exceeded or wind P6.7 exceeded for period P6.8 or blade angle below P12.10 for a period P6.8 | weather out time | Noone
8 | overvoltage | 6a | A | one of the mains voltages exceeded P20.1 for a period P20.7 | line out time | Utility
9 | undervoltage | 6a | A | one of the mains voltages below P20.1 for a period P20.7 | line out time | Utility
10
11
12
13 | asymmetric generator current | 4 | A | 2 current phased deviate from one another by P20.5 for more than 500 ms | down time | Operator
14 | generator overspeed | 6a |  | generator speed below P1.1 for a period of P1.2 | down time | Operator
15 | rotor overspeed | 6a |  | rotor speed below P1.3 for a period of P1.4 | down time | Operator
16 | rotor speed monitor | 6b |  | overspeed on (rotor) monitor, Ind. Proximity switch between gearbox and generator (DI12.11=1) | down time | Operator
17 | centrifugal switch | 6b |  | overspeed on centrifugal switch (DI11.18=1) | down time | Operator
18
19 | maximum motor power | 3 |  | power below P4.10 for 1 sec | down time | Operator
20 | cable twisting right | 2 | A | P11.5 rotations spinning or P11.6 rotations in all conditions exceeded | system OK time | Noone
21 | cable twisting left | 2 | A | P11.5 rotations spinning or P11.6 rotations in al conditions exceeded | system OK time | Noone
22 | yaw drive end position | 2 |  | nacelle rotations P11.7 exceeded | down time | Operator
23 | peak value for excessive output | 3 | 5 | power P4.2 exceeded for period P4.3 | down time | Operator
24 | primary braking time too long | 6a |  | blade drive time P8.7 for type 2 braking to feathered pitch position or speed not under 80 rpm in time P8.7 | down time | Operator
25 | no speed reduction with primary braking (pitch) | 6a |  | no reduction in rot. Speed with braking types 3-5 after the first 5 sec, after 0.5 sec thereafter and not below 300 rpm | down time | Operator
26
27 | secondary braking time too long | 6a |  | not below speed of 80 rpm after a period P8.6 after application of brake | down time | Operator
28 | no speed reduction with secondary braking | 6a |  | no reduction in rot. speed with braking types 6-7 after the first 5 sec, after 0.5 sec thereafter and not below 300 rpm | down time | Operator
29
30
31 | timeout yaw counter | 2 |  | for azimuth adjustment there is no pos. gear drive - signal flank (DI11.1) within a period P11.9 | down time | Operator
32
33
34 | brake not released secondary brake | 3 |  | after period P9.6 following opening of the brake, the brake is not released (DI12.3=0) for a period of P9.7 | down time | Operator
35 | emergency stop | 6b |  | emergency off button activated in control box (DI1.4=1) | down time | Operator
36 | speed with braked turbine | 6b |  | below gen. speed 14 rpm / rotor speed 1.5 rpm 30 sec after application of brake | down time | Operator
37
38 | secondary brake test | 7 | A | brake test after 1400 h below power 500 kW without pitch brake | down time | Operator
39
40
41 | vibration sensor defect | 3 | 1 | monitoring accelerometer (PCH): error signal DI11.32=0 or accel. with braking < test level (P7.11) or test brake < 2,5 m/s2 | down time | Operator
42 | wrong yaw drive direction | 2 | (A) | identification of wrong direction : apply brakes immed. and reset timer / counter. 1.: no fault message, 2.: shut down turbine with EM 42, 3.: stationary at v = v3 block restart, block azimuth for v > v3 - 5 m/s, 4.: stationary at v < v3 - 5 m/s EM 42 must be manually acknowledged, azimuth is blocked. If the rotational direction is correct for the trials 1-4, start the turbine and distrubance message 42 is withdrawn. | down time | Operator
43
44
45 | hydraulic pump time too long | 2 | 5 | hydraulic pump period below P9.5 (no EDS-built up in the period) | down time | Operator
46 | hydraulic pump time too long | 2 |  | hydraulic pump interval period below P9.4 | down time | Operator
47 | hydraulic service switch top cabinet | 2 |  | hydraulic service switch activated (DI11.14=0) | maintenance time. Rotory service switch will take precedence. | Should never select availability clock.
48
49
50
51 | gearbox oil level too low | 2 | 5 | gearbox oil level too low and gearbox temp. exceeded by 5oC for period P10.2 (DI12.5=0) | down time | Operator
52 | gearbox oil pressure too low | 2 | 5 | gearbox oil pressure too low for a period P10.1 delayed for a period P10.8 after switching on pump (DI12.9=0) | down time | Operator
53 | wind vane defect | 2 | 5 | azimuth adjustment angle 200o exceeded and no flank change in center signal (DI11.8) | down time | Operator
54 | anemometer defect | 2 | 5 | power P6.9 exceeded for period P6.10 and wind less than 4 m/s for period P6.10 | down time | Operator
55 | rotor pulse sensor defect | 2 | 5 | no rotor pulse (CNT11.8) for 10 sec, if rotor speed below P1.11 | down time | Operator
56 | gen. pulse sensor defect | 2 | 5 | no rotor pulse (CNT11.11) for 10 sec, if rotor speed below P1.11/P1.5 | down time | Operator
57 | ratio generator/rotor speed | 3 | 5 | variance P1.6 generator / rotor-gearbox for period P1.7 exceeded or immediate rot. speed list value failure | down time | Operator
58 | demand to stop by an external. device | 2 |  | DI1.27=0 | external stop time | Other
59 | vibration switch | 6 |  | vibration switch activated (DI11.9=1) | down time | Operator
60 | yaw end switch activated | 2 |  | azimuth end switch activated (DI1.15=1) | down time | Operator
61 |  | 4 |  |  | N/A
62 | PLC fault collection | 5 |  | failure fast bus communication to PLC slave at top box | down time | Operator
63 | safety chain | 6 |  | safety chain activated (DI1.14=0) | down time | Operator
64 | motor protection | 2 |  | motor protection control box MFR13 activated (DI1.5=0) | down time | Operator
65 | main switch activated | 4 |  | power switch activated (DI1.2=1) | down time | Operator
66
67
68
69
70
71 | gearbox oil soiled (shutdown) | 2 | 5 | filter soiled (course) for period P10.6 (DI12.7=1) | down time | Operator
72
73
74
75 | generator bearing A overtemperature | 2 | P13.11 | temperature above P13.4 for 60 sec, restart: temperature under P13.4 - 15oC | down time | Operator
76 | generator bearing B overtemperature | 2 | P13.11 | temperature above P13.5 for 60 sec, restart: temperature under P13.5 - 15oC | down time | Operator
77 | gearbox oil overtemperature | 2 | P13.11 | temperature above P13.8 for 60 sec, restart: temperature under P13.8 - 15oC | down time | Operator
78 | outside temperature too low | 2 | P13.11 | temperature above P13.10 for 60 sec, restart: temperature under P13.10 - 15oC | weather out time | Noone
79
80
81 | shaft bearing overtemperature | 2 | P13.11 | temperature above P13.12 for 60 sec, restart: temperature under P13.12 - 15oC (only from EW 1.5s) | down time. | Operator
82 | yaw motor overtemperature | 2 | A | one of the 3 PTC-temperature sensors on the azimuth motors report excessive temperature (> 155oC) (DI11.3=0) | down time | Operator
83 | gearbox bearing B overtemp. (ony offshore) | 2 | P13.11 | temperature above P13.10 for 60 sec, restart: temperature under P13.10 - 15oC | down time | Operator
84 | gearbox oil temp too low | 2 | P13.11 | temperature above P13.7 for 60 sec, restart: temperature under P13.7 + 5oC | weather out time | Noone
85
86 | brake pads worn, secondary brake | 2 |  | brake lining worn for 20 sec (DI12.2=0) (for BvB = 1) | down time | Operator
87 | restart time delay | 2 | A | set after mains outage, temperature errors, storm and calm, period P8.1 | system OK time | Noone
88 | multiple overtemp. Shutdown | 2 |  | display. P13.11 temp. errors 75-77, 81, 98-100, 107, 115, 139 exceeded | down time | Operator
89 | gearbox oil dirty (warning) | 0 | A | filter soiled (fine) for period P10.6 (DI12.6=1) | system OK time | Noone
90
91
92
93
94 | control call | 0 |  | parameter P23.6 > 0 causes an error number to be set for 30 sec. | system OK time | Noone
95 | PC restart | 0 |  | 180 sec after fresh PC reset set the message for 60 sec via watchdog function | system OK time | Noone
96
97 | generator cooling air overtemperature | 2 | P13.11 | temperature above P13.6 for 60 sec, restart: temperature below P13.6 - 15oC | down time | Operator
98 | gearbox bearing overtemperature | 2 | P13.11 | temperature above P13.9 for 60 sec, restart: temperature below P13.9 - 15oC | down time | Operator
99 | generator 1 overtemperature | 2 | P13.11 | temperature above P13.1 for 60 sec, restart: temperature below P13.1 - 15oC | down time | Operator
100 | generator 2 motor protection | 2 | P13.11 | temperature above P13.2 for 60 sec, restart: temperature below P13.2 - 15oC | down time | Operator
101 | motor protection fuse | 2 |  | 24V fuse protection in control box activated (DI1.6=0) | down time | Operator
102 | motor protection top cabinet | 2 |  | motor protection top cabinet activated (DI1.7=0) | down time | Operator
103 | generator 3 overtemperature | 2 | P13.11 | PTC-temperature generator sensor reports overtemp. (DI12.14=0) (for BvB and first Bachmann turbines not yet wired!) | down time | Operator
104
105 | rotor CCU fault voltage | 4 | 1 | voltage error, pulser (generator side) (DI1.19=0) | down time | Operator
106 | rotor CCU fault current | 4 | 1 | current error, pulser (generator side) DI1.20=0) | down time | Operator
107 | rotor CCU fault temperature | 4 | 5 | temperature error, pulser (generator side) (DI1.21=0) | down time | Operator
108 | rotor locking | 6b |  | one of the rotor locks is engaged (DI12.10=1) | maintenance time. Rotory service switch will take precedence. | Should never select availability clock.
109 | gen. carbon dust filter dirty | 0 |  | filter soiling for period P8.4 (DI11.20=1) | system OK time | Noone
110 | speed in tower resonance range | 2 | A | rot. speed in tower resonance range P1.8 - P1.9 for period P1.10 | system OK time | Noone
111
112 | response signal from CCU | 4 | 5 | control (DO1.13) and (acknowledgement freq. converter (DI1.18) AND acknowledgement main switch DI1.3)) differ from 65 sec | down time | Operator
113 | line CCU fault voltage | 4 | 1 | voltage error pulser (line side) (DI1.22=0) | down time | Operator
114 | line CCU fault current | 4 | 1 | current error pulser (line side) DI1.23=0) | down time | Operator
115 | line CCU fault temperature | 4 | 5 | temperature error pulser (line side) (DI1.24=0) | down time | Operator
116 | line fault voltage | 6a | A | mains voltage error (DI1.25=0) | line out time | Utility
117 | line fault frequency | 6a | A | mains frequency error (DI1.26=0) | line out time | Utility
118 | EMERGENCY STOP TOP-BOX | 6b |  | emergency off top-box/hub activated (DI1.16=1) | down time | Operator
119 | pitch controller timeout | 5 |  | 10 timeout periods of 150 ms exceeded from pitch controller | down time | Operator
120 | communication fault pitch controller | 5 |  | 6 communication errors in receipt package from pitch controller | down time | Operator
121 | axle disturbance 1 pitch controller | 5 | 1 | pitch controller reports axle disturbance for a period P12.12 (axle condition bit 7=1) | down time | Operator
122 | collective fault pitch controller | 5 | 1 | pitch controller reports unit disturbance for a period P12.12 (axle condition bit 7=1) | down time | Operator
123 | gearbox oil cooler switch contact | 2 | P13.11 | gearbox oil (60oC) exceeded for 1 sec (DI12.40=1), not for EW 1.5s | down time | Operator
124 | pitch overrun 0o | 5 |  | at least. 1 rotor blade at end switch (-30o) (DI11.28=0) | down time | Operator
125 | pitch overrun 90o | 4 |  | at least. 1 rotor blade at end switch (90o) (DI11.27=0) | down time | Operator
126
127
128
129 | generator speed implausible | 3 | 5 | variance P1.6 generator / gearbox exceeded for period P1.7 | down time | Operator
130 | braking time blade 1 too high | 6 |  | drive time P8.5 exceeded for blade 1 for blade shutdown to the feathered pitch position | down time | Operator
131 | braking time blade 2 too high | 6 |  | drive time P8.5 exceeded for blade 2 for blade shutdown to the feathered pitch position | down time | Operator
132 | braking time blade 3 tooo high | 6 |  | drive time P8.5 exceeded for blade 1 for blade shutdown to the feathered pitch position | down time | Operator
133 | battery charging rotor blade drive | 2 | A | battery charging at standstill for period 8.8 after message 'battery voltage too low' or 'braking time blade 1, 2 or 3 too long' after battery test double the time | down time | Operator
134 | battery charging voltage not OK | 2 | 5 | battery charging voltage not OK (KI11.29=0) or batt. Voltage too low (input 5 for each controller axis = 0, see P25.1-3) | down time | Operator
135 | battery test | 2 | A | battery test every 700 h, when the wind below 3.5 m/s | down time | Operator
136 | end switch rotor blade 0o defect | 6 |  | message blade at end switch (DI11.28=0) and blade angle > 0o | down time | Operator
137 | end switch rotor blade 90o defect | 4 |  | message blade at end switch (DI11.27=0) and blade angle < feathered pitch position | down time | Operator
138 | temperature warning pitch motor | 0 |  | warning temp exceeded for at least 1 pitch (bit 1 dig input pitch controller=0) | system OK time | Noone
139 | overtemperature pitch motor | 2 | P13.11 | max. temp exceeded for at least 1 pitch (bot 2 dig input pitch controller=0) | down time | Operator
140 | motor protection pitch motor | 4 |  | motor protection activated from at least one pitch motor (bit 1 dig input pitch controller=0) | down time | Operator
141 | rotor CCU collective fault | 4 | 1 | other errors PWR (DI1.19=0, DI1.20=0, DI2.21=0) | down time | Operator
142 | line CCU collective fault | 4 | 1 | other errors NPR (DI1.22=0, DI1.23=0, DI1.24=0) | down time | Operator
143 | pulse sensor rotor monitor defect | 2 | 5 | no pulses (DI12.1) to overspeed monitor for 10 sec, if gen. speed P1.11 is exceeded | down time | Operator
144 | blade angle asymmetry | 5 |  | deviation P12.9 of 2 blade angles for a period P12.10 or 4o for 200ms exceeded in pitch automatic mode | down time | Operator
145 | blade pitch control deviation | 5 |  | deviation P12.7 of blade angle actual and target values for aperiod P12.8 or in excess of 10o for 200 ms in regular pitch operation. When braking 6 times the deviation from P12.7 is allowable | down time | Operator
146 | turbine stopped due to calm | 2 | A | below 15% of speed P2.1 when spinning, 30 sec time delay, reset for exceeding wind 3.5 m/s at standstill | weather out time | Noone
147 | load shutdown | 2 |  | command load shutdown from turbine PC or remote PC causes shutdown in feathered pitch position | system ok time | Noone
148 | generator fan service switch | 2 |  | service switch gen. fan activated on top-box (DI11.15=0) | maintenance time. Rotory service switch will take precedence. | Should never select availability clock.
149 | axle 2 fault, pitch controller | 5 | 1 | pitch controller reports axle disturbance 2 for period P12.12 (axle condition bit 7=1) | down time | Operator
150 | axle 3 fault, pitch controller | 5 | 1 | pitch controller reports axle disturbance 3 for period P12.12 (axle condition bit 7=1) | down time | Operator
151 | response circuit breaker generator brush | 2 |  | not used in USA/Spain | down time | Operator
152 | obstruction light error/failure | 0 |  | if twilight switch (DI11.22)=1 and no appearance of a 24V signal of 24V-supply or fault/failure signal of Reetec device within 30 sec (DI11.23 / DI11.24=0) monitoring twilight switch : if P26.3 Bit 6=1 and between. 11 PM and 3 AM DI11.22=0 for 30 sec, then FM152, too. (from V1xx26) | system ok time | Noone
153 | brush wear generator | (2) |  | brush end switch reports excessive wear (DI11.19=0) (from turb. 3), after a period P8.11 the turbine is braked | system ok time / down time after P8.11 | Noone or Operator
154 | generator cooling water pressure/level not ok | 2 | 5 | only for TZ1.5cal monitor generator water cooling (DI11.21=0), if P26.3=1 | down time | Operator
155 | maintenance | 2 |  | service rotary switch is set to the 'maintenance' position (DI1.29= 1). No remote commands will be carried out. With a start command the turbine will restart for 30 minutes. | Maintenance Time | Operator for excess
156 | repair | 2 |  | service rotary switch is set to the 'repair' position (DI1.30 = 1). No remote commands will be carried out. With a start command the turbine will restart for 30 minutes. | Repair Time | Operator
157 | brake does not close | 6a |  | 1 sec after applying the brake message that brake still released (DI12.3 = 1) | Down time. | Operator
158
159
160
161 | Overvoltage protection triggered | 0 |  | The overvoltage protection device in main (DI1.16=0) or top switch cabinet (DI11.30-0) is faulty and can not make sure any overvoltage protection | System OK Time | Noone
162 | fault battery charge switching | 0 |  | charge switching relays stay 2h = 1 (dig Input 7 axis 2 at controller) | System OK Time | Noone
163 | torque deviation | 2 | 5 | assigned torque target value and power are implausible. Deviation converted to kW : 200 delayed by 30 sec. | Down Time | Operator
164 | maintenance switch pitch | 2 | A | a maintenance switch on the axle box switches the batteries away (DI11.26=0) | maintenance time. Rotory service switch will take precedence. | Should never select availability clock.
165 | service switch pitch | 2 | A | switch setting at the control box Hub is in manual operation, blade adjustment is possible from the controller, without an error or assigned target value from the PLC (dig. Input 7 axis 1 at controller) | System OK Time | Noone
166 | Normal operation | 0 |  | Signals end of : low noise operation, stop by an external device, ice alarm, Direction dependent shut-down | System OK Time | Noone
167 | voltage limitation activated | 0 |  | voltage is limited by assignment of an inductive reactive power < 1, phi <0o and/or power limitation | System OK Time | Noone
168 | azimuth slide lining | 0 | A | for changes in az. Tooth flanks (DI11.1, DI11.2) without az. Drive (30 sec delayed) | System OK Time | Noone
169 | waiting for gearbox oil pressure | 2 | A | when oil pump on (DO11.10=1), P10.1 (delay time oil pressure gearbox) >70 sec and curr. Delay time >5 sec. Note: why the turbine does not yet start after the START button has been activated | System OK Time | Noone
170 | increasing speed with falling blade angle | 0 | A | monitoring pitch / rot. Speed gradient: 50ms-averaged speed increases with falling blade angle -> delays for period P26.5 in ms, FM170 remains set for 2 sec | System OK Time | Noone
171 | service key brake release | 0 | A | when activating the button 'release brake' at the top-box (DI11.13-1) in the feathered pitch position. Message remains 30 sec after releasing the button | maintenance time. Rotory service switch will take precedence. | Should never select availability clock.
172 | Ice sensor alarm | 2 | A | The ice sensor detects for indicates low temperature and high humidity. Maybe there is ice at the rotor blades. | External Stop Time | Other
173 | low-noise operation | 0 | A | turbine runs at lower speed and power, cleared through P27.1. 'max. rotor speed 'low-noise' operation and activated via input DI1.31=1 | System OK Time in spec | Noone
174 | overtemp. Transformer warning (offshore only) | 0 |  | input D12.7-1 for 30 sec, signal from PTC resistor activation device MSF220K | N/A
175 | overtemp. Transformer disturbance (offshore only) | 2 |  | input D12.8=1 for 30 sec, signal from PTC resistor activation device MSF220K | N/A
176 | drive train vibration | 2 | 5 | drive train acceleration > P7.9 for period P7.10 and P2.12 bit 2=1 | Down Time | Operator
177 | tower vibration | 4 | 5 | Accelerometer monitors the frequency range around the tower's natural frequency (approx. 0.28 Hz) and alarms (DI11.31=0 and P7.12 bit 1 =1) or tower acceleration >P7.7 for period P7.8 and P7.12 bit 0-1 (for large/soft towers >=80m) | Down Time | Operator
178
179
180 | wind deviation | 4 | A | 1 sec-average wind direction deviation value>P7.5 (60o) or 10 sec average value ?P7.6 (40o) and 4 min-average wind speed >7 m/s | Down Time | Operator
181 | Idling position | 0 | A | turbine in spinning mode | System OK Time | Noone
182 | start up | 0 |  | turbine starting up / no/load mode | System OK Time | Noone
183 | load operation | 0 |  | turbine in load operation | System OK Time | Noone
184 | shutdown | 0 | A | turbine shutdown (braking) | System OK Time | Noone
185 | manual operation pitch | 4 |  | manual blade adjustment with pitch rate P12.5 (control function - blade angel or operating function at the top-box operating device) | maintenance time. Rotory service switch will take precedence. | Should never select availability clock.
186 | manual operation speed | 0 |  | manually assigned rot. Speed in no-load mode (control function - speed) | maintenance time. Rotory service switch will take precedence. | Should never select availability clock.
187 | manual operation torque | 0 |  | manually assigned torque in load operation (control function - frequency conversion) | maintenance time. Rotory service switch will take precedence. | Should never select availability clock.
188 | Manual operation, line separation | 0a |  | manual mains separation (control function - frequency conversion) speed regulation to target speed P3.4 in no-load mode | maintenance time. Rotory service switch will take precedence. | Should never select availability clock.
189 | manual operation yaw | 0 2, after 1h |  | manual azimuth adjustment or azimuth blocking with service switch (control - function - general, operation function at operating device at top-box) DI1.10-1, DI1.11-1 or DI11.10-1), 1h manual operation if the turbine is braked | maintenance time. Rotory service switch will take precedence. | Should never select availability clock.
190 | temperature error container (offshore only) | 0 | P13.11 | temperature below P13.14 for 60 sec or temperature above P13.15 for 60 sec, reset temperature over P13/14 +5oC and below P13.15 -5oC | Down Time. MVW- System Ok since no WTG braking. | Operator
191 | manual operation gen. Fan | 0 |  | in manual operation from PC (local or remote) or operating device, fan is then permanently on or off | maintenance time. Rotory service switch will take precedence. | Should never select availability clock.
192 | Wrong parameter checksum | 2 |  | At PLC restart the permanently stored parameters are checked against the saved check sum. If there is any differences the default values are loaded. This message 192 is generated and the tuirbine is stopped from running. Message remains set, until the release parameter (P26.12) and the tower resonce parameter (P1.8/9) are set correctly and the message is reset by the operator. | Down Time | Operator
193 | marine obstruction light (offshore only) | 0 |  | if twilight switch (DI11.22) - 1 DI12.15 (prewarning) or DI12.16 (failure) =0 longer than 30 sec | N/A
194 | by-pass filter soiling (offshore only) | 0 |  | if oil sump temp. >(P14.13 + P14.14)/2 (by-pass filter pump DO11.14-1) and DI12.8=1 longer than 5 mins. -> shutdown by-pass filter pump DO11.14-0 | N/A
195 | gearbox pressure loss by-pass filter (offshore only) | 0 |  | if by-pass filter pump P11.14-1 and DO11.14-1 and DI12.12-0 (pressure switch) longer than 10 sec -> shutdown by-pass filter pump DO11.14-0 | N/A
196 | Pre-heating fault CCU cooling system (offshore only) | 2 |  | No increasing of CCU cooling system temp. by 3K during 150s of pre-heating | N/A
197 | Overtemp. CCU cooling system (offshore only) | 2 | P13.11 | temperature above P13.15 for 60 sec, restart: temperature below P13.15-15oC | N/A
198 | pressure fault CCU cooling system (offshore only) | 2 |  | IF pump1- on OR (pump2= on AND valve 1,2-on) AND DI2.1=0 (pressure switch) THEN FM198 (5 sec delayed) | N/A
199 | test fault CCU cooling system (offshore only) | 0 |  | Not enough pressure (D12.1-0) during self test at turbine start | N/A
200 | Pre-heating CCU cooling system active (offshore only) | 2 |  | Pre-heating CCU cooling system active | N/A
201 | PLC fault 24V supply | 5 |  | The external 24V-power supply is failed at least one module of the control unit. (except DO216, DO232); possible error also defect module at 24V-side More details via P24.8, P24.9 | Down Time | Operator
202 | PLC module failure | 5 |  | There is a fault at at least 1 module of the control unit. (except power supply, CPU module) More details via P24.8, P24.9 | Down Time | Operator
203 | Fault temperature measurement | 2 |  | All temperature measurement at the PTAI module are constant for 10 minutes (resolution 01o) | Down Time | Operator
204 | FastBus Service Mode | 0 |  | From SW vers. 1x023 the PLC is configured without any reboot when there occurs a fast bus communication error. The communication to the slave is retired again only after a manual reboot of the PLC master. For service purposes the setting can be changed by the M-Manager to: - Reboot a Slave failure - Reboot at Slave detection With these settings FM204 appears. | System OK Time | Noone
205 | overtemperature TopBox (EW900 only) | 2 | P13.11 | temperature above P13.15 for 60 sec, restart: temperature below P13.15-15oC | N/A
206 | Gearbox pressure to0 high (EW900 only) | 2 |  | DI12.12=1 | N/A
207 | Ground fault LVMD (EW1.5/70.5(60Hz) only) | 2 |  | DI1.32-1, FM207 delayed P20.13 | Down Time | Operator
208 | No Activity CAN-Bus CCU | 3 |  | Live pulse (togglebit 15 in status word P29.1) stays constant for a period of 150ms -> CAN-Bus connection broken/disturbed or CCU switch off. | Down Time | Operator
209 | No activity CAN-Bus MFR13 | 2 | 5 | Multiplex number for CAN bus data from MFR13 (grid monitor device) stays constant for a period of 300ms -> CAN-Bus connection broken/disturbed or MFR13 switched off. | Down Time | Operator
210
211
212 | Battery Voltage low axis 1 | 2 |  | Battery voltage too low axis 1 (input 5 f. axis 1 at pitch controller =0, s. P25.1 and P25.9), from V1xx26 | Down Time | Operator
213 | Battery Voltage low axis 2 | 2 |  | Battery voltage too low axis 2 (input 5 f. axis 2 at pitch controller =0, s. P25.1 and P25.9), from V1xx26 | Down Time | Operator
214 | Battery Voltage low axis 3 | 2 |  | Battery voltage too low axis 1 (input 5 f. axis 3 at pitch controller =0, s. P25.1 and P25.9), from V1xx26 | Down Time | Operator
215 | Direction dependent shutdown | 2 | A | Nacelle position is inside the direction range defined by P24.4-8 and P> P27.9 or v> P24.10, restart if v <P27.11 or Nacelle position is outside the direction range from V1xx26 | External Stop Time | Noone
216 | obstruction light switch over to auxiliary lamps | 0 |  | If DI11.25-0 for 30 sec with activated twilight switch (DI11.22-1), then FM216, main lamps are defect, but obstruction light is still on with auxiliary lamps | System OK Time | Noone