## SUMMARY
PROJECT SUMMARY
VALUATION BASIS |  |  |  | VARIABLE O&M
| EXPECTED RUN HOURS | 1200 | Per Year |  | MAJOR MAINT ACCRUAL | 50 | $/TURBINE HOUR | see calc in SOURCEDATA
| VALUATION CAPACITY | 95* | Temp. |  | OTHER MAINTENANCE | 18 | $/TURBINE HOUR
| NET PLANT CAPACITY | 273.504 | MW |  | WATER | 0.5377 | $/MWh | see calc in SOURCEDATA
| NET PLANT HEAT RATE | 9332.0025 | Btu/kWh |  | TOTAL VARIABLE O&M | 2.0295 | $/MWh
USES OF FUNDS |  |  |  | FIXED O&M
TRUE | TOTAL EPC PROJECT COST | 142330.973 | '$(000) | TRUE | Direct Labor & Burden | 793.2592 | $1000/yr | cost scale factor | 171.2% | 30%
| CONSTRUCTION PERIOD | 9 | MONTHS |  | Admin | 295.0368 | $1000/yr
| INTEREST DURING CONSTRUCTION | 1793.3703 | '$(000) |  | Routine Maintenance | 561 | $1000/yr
| BOND FEES % | 0% | % |  | Misc Tools & Supplies | 109.9429 | $1000/yr
TRUE | BOND ISSUANCE CHARGE | 0 | '$(000) |  | SCR | 0 | $1000/yr | not turned on yet
| TOTAL USE OF FUNDS | 144124.3432 | '$(000) |  | LM6000 lease program | 0 | $1000/yr
|  |  |  | TRUE | Subcontracts | 244.9362 | $1000/yr
SOURCES OF FUNDS |  |  |  |  | TOTAL FIXED O&M | 0.61065 | $-kW month
| EQUITY | 50% | % |  |  | BRUCE, HEATHER HAS AN OEC ESTIMATE THAT ADDS UP TO 56¢ PER KW-MONTH
| EQUITY CONTRIBUTION | 72062.1716 | '$(000) | TOTAL OPERATING COST
| DEBT ISSUANCE | 72062.1716 | '$(000) | TRUE
| TERM | 20 | Years
| INTEREST RATE - MO. COMP. | 8% | Per Year
| ANNUAL DEBT SERVICE | 7233.0825 | '$(000)
| ANNUAL DEBT SERVICE | 2.9713 | Kw-month | TRUE
RETURN ON EQUITY
| TOTAL FIXED CHARGES (FOM & DEBT SRVC) | 3.5819
| PROPOSED CAPACITY PAYMENT | 6.37
| SALVAGE VALUE | 25%
| 20 YEAR IRR | 12%

## PROJECTCONFIGURATION
FALSE | PROJECT CONFIGURATION AT
|  | QTY |  | EACH |  | ADJ. |  | TOTAL |  | $/KW
| TURBINE |  |  | 14012 |  | 0 |  | 84072 |  | 307.3886
|  | UNION ? |  | EACH |  | ADJ. |  | TOTAL |  | $/KW
| BOP |  |  | 7840.1164 |  | 0 |  | 47040.6984 |  | 171.9927
|  | MILES |  | SIZE (IN.) |  | ADJ. |  | TOTAL |  | $/KW
| PIPELINE |  |  |  |  | 0 |  | 0 |  | 0
|  | YES |  | KV |  | ADJ. |  | TOTAL |  | $/KW
| POWER INTERCONNECTION |  |  |  |  | 0 |  | 0 |  | 0
|  | YES |  | EACH |  | ADJ. |  | TOTAL |  | $/KW
| SCR |  |  | 914.3078 |  | 0 |  | 5485.847 |  | 20.0576
|  | YES |  | EACH |  | ADJ. |  | TOTAL |  | $/KW
| DUAL FUEL |  |  | 0 |  | 0 |  | 0 |  | 0
|  | YES |  |  |  | ADJ. |  | TOTAL |  | $/KW
| BLACK START |  |  | FOR 1 TURBINE |  | 0 |  | 0 |  | 0
|  | YES |  | AVAILABLE PSIG |  | ADJ. |  | TOTAL |  | $/KW
| GAS COMPRESSION to 700 PSI |  |  | 600 |  |  |  | 0 |  | 0
|  |  |  | YES |  | ADJ. |  | TOTAL |  | $/KW
| DEMINERALIZED WATER FACILITY (need 75gpm/turbine) |  |  |  |  | 0 |  | 0 |  | 0
|  |  |  | YES |  |  |  | TOTAL |  | $/KW
| CHILLERS |  |  |  |  | 0 |  | 5732.4276 |  | 20.9592
|  |  |  | YES |  | ADJ. |  | TOTAL |  | $/KW
| SPARE PARTS |  |  |  |  | 0 |  | 0 |  | 0 |  | 1.25
6.25
| TOTAL ENGINEERING, PROCUREMENT AND CONSTRUCTION | [6 empty] | $000 |  | $/KW
[8 empty] | 142330.973 |  | 520.3981
28466.1946
|  | PIPELINE |  | KV |  | UNION ? | DUAL FUEL | BLACK START | COMPRESSION | DEMIN | SPARE | CHILLERS
| QTY TURBINES | MILES | SIZE | INTERCONNECT | SCR | [5 empty] | PARTS
| 6 | 0 | 16 | 230 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| 6 | 0 | 16 | 230 | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE
|  |  |  | FALSE | TRUE
| 0 | 0 | 0 | 0
| 1 | 1 | 4 | 69
| 2 | 2 | 10 | 138
| 3 | 3 | 16 | 230
| 4 | 4 | 24 | 345
| 5 | 5 |  | 500
| 6 | 6 |  | 745
| 7 | 7
| 8 | 8
| 9 | 9
| 10 | 10

## OPERATIONAL CHARACTERISTICS
OPERATIONAL CHARACTERISTICS
CAPACITY AND HEAT RATE |  |  | ISO | 95* | ISO | 95*
|  |  | with chilling | with chilling | no chilling | no chilling
| GROSS UNIT CAPACITY MW |  | 48.3 | 48.3 | 45.5 | 34.5
| UNIT AUXILIARY POWER (MW) | 1.5% | -0.7245 | -0.7245 | -0.6825 | -0.5175
| MAIN POWER TRANSFORMER (MW) | 0.5% | -0.2415 | -0.2415 | -0.2275 | -0.1725
| GAS COMPRESSION (MW) |  | 0 | 0 | 0 | 0 |  | this should be changed to incorporate real comprssion loads
| CHILLER LOAD |  | -0.2 | -1.75 | 0 | 0
45.584 | NET PLANT CAPACITY |  | 47.134 | 45.584 | 44.59 | 33.81
NOTE: These are New and Clean data
9332.0025 | HEAT RATE - PLANT NET OF GSU AND AUXILIARY (HHV) |  | 9025.1199 | 9332.0025 | 9054.9451 | 9657.202
| NOTE: These are New and Clean data | this also includes 3% GE/S&S margin
RAMP UP/DOWN TIME
| RAMP UP TIME |  | 10 | Minutes |  |  | this matches S&S claim - reality is more like 16 minutes for typical push button to full load
| RAMP DOWN TIME |  | 5 | Minutes
| TIME BEFORE RESTART |  | 30 | Minutes
RELIABILITY
| AVAILABILITY |  | 95% | Annually
| ENGINE LEASE PROGRAM - WITHIN 72 HOURS |  | 800 | $000 / Year
| MAJOR MAINTENANCE SCHEDULE |  | COST | TIME
| 5,000 HOURS |  | 250000 | 3 WEEKS
| 10,000 HOURS |  | 500000 | 5 WEEKS
| 15,000 HOURS |  | 250000 | 3 WEEKS
| 20,000 HOURS |  | 500000 | 5 WEEKS
| 25,000 HOURS |  | 1200000 | 10 WEEKS
CURRENT GE MARKET PRICE AND AVAILABILITY
| BASE TURBINE |  | 14000000
| SPRINT PACKAGE |  | 500000
| FIN FAN COOLER |  | 65000
| TOTAL TURBINE COST |  | 14565000
| DELIVERY |  | Q3 2001

## EPC DETAIL X 2 LM 6000
EPC DETAIL
PROJECT: | LM 6000 | 2 TURBINES IN |  | 2 TURBINES IN |  |  | 4 TURBINES IN |  | 4 TURBINES IN
LOCATION: | ROCKY MOUNT, NORTH CAROLINA | SIMPLE CYCLE |  | SIMPLE CYCLE |  |  | SIMPLE CYCLE |  | SIMPLE CYCLE
|  |  |  | base configuration |  |  |  |  | base configuration
DESCRIPTION OF ITEM |  | TOTAL |  | TOTAL |  |  | TOTAL |  | TOTAL
number of CTG's |  | 2 |  | 2 |  |  | 4 |  | 4
ENGINEERING
NEPCO ENGINEERING |  | 601000 |  | 601000 |  | 1.1 | 661100 |  | 661100
ENGINEERED EQUIPMENT
ELECTRICAL EQUIP |  | 2985080 |  | 2300080 |  | 2 | 5970160 |  | 4600160
DCS,CEMS,INST,VLVS |  | 476740 |  | 476740 |  | 2 | 953480 |  | 953480
HRSG |  | 0 |  | 0 |  | 2 | 0 |  | 0
GTG LM-6000 |  | 0 |  | 0 |  | 2 | 0 |  | 0
STG |  | 0 |  | 0 |  | 2 | 0 |  | 0
CHILLERS |  | 0 |  | 0 |  | 2 | 0 |  | 0
GAS COMPRESSORS |  | 0 |  | 0 |  | 2 | 0 |  | 0
FUEL GAS HEATERS |  | 0 |  | 0 |  | 2 | 0 |  | 0
FUEL GAS FILTERS |  | 40000 |  | 40000 |  | 2 | 80000 |  | 80000
ODORANT SKID |  | 0 |  | 0 |  | 2 | 0 |  | 0
PUMPS/MOTORS |  | 34350 |  | 34350 |  | 2 | 68700 |  | 68700
TANKS/VESSELS |  | 226500 |  | 120000 |  | 1.75 | 396375 |  | 210000
CHEMICAL FEEDS SKID |  | 25000 |  | 0 |  | 1.5 | 37500 |  | 0
AIR COMPRESSOR SKID |  | 21800 |  | 21800 |  | 1.5 | 32700 |  | 32700
STACK |  | 600000 |  | 600000 |  | 2 | 1200000 |  | 1200000
DIESEL GENERATOR -250KW |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  |  | this was a mistake - Nepco adjusted GC elsewhere
CTG TDI |  | 96000 |  | 96000 |  | 1.5 | 144000 |  | 144000
FREIGHT & HEAVY HAUL |  | 791990 |  | 791990 |  | 2 | 1583980 |  | 1583980
TOTAL ENGINEERED EQUIPMENT |  | 5297460 |  | 4480960 |  |  | 10466895 |  | 8873020
CONSTRUCTION
DIRECT COSTS
SITE WORK |  | 737360 |  | 650000 |  | 1.5 | 1106040 |  | 975000
U/G ELECTRICAL |  | 269335 |  | 200000 |  | 1.75 | 471336.25 |  | 350000
U/G PIPING |  | 469601 |  | 375000 |  | 1.75 | 821801.75 |  | 656250
CONCRETE & GROUT |  | 781695 |  | 600000 |  | 1.75 | 1367966.25 |  | 1050000
STRUCTURAL STEEL |  | 190710 |  | 175000 |  | 1.75 | 333742.5 |  | 306250
ARCHITECTURAL |  | 16500 |  | 16500 |  | 1.5 | 24750 |  | 24750
BUILDINGS |  | 187500 |  | 187500 |  | 1.5 | 281250 |  | 281250
A/G PIPING |  | 653657 |  | 550000 |  | 1.5 | 980485.5 |  | 825000
A/G ELECTRICAL |  | 754334 |  | 700000 |  | 1.5 | 1131501 |  | 1050000
INSTRUMENTATION |  | 129650 |  | 100000 |  | 1.5 | 194475 |  | 150000
INSULATION - MECH |  | 23919 |  | 23919 |  | 1.5 | 35878.5 |  | 35878.5
PAINTING |  | 56274 |  | 56274 |  | 1.5 | 84411 |  | 84411
HRSG |  | 0 |  | 0 |  | 1.5 | 0 |  | 0
GTG |  | 212000 |  | 212000 |  | 2 | 424000 |  | 424000
STG |  | 0 |  | 0 |  | 1.5 | 0 |  | 0
CHILLERS |  | 19800 |  | 0 |  | 2 | 39600 |  | 0
GAS COMPRESSORS |  | 0 |  | 0 |  | 1.5 | 0 |  | 0
PUMPS/MOTORS |  | 3700 |  | 3700 |  | 1.5 | 5550 |  | 5550
TANKS/VESSELS |  | 700 |  | 700 |  | 1.5 | 1050 |  | 1050
OTHER EQUIPMENT |  | 9750 |  | 9750 |  | 1.5 | 14625 |  | 14625
PRODUCTIVITY LOSS |  | 0 |  | 0 |  | 1.5 | 0 |  | 0
PER DIEM |  | 226812 |  | 226812 |  | 1.5 | 340218 |  | 340218
CONSTR BURDENS |  | 511273 |  | 425000 |  | 1.5 | 766909.5 |  | 637500
TOTAL DIRECT COSTS |  | 5254570 |  | 4512155 |  |  | 8425590.25 |  | 7211732.5
INDIRECT COSTS
PROJECT STAFF | 26% | 737100 |  | 700000 |  | 1.25 | 921375 |  | 875000
CONSTR EQUIPMENT | 3.5 | 305324 |  | 305324 |  | 1.25 | 381655 |  | 381655
SM TOOLS/CONSUM | 2 | 174471 |  | 174471 |  | 1.33 | 232046.43 |  | 232046.43
GEN'L COND - OTHER | 4.5 | 547560 |  | 520000 |  | 1.33 | 728254.8 |  | 691600
INDIRECT LABOR | 13% | 187100 |  | 187100 |  | 1.5 | 280650 |  | 280650
TOTAL INDIRECT COSTS |  | 1951555 |  | 1886895 |  |  | 2543981.23 |  | 2460951.43
TOTAL CONSTRUCTION |  | 7206125 |  | 6399050 |  |  | 10969571.48 |  | 9672683.93
START UP
START UP | 4.5 | 464256 |  | 464256 |  | 1.25 | 580320 |  | 580320
MANUALS & TRAINING |  | 35000 |  | 35000 |  | 1 | 35000 |  | 35000
TOTAL START UP |  | 499256 |  | 499256 |  |  | 615320 |  | 615320
OTHER COSTS
HOME OFFICE | 4% | 282045 |  | 282045 |  | 1.25 | 352556.25 |  | 352556.25
WARRANTY |  | 100000 |  | 100000 |  | 1 | 100000 |  | 100000
OVERHEAD |  | 1080930 |  | 1080930 |  | 1.5 | 1621395 |  | 1621395
TOTAL OTHER COSTS |  | 1462975 |  | 1462975 |  |  | 2073951.25 |  | 2073951.25
OTHER COSTS
TOTAL PROJECT COST |  | 15066816 |  | 13443241 |  |  | 24786837.73 |  | 21896075.18
MARGIN
CONTINGENCY |  | 450000 |  | 450000 |  | 1.75 | 787500 |  | 787500
FIXED G&A | 2% | 923000 |  | 923000 |  | 1.75 | 1615250 |  | 1615250
PROFIT |  | 2000000 |  | 2000000 |  | 1.5 | 3000000 |  | 3000000 |  | NO margin/Contingency
TOTAL MARGIN |  | 3373000 | LM6000's | 3373000 | LM6000's |  | 5402750 | LM6000's | 5402750 | LM6000's | LM6000's
|  |  | 28624000 |  | 28624000 |  |  | 57248000 |  | 57248000 | 57248000
| chillers |  | 1900000 |  | 0 |  |  | 3800000 |  | 0 | 0
| dual fuel |  | 560000 |  | 0 |  |  | 1120000 |  | 0 | 0
NEPCO TOTAL PROJECT COST WITH MARGIN |  | 18439816 | 49523816 | 16816241 | 45440241 |  | 30189587.73 | 92357587.73 | 27298825.18 | 84546825.18 | 79144075.18
|  | 9219908 | CHILLED | 8408120.5 | UN-CHILLED |  | 7547396.9325 | CHILLED | 6824706.295 | UN-CHILLED | UN-CHILLED
|  | ISO | 527.9725 |  | 501.5479 |  |  | 492.3112 |  | 466.594 | 436.7775
|  | CTG only at ISO | 305.1599 |  | 315.9382 |  |  | 305.1599 |  | 315.9382 | 315.9382
|  | 95 | 546.6205 |  | 676.1941 |  |  | 509.6997 |  | 629.0686 | 588.8696
|  | CTG only at 95F | 315.9382 |  | 425.9524 |  |  | 315.9382 |  | 425.9524 | 425.9524
MOBILIZATION (no spare parts) |  | 580000 |  | 580000 |  | 1.25 | 725000 |  | 725000
DEVELOPMENT COSTS |  | 0 |  | 0 |  | 1.25 | 0 |  | 0
INSURANCE/SITE/MISC OTHER OWNER COSTS |  | 0 |  | 0 |  | 1.75 | 0 |  | 0
SUBTOTAL OWNER COST |  | 580000 |  | 580000 |  |  | 725000 |  | 725000
TOTAL OWNER COST |  | 19019816 |  | 17396241 |  |  | 30914587.73 |  | 28023825.18
|  | 9509908 |  | 8698120.5 |  |  | 7728646.9325 |  | 7005956.295

## FINANCE
FINANCE
BREAK-EVEN ANALYSIS |  |  |  |  | DEBT SERVICE AMORTIZATION |  |  |  | EQUITY RETURNS
12%
GENERATION COST AT |  | 2.25 | / MMBTU IS | 23.7582 | MONTH | IPMT | PPMT | DEBT SRV. | YEAR | FIXED PMT | CAP PMT | IRR
-72062.1716
| RUN | FIXED | TOTAL |  | 1 | 480.4145 | 122.3424 | 602.7569 | 1 | 11756.1075 | 20906.6458 | 9150.5383
| HOURS | COST | GEN. COST |  | 2 | 479.5989 | 123.158 | 602.7569 | 2 | 11756.1075 | 20906.6458 | 9150.5383
| / YEAR | $ / MWH | $ / MWH |  | 3 | 478.7778 | 123.9791 | 602.7569 | 3 | 11756.1075 | 20906.6458 | 9150.5383
[5 empty] | 4 | 477.9513 | 124.8056 | 602.7569 | 4 | 11756.1075 | 20906.6458 | 9150.5383
| 500 | 85.9666 | 109.7248 | 23.7582 | 5 | 477.1192 | 125.6376 | 602.7569 | 5 | 11756.1075 | 20906.6458 | 9150.5383
| 600 | 71.6389 | 95.397 | 23.7582 | 6 | 476.2817 | 126.4752 | 602.7569 | 6 | 11756.1075 | 20906.6458 | 9150.5383
| 700 | 61.4047 | 85.1629 | 23.7582 | 7 | 475.4385 | 127.3184 | 602.7569 | 7 | 11756.1075 | 20906.6458 | 9150.5383
| 800 | 53.7291 | 77.4873 | 23.7582 | 8 | 474.5897 | 128.1672 | 602.7569 | 8 | 11756.1075 | 20906.6458 | 9150.5383
| 900 | 47.7592 | 71.5174 | 23.7582 | 9 | 473.7353 | 129.0216 | 602.7569 | 9 | 11756.1075 | 20906.6458 | 9150.5383
| 1000 | 42.9833 | 66.7415 | 23.7582 | 10 | 472.8751 | 129.8818 | 602.7569 | 10 | 11756.1075 | 20906.6458 | 9150.5383
| 1100 | 39.0757 | 62.8339 | 23.7582 | 11 | 472.0092 | 130.7476 | 602.7569 | 11 | 11756.1075 | 20906.6458 | 9150.5383
| 1200 | 35.8194 | 59.5776 | 23.7582 | 12 | 471.1376 | 131.6193 | 602.7569 | 12 | 11756.1075 | 20906.6458 | 9150.5383
| 1300 | 33.0641 | 56.8222 | 23.7582 | 13 | 470.2601 | 132.4968 | 602.7569 | 13 | 11756.1075 | 20906.6458 | 9150.5383
| 1400 | 30.7024 | 54.4605 | 23.7582 | 14 | 469.3768 | 133.3801 | 602.7569 | 14 | 11756.1075 | 20906.6458 | 9150.5383
| 1500 | 28.6555 | 52.4137 | 23.7582 | 15 | 468.4876 | 134.2693 | 602.7569 | 15 | 11756.1075 | 20906.6458 | 9150.5383
| 2000 | 21.4917 | 45.2498 | 23.7582 | 16 | 467.5925 | 135.1644 | 602.7569 | 16 | 11756.1075 | 20906.6458 | 9150.5383
| 2500 | 17.1933 | 40.9515 | 23.7582 | 17 | 466.6914 | 136.0655 | 602.7569 | 17 | 11756.1075 | 20906.6458 | 9150.5383
| 3000 | 14.3278 | 38.0859 | 23.7582 | 18 | 465.7843 | 136.9726 | 602.7569 | 18 | 11756.1075 | 20906.6458 | 9150.5383
| 3500 | 12.2809 | 36.0391 | 23.7582 | 19 | 464.8711 | 137.8858 | 602.7569 | 19 | 11756.1075 | 20906.6458 | 9150.5383
| 4000 | 10.7458 | 34.504 | 23.7582 | 20 | 463.9519 | 138.805 | 602.7569 | 20 | 11756.1075 | 56937.7316 | 45181.6241
[5 empty] | 21 | 463.0265 | 139.7304 | 602.7569 | 21 | 0 | 0 | 0
[5 empty] | 22 | 462.095 | 140.6619 | 602.7569 | 22 | 0 | 0 | 0
[5 empty] | 23 | 461.1572 | 141.5996 | 602.7569 | 23 | 0 | 0 | 0
[5 empty] | 24 | 460.2132 | 142.5436 | 602.7569 | 24 | 0 | 0 | 0
[5 empty] | 25 | 459.263 | 143.4939 | 602.7569 | 25 | 0 | 0 | 0
[5 empty] | 26 | 458.3063 | 144.4506 | 602.7569 | 26 | 0 | 0 | 0
[5 empty] | 27 | 457.3433 | 145.4136 | 602.7569 | 27 | 0 | 0 | 0
[5 empty] | 28 | 456.3739 | 146.383 | 602.7569 | 28 | 0 | 0 | 0
[5 empty] | 29 | 455.398 | 147.3589 | 602.7569 | 29 | 0 | 0 | 0
[5 empty] | 30 | 454.4156 | 148.3413 | 602.7569 | 30 | 0 | 0 | 0
[5 empty] | 31 | 453.4267 | 149.3302 | 602.7569
[5 empty] | 32 | 452.4311 | 150.3257 | 602.7569
[5 empty] | 33 | 451.429 | 151.3279 | 602.7569
[5 empty] | 34 | 450.4201 | 152.3368 | 602.7569
[5 empty] | 35 | 449.4045 | 153.3523 | 602.7569
[5 empty] | 36 | 448.3822 | 154.3747 | 602.7569
[5 empty] | 37 | 447.353 | 155.4039 | 602.7569
[5 empty] | 38 | 446.317 | 156.4399 | 602.7569
[5 empty] | 39 | 445.2741 | 157.4828 | 602.7569
[5 empty] | 40 | 444.2242 | 158.5327 | 602.7569
[5 empty] | 41 | 443.1673 | 159.5896 | 602.7569
[5 empty] | 42 | 442.1034 | 160.6535 | 602.7569
[5 empty] | 43 | 441.0323 | 161.7245 | 602.7569
[5 empty] | 44 | 439.9542 | 162.8027 | 602.7569
[5 empty] | 45 | 438.8688 | 163.888 | 602.7569
[5 empty] | 46 | 437.7762 | 164.9806 | 602.7569
[5 empty] | 47 | 436.6764 | 166.0805 | 602.7569
[5 empty] | 48 | 435.5692 | 167.1877 | 602.7569
[5 empty] | 49 | 434.4546 | 168.3023 | 602.7569
[5 empty] | 50 | 433.3326 | 169.4243 | 602.7569
[5 empty] | 51 | 432.2031 | 170.5538 | 602.7569
[5 empty] | 52 | 431.066 | 171.6908 | 602.7569
[5 empty] | 53 | 429.9214 | 172.8354 | 602.7569
[5 empty] | 54 | 428.7692 | 173.9877 | 602.7569
[5 empty] | 55 | 427.6093 | 175.1476 | 602.7569
[5 empty] | 56 | 426.4416 | 176.3152 | 602.7569
[5 empty] | 57 | 425.2662 | 177.4907 | 602.7569
[5 empty] | 58 | 424.0829 | 178.6739 | 602.7569
[5 empty] | 59 | 422.8918 | 179.8651 | 602.7569
[5 empty] | 60 | 421.6927 | 181.0642 | 602.7569
[5 empty] | 61 | 420.4856 | 182.2713 | 602.7569
[5 empty] | 62 | 419.2704 | 183.4864 | 602.7569
[5 empty] | 63 | 418.0472 | 184.7097 | 602.7569
[5 empty] | 64 | 416.8158 | 185.9411 | 602.7569
[5 empty] | 65 | 415.5762 | 187.1807 | 602.7569
[5 empty] | 66 | 414.3283 | 188.4286 | 602.7569
[5 empty] | 67 | 413.0721 | 189.6848 | 602.7569
[5 empty] | 68 | 411.8076 | 190.9493 | 602.7569
[5 empty] | 69 | 410.5346 | 192.2223 | 602.7569
[5 empty] | 70 | 409.2531 | 193.5038 | 602.7569
[5 empty] | 71 | 407.9631 | 194.7938 | 602.7569
[5 empty] | 72 | 406.6644 | 196.0924 | 602.7569
[5 empty] | 73 | 405.3571 | 197.3997 | 602.7569
[5 empty] | 74 | 404.0412 | 198.7157 | 602.7569
[5 empty] | 75 | 402.7164 | 200.0405 | 602.7569
[5 empty] | 76 | 401.3828 | 201.3741 | 602.7569
[5 empty] | 77 | 400.0403 | 202.7166 | 602.7569
[5 empty] | 78 | 398.6888 | 204.068 | 602.7569
[5 empty] | 79 | 397.3284 | 205.4285 | 602.7569
[5 empty] | 80 | 395.9589 | 206.798 | 602.7569
[5 empty] | 81 | 394.5802 | 208.1767 | 602.7569
[5 empty] | 82 | 393.1924 | 209.5645 | 602.7569
[5 empty] | 83 | 391.7953 | 210.9616 | 602.7569
[5 empty] | 84 | 390.3889 | 212.368 | 602.7569
[5 empty] | 85 | 388.9731 | 213.7838 | 602.7569
[5 empty] | 86 | 387.5478 | 215.209 | 602.7569
[5 empty] | 87 | 386.1131 | 216.6438 | 602.7569
[5 empty] | 88 | 384.6688 | 218.0881 | 602.7569
[5 empty] | 89 | 383.2149 | 219.542 | 602.7569
[5 empty] | 90 | 381.7513 | 221.0056 | 602.7569
[5 empty] | 91 | 380.2779 | 222.479 | 602.7569
[5 empty] | 92 | 378.7947 | 223.9621 | 602.7569
[5 empty] | 93 | 377.3016 | 225.4552 | 602.7569
[5 empty] | 94 | 375.7986 | 226.9583 | 602.7569
[5 empty] | 95 | 374.2856 | 228.4713 | 602.7569
[5 empty] | 96 | 372.7624 | 229.9945 | 602.7569
[5 empty] | 97 | 371.2291 | 231.5278 | 602.7569
[5 empty] | 98 | 369.6856 | 233.0713 | 602.7569
[5 empty] | 99 | 368.1318 | 234.6251 | 602.7569
[5 empty] | 100 | 366.5676 | 236.1893 | 602.7569
[5 empty] | 101 | 364.993 | 237.7638 | 602.7569
[5 empty] | 102 | 363.4079 | 239.3489 | 602.7569
[5 empty] | 103 | 361.8123 | 240.9446 | 602.7569
[5 empty] | 104 | 360.206 | 242.5509 | 602.7569
[5 empty] | 105 | 358.589 | 244.1679 | 602.7569
[5 empty] | 106 | 356.9612 | 245.7957 | 602.7569
[5 empty] | 107 | 355.3226 | 247.4343 | 602.7569
[5 empty] | 108 | 353.673 | 249.0839 | 602.7569
[5 empty] | 109 | 352.0124 | 250.7444 | 602.7569
[5 empty] | 110 | 350.3408 | 252.4161 | 602.7569
[5 empty] | 111 | 348.658 | 254.0989 | 602.7569
[5 empty] | 112 | 346.964 | 255.7928 | 602.7569
[5 empty] | 113 | 345.2587 | 257.4981 | 602.7569
[5 empty] | 114 | 343.5421 | 259.2148 | 602.7569
[5 empty] | 115 | 341.814 | 260.9429 | 602.7569
[5 empty] | 116 | 340.0744 | 262.6825 | 602.7569
[5 empty] | 117 | 338.3232 | 264.4337 | 602.7569
[5 empty] | 118 | 336.5603 | 266.1966 | 602.7569
[5 empty] | 119 | 334.7856 | 267.9713 | 602.7569
[5 empty] | 120 | 332.9991 | 269.7577 | 602.7569
[5 empty] | 121 | 331.2008 | 271.5561 | 602.7569
[5 empty] | 122 | 329.3904 | 273.3665 | 602.7569
[5 empty] | 123 | 327.5679 | 275.1889 | 602.7569
[5 empty] | 124 | 325.7334 | 277.0235 | 602.7569
[5 empty] | 125 | 323.8865 | 278.8703 | 602.7569
[5 empty] | 126 | 322.0274 | 280.7295 | 602.7569
[5 empty] | 127 | 320.1559 | 282.601 | 602.7569
[5 empty] | 128 | 318.2719 | 284.485 | 602.7569
[5 empty] | 129 | 316.3753 | 286.3816 | 602.7569
[5 empty] | 130 | 314.4661 | 288.2908 | 602.7569
[5 empty] | 131 | 312.5441 | 290.2127 | 602.7569
[5 empty] | 132 | 310.6094 | 292.1475 | 602.7569
[5 empty] | 133 | 308.6617 | 294.0951 | 602.7569
[5 empty] | 134 | 306.7011 | 296.0558 | 602.7569
[5 empty] | 135 | 304.7274 | 298.0295 | 602.7569
[5 empty] | 136 | 302.7405 | 300.0163 | 602.7569
[5 empty] | 137 | 300.7404 | 302.0164 | 602.7569
[5 empty] | 138 | 298.727 | 304.0299 | 602.7569
[5 empty] | 139 | 296.7001 | 306.0568 | 602.7569
[5 empty] | 140 | 294.6597 | 308.0971 | 602.7569
[5 empty] | 141 | 292.6058 | 310.1511 | 602.7569
[5 empty] | 142 | 290.5381 | 312.2188 | 602.7569
[5 empty] | 143 | 288.4566 | 314.3003 | 602.7569
[5 empty] | 144 | 286.3613 | 316.3956 | 602.7569
[5 empty] | 145 | 284.252 | 318.5049 | 602.7569
[5 empty] | 146 | 282.1286 | 320.6283 | 602.7569
[5 empty] | 147 | 279.9911 | 322.7658 | 602.7569
[5 empty] | 148 | 277.8393 | 324.9175 | 602.7569
[5 empty] | 149 | 275.6732 | 327.0837 | 602.7569
[5 empty] | 150 | 273.4927 | 329.2642 | 602.7569
[5 empty] | 151 | 271.2976 | 331.4593 | 602.7569
[5 empty] | 152 | 269.0878 | 333.669 | 602.7569
[5 empty] | 153 | 266.8634 | 335.8935 | 602.7569
[5 empty] | 154 | 264.6241 | 338.1328 | 602.7569
[5 empty] | 155 | 262.3699 | 340.387 | 602.7569
[5 empty] | 156 | 260.1006 | 342.6563 | 602.7569
[5 empty] | 157 | 257.8162 | 344.9406 | 602.7569
[5 empty] | 158 | 255.5166 | 347.2402 | 602.7569
[5 empty] | 159 | 253.2017 | 349.5552 | 602.7569
[5 empty] | 160 | 250.8713 | 351.8855 | 602.7569
[5 empty] | 161 | 248.5254 | 354.2314 | 602.7569
[5 empty] | 162 | 246.1639 | 356.593 | 602.7569
[5 empty] | 163 | 243.7866 | 358.9703 | 602.7569
[5 empty] | 164 | 241.3935 | 361.3634 | 602.7569
[5 empty] | 165 | 238.9844 | 363.7725 | 602.7569
[5 empty] | 166 | 236.5592 | 366.1977 | 602.7569
[5 empty] | 167 | 234.1179 | 368.639 | 602.7569
[5 empty] | 168 | 231.6603 | 371.0966 | 602.7569
[5 empty] | 169 | 229.1863 | 373.5705 | 602.7569
[5 empty] | 170 | 226.6959 | 376.061 | 602.7569
[5 empty] | 171 | 224.1888 | 378.5681 | 602.7569
[5 empty] | 172 | 221.665 | 381.0919 | 602.7569
[5 empty] | 173 | 219.1244 | 383.6325 | 602.7569
[5 empty] | 174 | 216.5668 | 386.19 | 602.7569
[5 empty] | 175 | 213.9922 | 388.7646 | 602.7569
[5 empty] | 176 | 211.4005 | 391.3564 | 602.7569
[5 empty] | 177 | 208.7914 | 393.9654 | 602.7569
[5 empty] | 178 | 206.165 | 396.5919 | 602.7569
[5 empty] | 179 | 203.5211 | 399.2358 | 602.7569
[5 empty] | 180 | 200.8595 | 401.8974 | 602.7569
[5 empty] | 181 | 198.1802 | 404.5767 | 602.7569
[5 empty] | 182 | 195.483 | 407.2739 | 602.7569
[5 empty] | 183 | 192.7678 | 409.989 | 602.7569
[5 empty] | 184 | 190.0346 | 412.7223 | 602.7569
[5 empty] | 185 | 187.2831 | 415.4738 | 602.7569
[5 empty] | 186 | 184.5133 | 418.2436 | 602.7569
[5 empty] | 187 | 181.725 | 421.0319 | 602.7569
[5 empty] | 188 | 178.9181 | 423.8388 | 602.7569
[5 empty] | 189 | 176.0925 | 426.6644 | 602.7569
[5 empty] | 190 | 173.2481 | 429.5088 | 602.7569
[5 empty] | 191 | 170.3847 | 432.3722 | 602.7569
[5 empty] | 192 | 167.5022 | 435.2547 | 602.7569
[5 empty] | 193 | 164.6005 | 438.1564 | 602.7569
[5 empty] | 194 | 161.6795 | 441.0774 | 602.7569
[5 empty] | 195 | 158.7389 | 444.0179 | 602.7569
[5 empty] | 196 | 155.7788 | 446.9781 | 602.7569
[5 empty] | 197 | 152.799 | 449.9579 | 602.7569
[5 empty] | 198 | 149.7992 | 452.9576 | 602.7569
[5 empty] | 199 | 146.7795 | 455.9773 | 602.7569
[5 empty] | 200 | 143.7397 | 459.0172 | 602.7569
[5 empty] | 201 | 140.6796 | 462.0773 | 602.7569
[5 empty] | 202 | 137.5991 | 465.1578 | 602.7569
[5 empty] | 203 | 134.498 | 468.2589 | 602.7569
[5 empty] | 204 | 131.3763 | 471.3806 | 602.7569
[5 empty] | 205 | 128.2337 | 474.5231 | 602.7569
[5 empty] | 206 | 125.0702 | 477.6866 | 602.7569
[5 empty] | 207 | 121.8857 | 480.8712 | 602.7569
[5 empty] | 208 | 118.6799 | 484.077 | 602.7569
[5 empty] | 209 | 115.4527 | 487.3042 | 602.7569
[5 empty] | 210 | 112.204 | 490.5529 | 602.7569
[5 empty] | 211 | 108.9336 | 493.8232 | 602.7569
[5 empty] | 212 | 105.6415 | 497.1154 | 602.7569
[5 empty] | 213 | 102.3274 | 500.4295 | 602.7569
[5 empty] | 214 | 98.9912 | 503.7657 | 602.7569
[5 empty] | 215 | 95.6327 | 507.1241 | 602.7569
[5 empty] | 216 | 92.2519 | 510.505 | 602.7569
[5 empty] | 217 | 88.8485 | 513.9083 | 602.7569
[5 empty] | 218 | 85.4225 | 517.3344 | 602.7569
[5 empty] | 219 | 81.9736 | 520.7833 | 602.7569
[5 empty] | 220 | 78.5017 | 524.2552 | 602.7569
[5 empty] | 221 | 75.0067 | 527.7502 | 602.7569
[5 empty] | 222 | 71.4883 | 531.2685 | 602.7569
[5 empty] | 223 | 67.9465 | 534.8103 | 602.7569
[5 empty] | 224 | 64.3811 | 538.3757 | 602.7569
[5 empty] | 225 | 60.792 | 541.9649 | 602.7569
[5 empty] | 226 | 57.1789 | 545.578 | 602.7569
[5 empty] | 227 | 53.5417 | 549.2152 | 602.7569
[5 empty] | 228 | 49.8803 | 552.8766 | 602.7569
[5 empty] | 229 | 46.1944 | 556.5625 | 602.7569
[5 empty] | 230 | 42.484 | 560.2729 | 602.7569
[5 empty] | 231 | 38.7488 | 564.008 | 602.7569
[5 empty] | 232 | 34.9888 | 567.7681 | 602.7569
[5 empty] | 233 | 31.2037 | 571.5532 | 602.7569
[5 empty] | 234 | 27.3933 | 575.3636 | 602.7569
[5 empty] | 235 | 23.5576 | 579.1993 | 602.7569
[5 empty] | 236 | 19.6962 | 583.0607 | 602.7569
[5 empty] | 237 | 15.8092 | 586.9477 | 602.7569
[5 empty] | 238 | 11.8962 | 590.8607 | 602.7569
[5 empty] | 239 | 7.9571 | 594.7998 | 602.7569
[5 empty] | 240 | 3.9918 | 598.7651 | 602.7569
[5 empty] | 241 | 0 | 0 | 0
[5 empty] | 242 | 0 | 0 | 0
[5 empty] | 243 | 0 | 0 | 0
[5 empty] | 244 | 0 | 0 | 0
[5 empty] | 245 | 0 | 0 | 0
[5 empty] | 246 | 0 | 0 | 0
[5 empty] | 247 | 0 | 0 | 0
[5 empty] | 248 | 0 | 0 | 0
[5 empty] | 249 | 0 | 0 | 0
[5 empty] | 250 | 0 | 0 | 0
[5 empty] | 251 | 0 | 0 | 0
[5 empty] | 252 | 0 | 0 | 0
[5 empty] | 253 | 0 | 0 | 0
[5 empty] | 254 | 0 | 0 | 0
[5 empty] | 255 | 0 | 0 | 0
[5 empty] | 256 | 0 | 0 | 0
[5 empty] | 257 | 0 | 0 | 0
[5 empty] | 258 | 0 | 0 | 0
[5 empty] | 259 | 0 | 0 | 0
[5 empty] | 260 | 0 | 0 | 0
[5 empty] | 261 | 0 | 0 | 0
[5 empty] | 262 | 0 | 0 | 0
[5 empty] | 263 | 0 | 0 | 0
[5 empty] | 264 | 0 | 0 | 0
[5 empty] | 265 | 0 | 0 | 0
[5 empty] | 266 | 0 | 0 | 0
[5 empty] | 267 | 0 | 0 | 0
[5 empty] | 268 | 0 | 0 | 0
[5 empty] | 269 | 0 | 0 | 0
[5 empty] | 270 | 0 | 0 | 0
[5 empty] | 271 | 0 | 0 | 0
[5 empty] | 272 | 0 | 0 | 0
[5 empty] | 273 | 0 | 0 | 0
[5 empty] | 274 | 0 | 0 | 0
[5 empty] | 275 | 0 | 0 | 0
[5 empty] | 276 | 0 | 0 | 0
[5 empty] | 277 | 0 | 0 | 0
[5 empty] | 278 | 0 | 0 | 0
[5 empty] | 279 | 0 | 0 | 0
[5 empty] | 280 | 0 | 0 | 0
[5 empty] | 281 | 0 | 0 | 0
[5 empty] | 282 | 0 | 0 | 0
[5 empty] | 283 | 0 | 0 | 0
[5 empty] | 284 | 0 | 0 | 0
[5 empty] | 285 | 0 | 0 | 0
[5 empty] | 286 | 0 | 0 | 0
[5 empty] | 287 | 0 | 0 | 0
[5 empty] | 288 | 0 | 0 | 0
[5 empty] | 289 | 0 | 0 | 0
[5 empty] | 290 | 0 | 0 | 0
[5 empty] | 291 | 0 | 0 | 0
[5 empty] | 292 | 0 | 0 | 0
[5 empty] | 293 | 0 | 0 | 0
[5 empty] | 294 | 0 | 0 | 0
[5 empty] | 295 | 0 | 0 | 0
[5 empty] | 296 | 0 | 0 | 0
[5 empty] | 297 | 0 | 0 | 0
[5 empty] | 298 | 0 | 0 | 0
[5 empty] | 299 | 0 | 0 | 0
[5 empty] | 300 | 0 | 0 | 0
[5 empty] | 301 | 0 | 0 | 0
[5 empty] | 302 | 0 | 0 | 0
[5 empty] | 303 | 0 | 0 | 0
[5 empty] | 304 | 0 | 0 | 0
[5 empty] | 305 | 0 | 0 | 0
[5 empty] | 306 | 0 | 0 | 0
[5 empty] | 307 | 0 | 0 | 0
[5 empty] | 308 | 0 | 0 | 0
[5 empty] | 309 | 0 | 0 | 0
[5 empty] | 310 | 0 | 0 | 0
[5 empty] | 311 | 0 | 0 | 0
[5 empty] | 312 | 0 | 0 | 0
[5 empty] | 313 | 0 | 0 | 0
[5 empty] | 314 | 0 | 0 | 0
[5 empty] | 315 | 0 | 0 | 0
[5 empty] | 316 | 0 | 0 | 0
[5 empty] | 317 | 0 | 0 | 0
[5 empty] | 318 | 0 | 0 | 0
[5 empty] | 319 | 0 | 0 | 0
[5 empty] | 320 | 0 | 0 | 0
[5 empty] | 321 | 0 | 0 | 0
[5 empty] | 322 | 0 | 0 | 0
[5 empty] | 323 | 0 | 0 | 0
[5 empty] | 324 | 0 | 0 | 0
[5 empty] | 325 | 0 | 0 | 0
[5 empty] | 326 | 0 | 0 | 0
[5 empty] | 327 | 0 | 0 | 0
[5 empty] | 328 | 0 | 0 | 0
[5 empty] | 329 | 0 | 0 | 0
[5 empty] | 330 | 0 | 0 | 0
[5 empty] | 331 | 0 | 0 | 0
[5 empty] | 332 | 0 | 0 | 0
[5 empty] | 333 | 0 | 0 | 0
[5 empty] | 334 | 0 | 0 | 0
[5 empty] | 335 | 0 | 0 | 0
[5 empty] | 336 | 0 | 0 | 0
[5 empty] | 337 | 0 | 0 | 0
[5 empty] | 338 | 0 | 0 | 0
[5 empty] | 339 | 0 | 0 | 0
[5 empty] | 340 | 0 | 0 | 0
[5 empty] | 341 | 0 | 0 | 0
[5 empty] | 342 | 0 | 0 | 0
[5 empty] | 343 | 0 | 0 | 0
[5 empty] | 344 | 0 | 0 | 0
[5 empty] | 345 | 0 | 0 | 0
[5 empty] | 346 | 0 | 0 | 0
[5 empty] | 347 | 0 | 0 | 0
[5 empty] | 348 | 0 | 0 | 0
[5 empty] | 349 | 0 | 0 | 0
[5 empty] | 350 | 0 | 0 | 0
[5 empty] | 351 | 0 | 0 | 0
[5 empty] | 352 | 0 | 0 | 0
[5 empty] | 353 | 0 | 0 | 0
[5 empty] | 354 | 0 | 0 | 0
[5 empty] | 355 | 0 | 0 | 0
[5 empty] | 356 | 0 | 0 | 0
[5 empty] | 357 | 0 | 0 | 0
[5 empty] | 358 | 0 | 0 | 0
[5 empty] | 359 | 0 | 0 | 0
[5 empty] | 360 | 0 | 0 | 0

## TURBINE AVAILABILITY
TURBINE DELIVERY SCHEDULE
UNIT | TURBINES | DELIVERY | LD'S
NUMBER | DELIVERED | SCHEDULE | ENFORCED ON
1-3 | 3 | 2000-07-30 | 2000-10-30
4-6 | 3 | 2000-08-30 | 2000-10-30
7-8 | 2 | 2000-09-30 | 2000-10-30
9-11 | 3 | 2000-10-30 | 2000-10-30
12-13 | 2 | 2000-11-30 | 2000-11-30
14-15 | 2 | 2000-12-30 | 2000-12-30
16-18 | 3 | 2000-01-30 | 2000-01-30
19-20 | 2 | 2001-02-28 | 2001-02-28
21-22 | 2 | 2001-03-30 | 2001-03-30
23-24 | 2 | 2001-04-30 | 2001-04-30
|  | BASE TURBINE | 13500000
|  | SPRINT OPTION | 450000
|  | FIN FAN COOLERS | 62000
|  | TOTAL PRICE | 14012000

## SOURCEDATA
SOURCE DATA
TURBINE | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| 14012 | 28024 | 42036 | 56048 | 70060 | 84072 | 98084 | 112096 | 126108 | 140120 |  | base $13800, $450Sprint, $62finfan
BOP | 8957.5 | 16905.9505 | 24608.9468 | 32172.6953 | 39641.8712 | 47040.6984 | 54384.195 | 61682.4929 | 68942.8411 | 76170.6539 |  | unit portion |  | 70% | took out HV breakers/switches
| 8957.5 | 8452.9753 | 8202.9823 | 8043.1738 | 7928.3742 | 7840.1164 | 7769.1707 | 7710.3116 | 7660.3157 | 7617.0654 |  | cost scale factor |  | 70%
PIPELINE $/MILE | 4 | 10 | 16 | 24
| 250 | 400 | 600 | 1000
POWER INTERCONNECTION |  | 69 | 138 | 240 | 345 | 500 | 745
| base cost >> | 235 | 235 | 235 | 235 | 235 | 235 |  |  |  |  | base 69 kV - $50-building, $30-UPS/batt, $120-metering,$30-base site/fence
| per bkr/Dend | 250 | 250 | 350 | 500 | 750 | 1000 |  |  |  |  | 138 kV breaker $$50K, 1 switch at $25k@, tubular buss 3 X 50' at $30/ft or $$5k, instrumentation $30k, deadend structure at $100k, construction at $40
| per breaker> | 150 | 200 | 300 | 400 | 500 | 600 |  |  |  |  | assumes 1 breaker per CTG plus 1 breaker as outgoing and one breaker position at far end
| 1 | 885 | 935 | 1235 | 1635 | 2235 | 2835 |  |  |  |  | table assumes paired units for ties to grid
| 2 | 885 | 935 | 1235 | 1635 | 2235 | 2835 |  |  |  |  | 138 kV breaker $$50K, 1 switch at $25k@, tubular buss 3 X 200' at $30/ft or $$18k, instrumentation $10k, construction at $47
| 3 | 1035 | 1135 | 1535 | 2035 | 2735 | 3435 |  |  |  |  | 230 kV breaker $$70K, 1 switch at $35k@, tubular buss 3 X 200' at $40/ft or $$24k, instrumentation $10k, construction at $60
| 4 | 1035 | 1135 | 1535 | 2035 | 2735 | 3435
| 5 | 1185 | 1335 | 1835 | 2435 | 3235 | 4035
| 6 | 1185 | 1335 | 1835 | 2435 | 3235 | 4035
| 7 | 1335 | 1535 | 2135 | 2835 | 3735 | 4635
| 8 | 1335 | 1535 | 2135 | 2835 | 3735 | 4635
| 9 | 1485 | 1735 | 2435 | 3235 | 4235 | 5235
| 10 | 1485 | 1735 | 2435 | 3235 | 4235 | 5235
SCR | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| 1000 | 1931.8727 | 2839.6525 | 3732.132 | 4613.4042 | 5485.847 | 6351.015 | 7210.0037 | 8063.6261 | 8912.5094 |  | cost scale factor |  | 95%
DUAL FUEL | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| 680 | 1268.9249 | 1827.7553 | 2367.8975 | 2894.5557 | 3410.7119 | 3918.2952 | 4418.653 | 4912.7784 | 5401.432 |  | cost scale factor |  | 90% | assume $280/CTG + fuel tank increase + filter - should add centrifuge if long downtimes or poor fuel
UNION PREMIUM | 20%
BLACK START | 1000
COMPRESSION |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | suction press. | psig | 600
INCREASE | 100 | 267.7869 | 405.889 | 517.6808 | 615.2127 | 703.3497 | 784.6574 | 860.6927 | 932.4881 | 1000.7712 | 1066.0788 | discharge press. | psig | 700
| 200 | 580.2049 | 879.4262 | 1121.6417 | 1332.9609 | 1523.9243 | 1700.091 | 1864.8342 | 2020.3909 | 2168.3377 | 2309.8374 | suction temp. | F | 80
| 300 | 900 | 1500.5594 | 1913.8502 | 2274.4227 | 2600.2625 | 2900.8545 | 3181.9549 | 3447.3802 | 3699.8209 | 3941.261 | compressor efficiency | % | 82%
| 400 | 1497.1721 | 2269.2886 | 2894.3063 | 3439.5983 | 3932.3642 | 4386.948 | 4812.0547 | 5213.4562 | 5595.2209 | 5960.3496 | design gas flow | MMscfd | 10
| 500 | 2511.5164 | 3806.747 | 4855.2184 | 5769.9495 | 6596.5676 | 7359.135 | 8072.2544 | 8745.608 | 9386.021 | 9998.5269 | gas compressibility |  | 0.92511
[12 empty] | compression ratio |  | 1.1804
[12 empty] | compression power | kW | 66.0526
[12 empty] | cost scale factor |  | 60%
[12 empty] | compression ratio factor |  | 1.1
DEMIN WATER | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| 600 | 848.5281 | 1039.2305 | 1200 | 1341.6408 | 1469.6938 | 1587.4508 | 1697.0563 | 1800 | 1897.3666 |  | cost scale factor |  | 50% | assumes 2X100% based on my catalog data
SPARE PARTS | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| 500 | 812.2524 | 1078.8346 | 1319.5079 | 1542.5847 | 1752.572 | 1952.2644 | 2143.5469 | 2327.7684 | 2505.9362 |  | cost scale factor |  | 70%
CHILLERS | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| 1250 | 2253.1262 | 3180.2633 | 4061.262 | 4909.4689 | 5732.4276 | 6534.9662 | 7320.4285 | 8091.2598 | 8849.3223 |  | cost scale factor |  | 85% | assumes at three CTG's goes to plant config
DEMIN WATER CONSUMPTION |  | 1: gal/MWhr; 2: 76.5957
| cost | 1: US$/1000gal; 2: 3.5
|  | US$/MWhr | 0.26809
RAW WATER CONSUMPTION |  | 1: gal/MWhr; 2: 168.5106
| cost | 1: US$/1000gal; 2: 1.6
|  | US$/MWhr | 0.26962
total water consumption |  | 1: US$/MWhr; 2: 0.5377
Estimated CTG accural |  | 1: US$/CTGyr; 2: 240000; 3: includes gas compression/chillers
Estimated operating hours |  | 1: hr/yr; 2: 1314
Estimated CTG accural |  | 1: US$/CTGhr; 2: 182.6484

## CLARIFICATIONS
Clarifications
1 | site assumed to be provided cleared and grubbed (usually Owner can get to clear and grub for the value of the lumber/pulpwood he gets)
2 | based on use of spread footings on a site that has a soil bearing pressure of 3000 psf at 3 feet
3 | soil from excavations on site is assumed to be suitable for backfill
4 | spoils will be stockpiled at site
5 | EPC includes initial fill of lubricants in equipment but does not include filling bulk storage tanks
6 | temporary utilities provided by others at site boundary including the following:
construction power - nominally 480V 3 phase 500 kVA
municipal or potable treated water - nominally 50 gpm at 50 psig
telephone service - ten lines
7 | all offsites not specifically included per the selection sheet will be provided by others including but not limited to the following:
all-weather hard surface access road from local highway (suitable for transport of the major components)
stormwater and treated wastewater drainage from the site boundary to the designated receiving stream or waters
temporary construction laydown, fabrication, equipment storage, … area
construction craft/equipment technician parking area
8 | all underground piping assumed to be installed with excavated materials from site (no imported fill)
9 | noise will be manufacturer standard - expect nominally 65 dBA at 400 feet from unit for single unit plant
10
11
12
Exclusions
1 | Permits and permit fees. EPC Cost includes supply of normal technical data in support of the Owner permit applications.
2 | Payment and Performance Bonds
3 | All Risk Insurance
4 | Sales and Use Taxes
5 | Extended Waranties beyond manufacturer standard 12 months.
6 | Spare parts except those required for plant startup
7 | Utility charges after initial synchronization to grid including backfeed through switchyard for startup.
8 | Utilities including water, sewer and fuel required for plant operation after Mechanical/Substantial Completion.
9 | Personnel for plant startup
10 | Disposal, handling or treatment of any existing hazardous materials.
11 | Demolition and removal of any existing structures or equipment, if required.
12 | Blasting or rock removal, per a comprehensive soils study
13 | Dewatering or well pointing beyond casual dewatering
14 | Caissons and/or piling.
15 | Tie-ins to municipal water and sewer
16 | Electrical transmission from power plant to untility substation and interconnection costs to local utility
17 | Cathodic protection.
18 | Mobil equipment
19 | monitoring wells
20 | machine shop equipment and tools
21 | Cancellation and accelerated equipment delivery costs
22 | furnishings for offices, buildings and laboratory
23 | Continuous Air Emission Monitoring System (CEMS)
24 | Administration building, shops, warehouse, laboratory