## 0102
Clear Sky Project Operational Report For January 2002
Executive Summary
This interim report was generated to comply with the contractual monthly reporting requirement from the Windsystem, Operations, & Maintenance Agreement.
The description of outages, safety near miss events, accidents, infrastructure work, and maintenance records are not included in this interim report.
All other required components are provided below. Production increased over prior Jan report due to corrections for incorrect turbine id's & comm losses.
|  |  |  | Operational Parameters | [7 empty] | Raw |  |  |  | Corrections
Site | Row | Pad | Reporting Month | kWh Generated 2 | kWh Consumed 2 | Net kWh Production | Capacity Factor | Availability1 | Operating Hrs |  | Data Recovery | kWhgen | kWhcons | Avail,num | Avail, denom | kWhgen | kWhcons | Avail,num | Avail, denom
ClearSky | 1 | 001 | 2002-01-01 | 237157 | 1024 | 236133 | 21.25% | 84.07% | 625.4755 |  | 0.96774 | 237157 | 1024 | 608.6086 | 723.9369
ClearSky | 1 | 002 | 2002-01-01 | 340336 | 544 | 339792 | 30.5% | 97.89% | 728.3278 |  | 0.90323 | 340336 | 544 | 724.3242 | 739.9102
ClearSky | 1 | 003 | 2002-01-01 | 359405 | 1225 | 358180 | 32.2% | 98.47% | 732.6317 |  | 0.90323 | 359405 | 1225 | 714.5481 | 725.6358
ClearSky | 1 | 004 | 2002-01-01 | 262481 | 901 | 261580 | 23.52% | 93.74% | 697.461 |  | 1 | 262481 | 901 | 693.6197 | 739.9025
ClearSky | 1 | 005 | 2002-01-01 | 330439 | 558 | 329881 | 29.61% | 89.16% | 663.3297 |  | 1 | 330439 | 558 | 646.6008 | 725.2366
ClearSky | 1 | 007 | 2002-01-01 | 337219 | 798 | 336421 | 30.22% | 93.62% | 696.5074 |  | 0.90323 | 337219 | 798 | 692.6428 | 739.8719
ClearSky | 1 | 008 | 2002-01-01 | 240905 | 1071 | 239834 | 21.59% | 75.42% | 561.1022 |  | 0.87097 | 240905 | 1071 | 557.9847 | 739.8663
ClearSky | 1 | 009 | 2002-01-01 | 341485 | 398 | 341087 | 30.6% | 94.35% | 701.9588 |  | 0.93548 | 341485 | 398 | 659.8936 | 699.4155
ClearSky | 1 | 013 | 2002-01-01 | 257440 | 616 | 256824 | 23.07% | 95.13% | 707.7965 |  | 1 | 257440 | 616 | 675.8931 | 710.4647
ClearSky | 1 | 014 | 2002-01-01 | 165909 | 390 | 165519 | 14.87% | 93.47% | 695.4342 |  | 0.90323 | 165909 | 390 | 691.5711 | 739.8672
ClearSky | 1 | 015 | 2002-01-01 | 236218 | 2046 | 234172 | 21.17% | 87.89% | 653.9214 |  | 0.93548 | 236218 | 2046 | 633.1028 | 720.3136
ClearSky | 1 | 017 | 2002-01-01 | 272174 | 928 | 271246 | 24.39% | 76.84% | 571.7252 |  | 1 | 272174 | 928 | 559.8686 | 728.5708
ClearSky | 1 | 018 | 2002-01-01 | 271772 | 536 | 271236 | 24.35% | 84.35% | 627.5862 |  | 0.87097 | 271772 | 536 | 587.5675 | 696.558
ClearSky | 1 | 019 | 2002-01-01 | 232681 | 1175 | 231506 | 20.85% | 83.97% | 624.7088 |  | 1 | 232681 | 1175 | 565.385 | 673.348
ClearSky | 1 | 020 | 2002-01-01 | 288700 | 583 | 288117 | 25.87% | 92.61% | 689.0213 |  | 0.80645 | 288700 | 583 | 645.5278 | 697.0361
ClearSky | 1 | 021 | 2002-01-01 | 297756 | 470 | 297286 | 26.68% | 87.6% | 651.7648 |  | 0.74194 | 277839 | 461 | 634.5389 | 724.3363 | 19917 | 9
ClearSky | 1 | 022 | 2002-01-01 | 297136 | 429 | 296707 | 26.63% | 85.68% | 637.4741 |  | 0.83871 | 297136 | 429 | 624.2403 | 728.5547
ClearSky | 1 | 023 | 2002-01-01 | 307152 | 273 | 306879 | 27.52% | 83.42% | 620.6727 |  | 0.96774 | 307152 | 273 | 617.2594 | 739.9086
ClearSky | 1 | 024 | 2002-01-01 | 281145 | 815 | 280330 | 25.19% | 92.24% | 686.2625 |  | 0.80645 | 281145 | 815 | 682.5019 | 739.923
ClearSky | 1 | 025 | 2002-01-01 | 286117 | 355 | 285762 | 25.64% | 75.97% | 565.1975 |  | 0.83871 | 286117 | 355 | 550.44 | 724.5738
ClearSky | 1 | 026 | 2002-01-01 | 330373 | 926 | 329447 | 29.6% | 86.58% | 644.161 |  | 0.74194 | 330373 | 926 | 640.6258 | 739.9169
ClearSky | 1 | 027 | 2002-01-01 | 364534 | 1056 | 363478 | 32.66% | 83.03% | 617.722 |  | 0.80645 | 364534 | 1056 | 614.3317 | 739.9166
ClearSky | 1 | 028 | 2002-01-01 | 388261 | 985 | 387276 | 34.79% | 85.66% | 637.3462 |  | 0.74194 | 388261 | 985 | 633.7131 | 739.7588
ClearSky | 1 | 029 | 2002-01-01 | 299825 | 759 | 299066 | 26.87% | 90.84% | 675.8644 |  | 0.96774 | 299825 | 759 | 672.1106 | 739.8677
ClearSky | 1 | 030 | 2002-01-01 | 253708 | 538 | 253170 | 22.73% | 88.45% | 658.1001 |  | 0.87097 | 253708 | 538 | 654.3653 | 739.7777
ClearSky | 1 | 031 | 2002-01-01 | 290863 | 691 | 290172 | 26.06% | 76.8% | 571.3704 |  | 0.93548 | 290863 | 691 | 568.2197 | 739.8975
ClearSky | 1 | 032 | 2002-01-01 | 360423 | 426 | 359997 | 32.3% | 100% | 744 |  | 0.87097 | 355074 | 285 | 735.3139 | 739.9094 | 5349 | 141 | 64.8258 | 0
ClearSky | 1 | 033 | 2002-01-01 | 281477 | 762 | 280715 | 25.22% | 100% | 744 |  | 0.83871 | 281477 | 662 | 662.3697 | 722.4025 |  | 100 | 62.7181 | 0
ClearSky | 1 | 034 | 2002-01-01 | 324855 | 610 | 324245 | 29.11% | 84.54% | 629.0134 |  | 1 | 324855 | 610 | 624.5689 | 738.743
ClearSky | 1 | 035 | 2002-01-01 | 323596 | 537 | 323059 | 29% | 81.35% | 605.2405 |  | 0.83871 | 323596 | 537 | 601.8353 | 739.8141
ClearSky | 1 | 036 | 2002-01-01 | 343692 | 589 | 343103 | 30.8% | 100% | 744 |  | 0.93548 | 343692 | 429 | 701.0714 | 725.6627 |  | 160 | 58.3933 | 0.0086111
ClearSky | 1 | 037 | 2002-01-01 | 70369 | 1631 | 68738 | 6.305% | 50.34% | 374.536 |  | 0.83871 | 70369 | 1631 | 372.0786 | 739.1186
ClearSky | 1 | 038 | 2002-01-01 | 43026 | 1283 | 41743 | 3.855% | 66.3% | 493.3045 |  | 1 | 43026 | 1283 | 489.3828 | 738.0852
ClearSky | 1 | 039 | 2002-01-01 | 88345 | 1675 | 86670 | 7.916% | 58.09% | 432.1798 |  | 0.93548 | 88345 | 1675 | 429.8028 | 739.908
ClearSky | 1 | 040 | 2002-01-01 | 330316 | 746 | 329570 | 29.6% | 85.41% | 635.4817 |  | 0.96774 | 330316 | 746 | 611.0244 | 715.3663
ClearSky | 1 | 041 | 2002-01-01 | 241341 | 1272 | 240069 | 21.63% | 70.72% | 526.1497 |  | 0.87097 | 241341 | 1272 | 523.2414 | 739.8875
ClearSky | 1 | 042 | 2002-01-01 | 134809 | 1832 | 132977 | 12.08% | 66.55% | 495.1684 |  | 1 | 134809 | 1832 | 484.6797 | 728.2405
ClearSky | 1 | 043 | 2002-01-01 | 345018 | 1026 | 343992 | 30.92% | 88.64% | 659.4472 |  | 0.83871 | 345018 | 1026 | 655.7681 | 739.8491
ClearSky | 1 | 044 | 2002-01-01 | 163093 | 1537 | 161556 | 14.61% | 61.29% | 456.001 |  | 0.74194 | 163093 | 1537 | 450.895 | 735.6691
ClearSky | 1 | 045 | 2002-01-01 | 74099 | 408 | 73691 | 6.64% | 32.24% | 239.8412 |  | 0.3871 | 74099 | 408 | 214.2936 | 664.75
ClearSky | 1 | 046 | 2002-01-01 | 337444 | 336 | 337108 | 30.24% | 79.82% | 593.8874 |  | 0.90323 | 337444 | 336 | 590.5769 | 739.8527
ClearSky | 1 | 047 | 2002-01-01 | 350904 | 543 | 350361 | 31.44% | 88.31% | 657.0162 |  | 0.80645 | 350904 | 543 | 653.3825 | 739.8852
ClearSky | 1 | 049 | 2002-01-01 | 305070 | 205 | 304865 | 27.34% | 80.59% | 599.5537 |  | 0.93548 | 305070 | 205 | 582.6119 | 722.9766
ClearSky | 1 | 050 | 2002-01-01 | 258506 | 364 | 258142 | 23.16% | 81.33% | 605.0773 |  | 0.87097 | 258506 | 364 | 586.1783 | 720.7619
ClearSky | 1 | 051 | 2002-01-01 | 299847 | 166 | 299681 | 26.87% | 89.12% | 663.064 |  | 0.54839 | 299847 | 166 | 659.41 | 739.9
ClearSky | 1 | 052 | 2002-01-01 | 291009 | 601 | 290408 | 26.08% | 86.83% | 646.0489 |  | 1 | 291009 | 601 | 642.4886 | 739.9
ClearSky | 1 | 053 | 2002-01-01 | 159083 | 1492 | 157591 | 14.25% | 60.71% | 451.6504 |  | 0.90323 | 159083 | 1492 | 449.1606 | 739.8986
ClearSky | 1 | 054 | 2002-01-01 | 320371 | 589 | 319782 | 28.71% | 86.49% | 643.5045 |  | 0.90323 | 320371 | 589 | 639.9706 | 739.9141
ClearSky | 1 | 055 | 2002-01-01 | 256089 | 998 | 255091 | 22.95% | 77.33% | 575.368 |  | 0.90323 | 256089 | 998 | 571.5142 | 739.0166
ClearSky | 1 | 056 | 2002-01-01 | 103702 | 813 | 102889 | 9.292% | 32.48% | 241.6825 |  | 1 | 103702 | 813 | 229.5533 | 706.6613
ClearSky | 1 | 057 | 2002-01-01 | 283241 | 1484 | 281757 | 25.38% | 71.67% | 533.211 |  | 0.83871 | 283241 | 1484 | 530.2853 | 739.9177
ClearSky | 1 | 058 | 2002-01-01 | 293972 | 1308 | 292664 | 26.34% | 63.47% | 472.2417 |  | 1 | 293972 | 1308 | 469.6467 | 739.9116
ClearSky | 1 | 059 | 2002-01-01 | 193139 | 1330 | 191809 | 17.31% | 87.99% | 654.6221 |  | 0.93548 | 193139 | 1330 | 565.8497 | 643.1072
ClearSky | 1 | 060 | 2002-01-01 | 270898 | 178 | 270720 | 24.27% | 87.69% | 652.4062 |  | 0.87097 | 270898 | 178 | 642.3017 | 732.4769
ClearSky | 1 | 061 | 2002-01-01 | 276154 | 637 | 275517 | 24.74% | 80.74% | 600.6884 |  | 0.83871 | 276154 | 637 | 597.3367 | 739.8486
ClearSky | 1 | 062 | 2002-01-01 | 313427 | 521 | 312906 | 28.08% | 100% | 744 |  | 0.90323 | 313427 | 324 | 700.8758 | 736.0975 |  | 197 | 70.1842 | 0
ClearSky | 1 | 063 | 2002-01-01 | 272480 | 900 | 271580 | 24.42% | 99.86% | 742.9453 |  | 0.80645 | 272480 | 629 | 661.8742 | 738.0813 |  | 271 | 75.1608 | 0
ClearSky | 1 | 064 | 2002-01-01 | 182625 | 1370 | 181255 | 16.36% | 90.91% | 676.3782 |  | 0.96774 | 182625 | 1116 | 577.3008 | 718.1 |  | 254 | 75.5314 | 0
ClearSky | 1 | 065 | 2002-01-01 | 300844 | 736 | 300108 | 26.96% | 100% | 744 |  | 0.87097 | 300844 | 445 | 684.4794 | 739.1486 |  | 291 | 98.1636 | 0
ClearSky | 1 | 066 | 2002-01-01 | 266352 | 703 | 265649 | 23.87% | 87.01% | 647.3824 |  | 0.93548 | 266352 | 504 | 565.0381 | 739.8775 |  | 199 | 78.7642 | 0.0080556
ClearSky | 1 | 067 | 2002-01-01 | 99657 | 197 | 99460 | 8.93% | 97.03% | 721.9287 |  | 0.25806 | 99657 | 197 | 717.9506 | 739.9002
ClearSky | 1 | 068 | 2002-01-01 | 347291 | 537 | 346754 | 31.12% | 91.4% | 680.0378 |  | 0.80645 | 347291 | 537 | 675.6014 | 739.1463
ClearSky | 1 | 069 | 2002-01-01 | 279662 | 971 | 278691 | 25.06% | 85.64% | 637.1355 |  | 0.93548 | 279662 | 971 | 632.1847 | 738.2188
ClearSky | 1 | 070 | 2002-01-01 | 274807 | 1044 | 273763 | 24.62% | 68.18% | 507.2732 |  | 1 | 274807 | 1044 | 503.9722 | 739.1586
ClearSky | 1 | 071 | 2002-01-01 | 303190 | 764 | 302426 | 27.17% | 77.68% | 577.912 |  | 1 | 303190 | 764 | 574.1019 | 739.095
ClearSky | 1 | 072 | 2002-01-01 | 168312 | 1081 | 167231 | 15.08% | 77.4% | 575.8416 |  | 1 | 168312 | 1081 | 557.55 | 720.3669
ClearSky | 1 | 073 | 2002-01-01 | 376847 | 637 | 376210 | 33.77% | 100% | 744 |  | 0.70968 | 376847 | 351 | 724.7567 | 734.5902 |  | 286 | 90.4308 | 0
ClearSky | 1 | 074 | 2002-01-01 | 216791 | 1292 | 215499 | 19.43% | 79.7% | 592.9437 |  | 1 | 216791 | 1292 | 589.6781 | 739.9025
ClearSky | 1 | 075 | 2002-01-01 | 381763 | 656 | 381107 | 34.21% | 85.17% | 633.7 |  | 1 | 381763 | 656 | 630.1725 | 739.8586
ClearSky | 1 | 076 | 2002-01-01 | 317511 | 458 | 317053 | 28.45% | 76.79% | 571.3412 |  | 1 | 317511 | 458 | 567.6056 | 739.1355
ClearSky | 1 | 077 | 2002-01-01 | 342701 | 1391 | 341310 | 30.71% | 76.62% | 570.0864 |  | 0.96774 | 342701 | 1391 | 566.3456 | 739.118
ClearSky | 1 | 078 | 2002-01-01 | 251998 | 1018 | 250980 | 22.58% | 72.1% | 536.4288 |  | 1 | 251998 | 1018 | 532.9139 | 739.125
ClearSky | 1 | 079 | 2002-01-01 | 314685 | 418 | 314267 | 28.2% | 91.27% | 679.0523 |  | 0.87097 | 314685 | 418 | 653.8519 | 716.3894
ClearSky | 1 | 080 | 2002-01-01 | 301697 | 609 | 301088 | 27.03% | 76.89% | 572.0876 |  | 0.87097 | 301697 | 609 | 568.3431 | 739.1302
ClearSky | 1 | 081 | 2002-01-01 | 342455 | 396 | 342059 | 30.69% | 89.57% | 666.3945 |  | 0.93548 | 342455 | 396 | 642.2172 | 717.0072
ClearSky | 1 | 082 | 2002-01-01 | 179931 | 1096 | 178835 | 16.12% | 55.27% | 411.2034 |  | 1 | 179931 | 1096 | 402.9328 | 729.0358
ClearSky | 1 | 083 | 2002-01-01 | 68064 | 1244 | 66820 | 6.099% | 51.05% | 379.8117 |  | 0.90323 | 68064 | 1244 | 376.8556 | 738.2094
ClearSky | 1 | 084 | 2002-01-01 | 349537 | 533 | 349004 | 31.32% | 96.16% | 715.4211 |  | 0.87097 | 349537 | 460 | 687.4164 | 743.2272 |  | 73 | 27.2617 | 0
ClearSky | 1 | 085 | 2002-01-01 | 303353 | 744 | 302609 | 27.18% | 81.89% | 609.2372 |  | 0.87097 | 303353 | 635 | 605.2714 | 739.1569
ClearSky | 1 | 086 | 2002-01-01 | 196825 | 991 | 195834 | 17.64% | 66.08% | 491.6486 |  | 0.87097 | 196825 | 991 | 488.4042 | 739.0902
ClearSky | 1 | 087 | 2002-01-01 | 375257 | 429 | 374828 | 33.63% | 86.17% | 641.1045 |  | 0.93548 | 375257 | 429 | 636.9297 | 739.1552
ClearSky | 1 | 088 | 2002-01-01 | 297880 | 676 | 297204 | 26.69% | 68.2% | 507.4397 |  | 0.93548 | 297880 | 676 | 504.6592 | 739.9233
ClearSky | 1 | 089 | 2002-01-01 | 379593 | 686 | 378907 | 34.01% | 93.18% | 693.2858 |  | 0.74194 | 379593 | 577 | 656.5831 | 739.1452 |  | 109 | 32.1789 | 0
ClearSky | 1 | 090 | 2002-01-01 | 394981 | 546 | 394435 | 35.39% | 90.81% | 675.5938 |  | 0.83871 | 394981 | 546 | 671.1944 | 739.1552
ClearSky | 1 | 091 | 2002-01-01 | 227587 | 1073 | 226514 | 20.39% | 77.21% | 574.4194 |  | 1 | 227587 | 1073 | 534.7433 | 692.6108
ClearSky | 1 | 092 | 2002-01-01 | 252263 | 1052 | 251211 | 22.6% | 76.26% | 567.3424 |  | 0.90323 | 252263 | 1052 | 564.0761 | 739.7166
ClearSky | 1 | 093 | 2002-01-01 | 225348 | 1055 | 224293 | 20.19% | 61.84% | 460.0805 |  | 0.87097 | 225348 | 1055 | 422.6089 | 683.4044
ClearSky | 1 | 096 | 2002-01-01 | 327767 | 610 | 327157 | 29.37% | 85.59% | 636.7658 |  | 0.77419 | 327767 | 610 | 612.2014 | 715.2988
ClearSky | 1 | 100 | 2002-01-01 | 369911 | 653 | 369258 | 33.15% | 87.05% | 647.675 |  | 0.96774 | 369911 | 653 | 610.6431 | 701.4605
ClearSky | 1 | 102 | 2002-01-01 | 242023 | 887 | 241136 | 21.69% | 81.5% | 606.3966 |  | 0.87097 | 242023 | 887 | 506.8222 | 621.8302
ClearSky | 1 | 103 | 2002-01-01 | 298329 | 565 | 297764 | 26.73% | 77.9% | 579.5969 |  | 0.96774 | 298329 | 565 | 528.07 | 677.8575
ClearSky | 1 | 104 | 2002-01-01 | 328348 | 510 | 327838 | 29.42% | 82.22% | 611.7386 |  | 0.80645 | 328348 | 510 | 576.7667 | 701.4669
ClearSky | 1 | 105 | 2002-01-01 | 340965 | 685 | 340280 | 30.55% | 77.35% | 575.4683 |  | 1 | 340965 | 685 | 542.5475 | 701.438
ClearSky | 1 | 106 | 2002-01-01 | 233838 | 939 | 232899 | 20.95% | 71.11% | 529.0662 |  | 1 | 233838 | 939 | 525.9619 | 739.6347
ClearSky | 1 | 107 | 2002-01-01 | 177794 | 1160 | 176634 | 15.93% | 62.06% | 461.7336 |  | 1 | 177794 | 1160 | 450.3061 | 725.5866
ClearSky | 1 | 108 | 2002-01-01 | 304932 | 1167 | 303765 | 27.32% | 74.28% | 552.6643 |  | 1 | 304932 | 1167 | 547.7211 | 737.3455
ClearSky | 1 | 109 | 2002-01-01 | 355899 | 620 | 355279 | 31.89% | 87.66% | 652.2221 |  | 0.87097 | 355899 | 620 | 647.9783 | 739.1591
ClearSky | 1 | 113 | 2002-01-01 | 131269 | 1305 | 129964 | 11.76% | 67.3% | 500.7293 |  | 0.93548 | 131269 | 1305 | 440.3675 | 654.3125
ClearSky | 1 | 114 | 2002-01-01 | 353396 | 129 | 353267 | 31.67% | 95.99% | 714.2006 |  | 1 | 353396 | 129 | 708.7825 | 738.3558
ClearSky | 1 | 115 | 2002-01-01 | 240150 | 685 | 239465 | 21.52% | 79% | 587.7966 |  | 1 | 240150 | 685 | 584.5758 | 739.9233
ClearSky | 1 | 116 | 2002-01-01 | 180856 | 2017 | 178839 | 16.21% | 52.89% | 393.502 |  | 0.93548 | 180856 | 2017 | 390.7025 | 738.7069
ClearSky | 1 | 117 | 2002-01-01 | 369910 | 705 | 369205 | 33.15% | 92.71% | 689.7383 |  | 0.74194 | 369910 | 625 | 658.3381 | 739.1508 |  | 80 | 26.9047 | 0
ClearSky | 1 | 118 | 2002-01-01 | 317736 | 884 | 316852 | 28.47% | 74.88% | 557.1185 |  | 1 | 317736 | 884 | 553.4522 | 739.1038
ClearSky | 1 | 119 | 2002-01-01 | 235827 | 897 | 234930 | 21.13% | 78.28% | 582.3921 |  | 0.80645 | 235827 | 897 | 578.5806 | 739.1308
ClearSky | 1 | 120 | 2002-01-01 | 293222 | 701 | 292521 | 26.27% | 94.55% | 703.4418 |  | 0.70968 | 293222 | 701 | 682.9097 | 722.2841
ClearSky | 1 | 121 | 2002-01-01 | 139950 | 966 | 138984 | 12.54% | 36.4% | 270.8197 |  | 0.83871 | 139950 | 966 | 258.6675 | 710.6152
ClearSky | 1 | 122 | 2002-01-01 | 27558 | 124 | 27434 | 2.469% | 98.73% | 734.5614 |  | 0.096774 | 27558 | 124 | 730.5183 | 739.905
|  | Project, Before line losses | 2002-01-01 | 28870473 | 87501 | 28782972 | 24.18% | 80.95% | 64446.3938 |  | 0.74194 | 253919 | 538 | 675.8514 | 718.3441
|  | Assumed 2% Line Loss | 2002-01-01 | 577409.46 | 1750.02 | 575659.44 |  |  |  |  | 0.83871 | 281477 | 662 | 0 | 0
|  | Project, After line losses | 2002-01-01 | 28293063.54 | 85750.98 | 28207312.56 | 23.69% | 80.95% | 64446.3938 |  | 0.96774 | 363516 | 801 | 666.7517 | 743.2286
|  | Project, After line losses | Year To Date | 28293063.54 | 85750.98 | 28207312.56 | 23.69% | 80.95% | 64446.3938
Notes:
1) Turbines 21, 32,33, 36, 62-67, 73, 84, 89, 117, & 121 corrected for data loss at month end. WTG's 33, 42, 122, & 84 corrected for incorrect turbine id.
2) Data for Turbines 7,18,42,49,71,79,113 now provided.
OUTAGES AND CURTAILMENTS IN Jan 2002
Clear Sky
Grid Availability= |  | 100%
Time Off |  | Time On | Machines Affected | Reason |  |  | Charge | Elapsed Hrs | No of WTG Affected | Lost WTGHrs
No outages reported
0
74400
1

## 0202
Clear Sky Project Operational Report For February 2002
Executive Summary
This interim report was generated to comply with the contractual monthly reporting requirement from the Windsystem, Operations, & Maintenance Agreement.
The description of outages, safety near miss events, accidents, infrastructure work, and maintenance records are not included in this interim report.
All other required components are provided below.
|  |  |  | Operational Parameters | [6 empty] | Raw |  |  |  | Corrections
Site | Row | Pad | Reporting Month | kWh Generated | kWh Consumed | Net kWh Production | Capacity Factor | Availability1 | Operating Hrs | Data Recovery | kWhgen | kWhcons | Avail,num | Avail, denom | kWhgen | kWhcons | Avail,num | Avail, denom
ClearSky | 1 | 001 | 2002-02-01 | 191941 | 1028 | 190913 | 19.04% | 94.59% | 635.6581 | 1 | 191941 | 1028 | 606.6194 | 641.6189
ClearSky | 1 | 002 | 2002-02-01 | 219688 | 790 | 218898 | 21.79% | 99.59% | 669.2743 | 0.96429 | 219688 | 790 | 650.6081 | 653.5756
ClearSky | 1 | 003 | 2002-02-01 | 200828 | 1782 | 199046 | 19.92% | 99.76% | 670.3848 | 1 | -664851 | -3389 | 703.2064 | 683.2923
ClearSky | 1 | 004 | 2002-02-01 | 195687 | 867 | 194820 | 19.41% | 94.8% | 637.0279 | 1 | 195687 | 867 | 619.7197 | 654.0595
ClearSky | 1 | 005 | 2002-02-01 | 171906 | 883 | 171023 | 17.05% | 86.71% | 582.7069 | 1 | 171906 | 883 | 548.1128 | 632.4225
ClearSky | 1 | 007 | 2002-02-01 | 206613 | 1006 | 205607 | 20.5% | 96.16% | 646.1976 | 1 | 206613 | 1006 | 627.1042 | 652.462
ClearSky | 1 | 008 | 2002-02-01 | 157590 | 1082 | 156508 | 15.63% | 88.29% | 593.3393 | 1 | -256816 | -2434 | 831.7558 | 657.3811
ClearSky | 1 | 009 | 2002-02-01 | 241195 | 572 | 240623 | 23.93% | 94.59% | 635.6291 | 1 | 241195 | 572 | 617.5117 | 653.1636
ClearSky | 1 | 013 | 2002-02-01 | 161573 | 635 | 160938 | 16.03% | 92.36% | 620.6842 | 1 | 161573 | 635 | 590.9406 | 640.115
ClearSky | 1 | 014 | 2002-02-01 | 203040 | 282 | 202758 | 20.14% | 99.47% | 668.4283 | 1 | 203040 | 282 | 633.5933 | 637.2967
ClearSky | 1 | 015 | 2002-02-01 | 195268 | 1538 | 193730 | 19.37% | 85.11% | 571.9638 | 1 | 195268 | 1538 | 553.5225 | 650.6511
ClearSky | 1 | 017 | 2002-02-01 | 228194 | 252 | 227942 | 22.64% | 91.59% | 615.4816 | 0.39286 | 89158 | 252 | 650.8339 | 654.1239 | 139036 | 458 | 54.2472 | 2.7539
ClearSky | 1 | 018 | 2002-02-01 | 190141 | 477 | 189664 | 18.86% | 92.27% | 620.0813 | 0.96429 | 190141 | 477 | 581.4872 | 630.4923
ClearSky | 1 | 019 | 2002-02-01 | 177522 | 616 | 176906 | 17.61% | 95% | 638.421 | 0.96429 | 177522 | 616 | 542.5531 | 571.4075
ClearSky | 1 | 020 | 2002-02-01 | 223513 | 520 | 222993 | 22.17% | 95.8% | 643.8051 | 1 | 223513 | 520 | 590.1589 | 616.3223
ClearSky | 1 | 021 | 2002-02-01 | 198038 | 558 | 197480 | 19.65% | 92.47% | 621.3653 | 1 | 198038 | 558 | 594.3267 | 643.0759
ClearSky | 1 | 022 | 2002-02-01 | 205314 | 464 | 204850 | 20.37% | 98.16% | 659.6402 | 1 | 205314 | 464 | 610.4158 | 622.1711
ClearSky | 1 | 023 | 2002-02-01 | 249154 | 271 | 248883 | 24.72% | 99.15% | 666.2654 | 1 | 249154 | 271 | 647.1683 | 653.0564
ClearSky | 1 | 024 | 2002-02-01 | 163649 | 898 | 162751 | 16.24% | 70.41% | 473.1379 | 1 | 163649 | 898 | 446.9867 | 635.175
ClearSky | 1 | 025 | 2002-02-01 | 241362 | 287 | 241075 | 23.94% | 93.64% | 629.2417 | 1 | 241362 | 287 | 591.5478 | 632.0625
ClearSky | 1 | 026 | 2002-02-01 | 238995 | 954 | 238041 | 23.71% | 97.45% | 654.8499 | 1 | 238995 | 954 | 628.0025 | 644.7673
ClearSky | 1 | 027 | 2002-02-01 | 265585 | 1069 | 264516 | 26.35% | 99.08% | 665.799 | 1 | 265585 | 1069 | 646.8411 | 653.1834
ClearSky | 1 | 028 | 2002-02-01 | 330725 | 668 | 330057 | 32.81% | 99.31% | 667.3655 | 1 | 330725 | 668 | 648.3628 | 653.1831
ClearSky | 1 | 029 | 2002-02-01 | 240435 | 796 | 239639 | 23.85% | 98.51% | 662.0046 | 1 | 240435 | 796 | 641.4072 | 651.4095
ClearSky | 1 | 030 | 2002-02-01 | 220828 | 529 | 220299 | 21.91% | 97.15% | 652.8416 | 1 | 220828 | 529 | 626.2967 | 644.9939
ClearSky | 1 | 031 | 2002-02-01 | 237174 | 527 | 236647 | 23.53% | 93.11% | 625.7086 | 1 | 237174 | 527 | 596.4258 | 640.8686
ClearSky | 1 | 032 | 2002-02-01 | 197322 | 545 | 196777 | 19.58% | 91.63% | 615.7415 | 0.46429 | 197322 | 545 | 588.9861 | 643.1178
ClearSky | 1 | 033 | 2002-02-01 | 184520 | 870 | 183650 | 18.31% | 78% | 524.128 | 0.89286 | 184520 | 870 | 502.655 | 644.7867
ClearSky | 1 | 034 | 2002-02-01 | 183218 | 576 | 182642 | 18.18% | 93.59% | 628.9118 | 1 | 183218 | 576 | 598.9117 | 640.2623
ClearSky | 1 | 035 | 2002-02-01 | 266034 | 469 | 265565 | 26.39% | 91.91% | 617.6507 | 0.78571 | 266034 | 469 | 586.7225 | 638.6681
ClearSky | 1 | 036 | 2002-02-01 | 166238 | 722 | 165516 | 16.49% | 87.25% | 586.2918 | 1 | -406093 | -598 | 755.3964 | 683.6217
ClearSky | 1 | 037 | 2002-02-01 | 210569 | 668 | 209901 | 20.89% | 84.02% | 564.6041 | 1 | 210569 | 668 | 539.3033 | 642.2045
ClearSky | 1 | 038 | 2002-02-01 | 203768 | 644 | 203124 | 20.22% | 82.87% | 556.898 | 1 | 203768 | 644 | 531.2989 | 641.4278
ClearSky | 1 | 039 | 2002-02-01 | 291435 | 629 | 290806 | 28.91% | 96.44% | 648.0641 | 0.85714 | 291435 | 629 | 622.3558 | 645.66
ClearSky | 1 | 040 | 2002-02-01 | 181677 | 884 | 180793 | 18.02% | 86.97% | 584.4498 | 1 | 181677 | 884 | 544.5319 | 626.4203
ClearSky | 1 | 041 | 2002-02-01 | 289129 | 852 | 288277 | 28.68% | 85.58% | 575.0803 | 0.92857 | 289129 | 852 | 546.1856 | 638.5534
ClearSky | 1 | 042 | 2002-02-01 | 244232 | 779 | 243453 | 24.23% | 94.8% | 637.0266 | 0.96429 | 244232 | 712 | 609.6856 | 629.3209
ClearSky | 1 | 043 | 2002-02-01 | 324087 | 948 | 323139 | 32.15% | 71.12% | 477.951 | 0.96429 | 324087 | 779 | 609.7583 | 643.5525
ClearSky | 1 | 044 | 2002-02-01 | 267305 | 584 | 266721 | 26.52% | 94.88% | 637.6115 | 0.82143 | 267305 | 948 | 447.385 | 629.342
ClearSky | 1 | 045 | 2002-02-01 | 284784 | 384 | 284400 | 28.25% | 83.57% | 561.6104 | 1 | 284784 | 584 | 609.4147 | 642.6003
ClearSky | 1 | 046 | 2002-02-01 | 246342 | 580 | 245762 | 24.44% | 94.13% | 632.5408 | 1 | 246342 | 384 | 538.3622 | 644.5
ClearSky | 1 | 047 | 2002-02-01 | 276432 | 182 | 276250 | 27.42% | 98.11% | 659.2847 | 1 | 276432 | 580 | 607.1864 | 645.3817
ClearSky | 1 | 049 | 2002-02-01 | 262486 | 284 | 262202 | 26.04% | 97.45% | 654.8462 | 1 | 262486 | 182 | 631.0536 | 643.5423
ClearSky | 1 | 050 | 2002-02-01 | 243015 | 239 | 242776 | 24.11% | 88.83% | 596.911 | 1 | 243015 | 284 | 626.8439 | 643.582
ClearSky | 1 | 051 | 2002-02-01 | 231897 | 568 | 231329 | 23.01% | 95.38% | 640.9811 | 0.92857 | 231897 | 239 | 573.3558 | 645.7995
ClearSky | 1 | 052 | 2002-02-01 | 201797 | 1048 | 200749 | 20.02% | 77.11% | 518.1484 | 0.92857 | -296276 | -2202 | 852.6014 | 673.88
ClearSky | 1 | 053 | 2002-02-01 | 201797 | 545 | 201252 | 20.02% | 94.29% | 633.596 | 1 | 201797 | 1048 | 494.2425 | 641.3136
ClearSky | 1 | 054 | 2002-02-01 | 173575 | 1112 | 172463 | 17.22% | 71.35% | 479.5026 | 0.92857 | -309665 | -1635 | 756.2161 | 653.3189
ClearSky | 1 | 055 | 2002-02-01 | 173575 | 404 | 173171 | 17.22% | 68.01% | 457.012 | 1 | 173575 | 1112 | 457.7964 | 641.8975
ClearSky | 1 | 056 | 2002-02-01 | 155874 | 1051 | 154823 | 15.46% | 93.28% | 626.8385 | 1 | 155874 | 404 | 436.1289 | 641.6109
ClearSky | 1 | 057 | 2002-02-01 | 269805 | 745 | 269060 | 26.77% | 90.15% | 605.7769 | 1 | 269805 | 1051 | 597.9514 | 641.3495
ClearSky | 1 | 058 | 2002-02-01 | 300508 | 925 | 299583 | 29.81% | 95.05% | 638.7245 | 1 | 300508 | 745 | 568.2233 | 630.6589
ClearSky | 1 | 059 | 2002-02-01 | 277190 | 298 | 276892 | 27.5% | 48.91% | 328.6949 | 1 | 277190 | 925 | 578.3681 | 608.817
ClearSky | 1 | 060 | 2002-02-01 | 92081 | 820 | 91261 | 9.135% | 69.41% | 466.4473 | 0.85714 | 92081 | 298 | 320.5347 | 655.6348 |  | 80 | 74.3397 | 0.0052778
ClearSky | 1 | 061 | 2002-02-01 | 152371 | 721 | 151650 | 15.12% | 76.71% | 515.4879 | 1 | 152371 | 820 | 462.255 | 666.2781
ClearSky | 1 | 062 | 2002-02-01 | 173761 | 656 | 173105 | 17.24% | 98.56% | 662.344 | 0.92857 | 173761 | 721 | 502.7981 | 655.775 |  | 197 | 70.1842 | 0
ClearSky | 1 | 063 | 2002-02-01 | 234230 | 354 | 233876 | 23.24% | 91.78% | 616.759 | 0.89286 | 234230 | 656 | 646.94 | 656.6892 |  | 271 | 75.1608 | 0
ClearSky | 1 | 064 | 2002-02-01 | 145130 | 615 | 144515 | 14.4% | 75.5% | 507.3722 | 0.60714 | 145130 | 354 | 427.2239 | 465.8067 |  | 254 | 75.5314 | 0
ClearSky | 1 | 065 | 2002-02-01 | 217488 | 701 | 216787 | 21.58% | 89.18% | 599.2633 | 0.89286 | 217488 | 615 | 588.8714 | 656.587 |  | 291 | 98.1636 | 0
ClearSky | 1 | 066 | 2002-02-01 | 177638 | 924 | 176714 | 17.62% | 90.25% | 606.4504 | 0.96429 | 177638 | 701 | 586.4033 | 657.897 |  | 199 | 78.7642 | 0.0080556
ClearSky | 1 | 067 | 2002-02-01 | 194607 | 830 | 193777 | 19.31% | 90.24% | 606.3944 | 0.92857 | 194607 | 924 | 590.4636 | 654.6031
ClearSky | 1 | 068 | 2002-02-01 | 194607 | 848 | 193759 | 19.31% | 79.81% | 536.3415 | 0.92857 | 194607 | 924 | 590.4636 | 654.6031 |  | 305 | 71.8236 | 0.068611
ClearSky | 1 | 069 | 2002-02-01 | 217157 | 581 | 216576 | 21.54% | 91.75% | 616.5431 | 1 | 217157 | 830 | 590.2008 | 654.3723
ClearSky | 1 | 070 | 2002-02-01 | 212816 | 723 | 212093 | 21.11% | 89.64% | 602.3592 | 1 | 212816 | 848 | 523.7717 | 656.5686
ClearSky | 1 | 071 | 2002-02-01 | 247870 | 630 | 247240 | 24.59% | 92.25% | 619.9248 | 0.96429 | 247870 | 581 | 595.0436 | 648.8845
ClearSky | 1 | 072 | 2002-02-01 | 235307 | 909 | 234398 | 23.34% | 90.56% | 608.5429 | 1 | 235307 | 723 | 587.3475 | 655.5706
ClearSky | 1 | 073 | 2002-02-01 | 245600 | 687 | 244913 | 24.37% | 82.64% | 555.3207 | 0.92857 | 245600 | 630 | 605.1314 | 656.2817 |  | 286 | 90.4308 | 0
ClearSky | 1 | 074 | 2002-02-01 | 228434 | 528 | 227906 | 22.66% | 75.57% | 507.849 | 1 | 228434 | 909 | 594.0053 | 656.2642
ClearSky | 1 | 075 | 2002-02-01 | 222299 | 1280 | 221019 | 22.05% | 80.07% | 538.0422 | 0.96429 | 222299 | 687 | 539.0656 | 652.6473
ClearSky | 1 | 076 | 2002-02-01 | 217782 | 598 | 217184 | 21.61% | 83.51% | 561.1875 | 0.89286 | 217782 | 528 | 494.8167 | 655.0731
ClearSky | 1 | 077 | 2002-02-01 | 231740 | 754 | 230986 | 22.99% | 76.75% | 515.7767 | 0.89286 | 231740 | 1280 | 524.3225 | 655.1823
ClearSky | 1 | 078 | 2002-02-01 | 214838 | 780 | 214058 | 21.31% | 84.87% | 570.3578 | 1 | 214838 | 598 | 546.2325 | 654.4098
ClearSky | 1 | 079 | 2002-02-01 | 175487 | 649 | 174838 | 17.41% | 87.28% | 586.5529 | 1 | 175487 | 754 | 502.0297 | 654.407
ClearSky | 1 | 080 | 2002-02-01 | 207314 | 779 | 206535 | 20.57% | 72% | 483.8476 | 0.85714 | 207314 | 780 | 555.3394 | 654.6231
ClearSky | 1 | 081 | 2002-02-01 | 191862 | 686 | 191176 | 19.03% | 81.34% | 546.6354 | 1 | 191862 | 649 | 561.1611 | 643.227
ClearSky | 1 | 082 | 2002-02-01 | 242904 | 767 | 242137 | 24.1% | 83.46% | 560.8664 | 0.78571 | 242904 | 779 | 471.4844 | 655.147
ClearSky | 1 | 083 | 2002-02-01 | 178144 | 713 | 177431 | 17.67% | 85.64% | 575.5201 | 0.85714 | 178144 | 686 | 532.6208 | 655.0892
ClearSky | 1 | 084 | 2002-02-01 | 223313 | 870 | 222443 | 22.15% | 73.5% | 493.9276 | 0.92857 | 223313 | 767 | 544.4181 | 652.6103
ClearSky | 1 | 085 | 2002-02-01 | 231124 | 639 | 230485 | 22.93% | 85.13% | 572.0642 | 0.92857 | 231124 | 713 | 562.0625 | 656.6042
ClearSky | 1 | 086 | 2002-02-01 | 179137 | 928 | 178209 | 17.77% | 55.05% | 369.9572 | 0.89286 | 179137 | 870 | 482.3731 | 656.5975
ClearSky | 1 | 087 | 2002-02-01 | 253626 | 843 | 252783 | 25.16% | 82.02% | 551.206 | 0.89286 | 253626 | 639 | 558.6825 | 656.5984
ClearSky | 1 | 088 | 2002-02-01 | 166051 | 716 | 165335 | 16.47% | 86.75% | 582.9545 | 0.89286 | 166051 | 928 | 367.7392 | 668.2889
ClearSky | 1 | 089 | 2002-02-01 | 232603 | 662 | 231941 | 23.08% | 93.76% | 630.0517 | 0.89286 | 232603 | 822 | 542.8069 | 654.8148
ClearSky | 1 | 090 | 2002-02-01 | 255983 | 1206 | 254777 | 25.4% | 56.57% | 380.1195 | 0.92857 | 255983 | 716 | 568.0375 | 655.1223
ClearSky | 1 | 091 | 2002-02-01 | 216998 | 981 | 216017 | 21.53% | 60.62% | 407.3847 | 0.89286 | 216998 | 662 | 620.2636 | 656.287 |  | 259 | 80.6628 | 0
ClearSky | 1 | 092 | 2002-02-01 | 136176 | 778 | 135398 | 13.51% | 84.85% | 570.1705 | 0.96429 | 136176 | 1206 | 371.8444 | 657.6886
ClearSky | 1 | 093 | 2002-02-01 | 129445 | 612 | 128833 | 12.84% | 82.26% | 552.8034 | 0.92857 | 129445 | 981 | 397.7797 | 656.4739
ClearSky | 1 | 096 | 2002-02-01 | 278531 | 746 | 277785 | 27.63% | 96.79% | 650.4494 | 0.82143 | 278531 | 778 | 556.8219 | 656.5853
ClearSky | 1 | 100 | 2002-02-01 | 297259 | 812 | 296447 | 29.49% | 75.8% | 509.3904 | 0.92857 | 297259 | 748 | 555.5342 | 656.5678
ClearSky | 1 | 102 | 2002-02-01 | 298642 | 582 | 298060 | 29.63% | 80.19% | 538.892 | 1 | 298642 | 746 | 645.8208 | 667.5359
ClearSky | 1 | 103 | 2002-02-01 | 282934 | 642 | 282292 | 28.07% | 83.71% | 562.5393 | 1 | 282934 | 812 | 495.9867 | 654.6353
ClearSky | 1 | 104 | 2002-02-01 | 286804 | 819 | 285985 | 28.45% | 76.62% | 514.8918 | 1 | 286804 | 582 | 535.0392 | 667.5134
ClearSky | 1 | 105 | 2002-02-01 | 318212 | 1056 | 317156 | 31.57% | 76.16% | 511.8147 | 1 | 318212 | 642 | 549.3592 | 656.5731
ClearSky | 1 | 106 | 2002-02-01 | 181104 | 1288 | 179816 | 17.97% | 64.98% | 436.6798 | 0.92857 | 181104 | 819 | 502.2128 | 655.77
ClearSky | 1 | 107 | 2002-02-01 | 196699 | 679 | 196020 | 19.51% | 67.59% | 454.1791 | 1 | 196699 | 1056 | 498.7739 | 655.1956
ClearSky | 1 | 108 | 2002-02-01 | 199353 | 1232 | 198121 | 19.78% | 53.68% | 360.7585 | 0.96429 | 199353 | 1288 | 425.6164 | 655.2925
ClearSky | 1 | 109 | 2002-02-01 | 249741 | 167 | 249574 | 24.78% | 96.58% | 649.0106 | 0.78571 | 249741 | 679 | 425.0789 | 629.2614
ClearSky | 1 | 113 | 2002-02-01 | 160697 | 816 | 159881 | 15.94% | 70.97% | 476.9227 | 1 | 160697 | 1232 | 347.4442 | 647.5167
ClearSky | 1 | 114 | 2002-02-01 | 317307 | 1394 | 315913 | 31.48% | 75.5% | 507.3373 | 1 | 317307 | 167 | 625.9175 | 648.4067
ClearSky | 1 | 115 | 2002-02-01 | 231238 | 757 | 230481 | 22.94% | 79.15% | 531.8796 | 1 | 231238 | 816 | 453.1694 | 638.8486
ClearSky | 1 | 116 | 2002-02-01 | 227379 | 986 | 226393 | 22.56% | 70.7% | 475.1092 | 1 | 227379 | 1394 | 484.69 | 642.32
ClearSky | 1 | 117 | 2002-02-01 | 290713 | 819 | 289894 | 28.84% | 60.32% | 405.3813 | 0.78571 | 290713 | 757 | 519.335 | 656.4684
ClearSky | 1 | 118 | 2002-02-01 | 221840 | 587 | 221253 | 22.01% | 82.46% | 554.1276 | 0.92857 | 221840 | 986 | 463.9219 | 656.4945
ClearSky | 1 | 119 | 2002-02-01 | 189257 | 650 | 188607 | 18.78% | 97.32% | 653.9643 | 0.89286 | 189257 | 819 | 380.9839 | 631.8742
ClearSky | 1 | 120 | 2002-02-01 | 248491 | 933 | 247558 | 24.65% | 83.23% | 559.3219 | 0.92857 | 248491 | 587 | 550.78 | 668.2581
ClearSky | 1 | 121 | 2002-02-01 | 269431 | 966 | 268465 | 26.73% | 38.92% | 261.5129 | 1 | 269431 | 650 | 636.9167 | 654.8
ClearSky | 1 | 122 | 2002-02-01 | 211588 | 801 | 210787 | 20.99% | 90.1% | 605.472 | 0.96429 | 211588 | 933 | 553.6106 | 665.4559
|  | Project, Before line losses | 2002-02-01 | 23697712 | 79386 | 23618326 | 21.97% | 84.85% | 61012.6401
|  | Assumed 2% Line Loss | 2002-02-01 | 473954.24 | 1587.72 | 472366.52
|  | Project, After line losses | 2002-02-01 | 23223757.76 | 77798.28 | 23145959.48 | 21.53% | 84.85% | 61012.6401
|  | Project, After line losses | Year To Date | 51516821.3 | 163549.26 | 51353272.04 | 22.61% | 82.9% | 125459.0339
Notes:
1) Availability is based on Visupro Mon file instead of data displayed on Visupro screen. Turbines 3,8,36,52, and 54 corrected for meter resets.
2) Turbines 17, 60, 62-68, 73, and 91 were corrected to compensate for comm loss at beginning of month.
3) There were clock & meter adjustments (WTG 60-68) related to software changes that couldn't be corrected for. kWh could be low but the
affect on availability should be very small.
Clear Sky
GRID VARIANCE
Month: | 2002-02-02 |  |  | Reason: U=unscheduled outage, S= scheduled outage, F=fluctuation
Charge | Date off | Time off | Date on | Time on | Hrs. | 138/69 KV | Reason | Comments
W | 2002-02-12 | 13:30 | 2002-02-12 | 2:15 PM | 0.75 | 69 | U | Leak on 69 KV transformer
E | 2002-02-20 | 9:00 | 2002-02-20 | 17:20 | 8.3333 | 138 | S | Tie buss installation, not completed high winds
E | 2002-02-23 | 8:00 | 2002-02-23 | 14:30 | 6.5 | 138 | S | Complete tie bus welding.
E | 2002-02-28 | 8:00 | 2002-02-28 | 19:00 | 11 | 69 | S | Completion on lien items against site.

## 0302
Clear Sky Project Operational Report For March 2002
Executive Summary
This interim report was generated to comply with the contractual monthly reporting requirement from the Windsystem, Operations, & Maintenance Agreement.
The description of outages, safety near miss events, accidents, infrastructure work, and maintenance records are not included in this interim report.
All other required components are provided below.
|  |  |  | Operational Parameters | [6 empty] | Raw |  |  |  | Corrections
Site | Row | Pad | Reporting Month | kWh Generated | kWh Consumed | Net kWh Production | Capacity Factor | Availability1 | Operating Hrs | Data Recovery | kWhgen | kWhcons | Avail,num | Avail, denom | kWhgen | kWhcons | Avail,num | Avail, denom
ClearSky | 1 | 001 | 2002-03-01 | 306425 | 1040 | 305385 | 27.46% | 96.11% | 645.8665 | 100% | 306425 | 1040 | 711.0733 | 739.8452
ClearSky | 1 | 002 | 2002-03-01 | 298906 | 2181 | 296725 | 26.78% | 96.56% | 648.8713 | 100% | 298906 | 2181 | 711.9506 | 737.3277
ClearSky | 1 | 003 | 2002-03-01 | 340500 | 1531 | 338969 | 30.51% | 95.84% | 644.0711 | 100% | 340500 | 1531 | 696.2197 | 726.41
ClearSky | 1 | 004 | 2002-03-01 | 226549 | 1082 | 225467 | 20.3% | 84.27% | 566.2781 | 100% | 226549 | 1082 | 592.3808 | 702.9761
ClearSky | 1 | 005 | 2002-03-01 | 324605 | 890 | 323715 | 29.09% | 97.02% | 651.9868 | 100% | 324605 | 890 | 714.7294 | 736.6686
ClearSky | 1 | 007 | 2002-03-01 | 310980 | 1138 | 309842 | 27.87% | 100% | 672 | 100% | 310980 | 1138 | 740.3953 | 739.8386
ClearSky | 1 | 008 | 2002-03-01 | 240446 | 991 | 239455 | 21.55% | 95.59% | 642.3443 | 100% | 240446 | 991 | 645.9375 | 675.7591
ClearSky | 1 | 009 | 2002-03-01 | 247084 | 811 | 246273 | 22.14% | 96.89% | 651.1159 | 100% | 247084 | 811 | 716.7186 | 739.7069
ClearSky | 1 | 013 | 2002-03-01 | 251741 | 777 | 250964 | 22.56% | 91.39% | 614.1208 | 100% | 251741 | 777 | 675.2153 | 738.8525
ClearSky | 1 | 014 | 2002-03-01 | 253077 | 417 | 252660 | 22.68% | 94.28% | 633.5398 | 100% | 253077 | 417 | 691.9219 | 733.9263
ClearSky | 1 | 015 | 2002-03-01 | 179856 | 2773 | 177083 | 16.12% | 55.84% | 375.2447 | 100% | 179856 | 2773 | 410.3833 | 734.9275
ClearSky | 1 | 017 | 2002-03-01 | 181083 | 808 | 180275 | 16.23% | 98.23% | 660.1181 | 100% | -538790 | -3351 | 1003.0089 | 697.2341 | 719873 | 4159 | 360.3761 | 43.0342
ClearSky | 1 | 018 | 2002-03-01 | 228418 | 749 | 227669 | 20.47% | 100% | 672 | 100% | 228418 | 749 | 741.3589 | 739.8441
ClearSky | 1 | 019 | 2002-03-01 | 226485 | 1422 | 225063 | 20.29% | 98.28% | 660.4728 | 100% | 226485 | 1422 | 723.1647 | 735.7861
ClearSky | 1 | 020 | 2002-03-01 | 192230 | 807 | 191423 | 17.22% | 97.31% | 653.9468 | 100% | 192230 | 807 | 665.6819 | 684.0591
ClearSky | 1 | 021 | 2002-03-01 | 266157 | 859 | 265298 | 23.85% | 99.58% | 669.1901 | 100% | 266157 | 859 | 736.8194 | 739.9133
ClearSky | 1 | 022 | 2002-03-01 | 243024 | 482 | 242542 | 21.78% | 94.69% | 636.3325 | 100% | 243024 | 482 | 699.0128 | 738.1936
ClearSky | 1 | 023 | 2002-03-01 | 211946 | 430 | 211516 | 18.99% | 81.95% | 550.7047 | 100% | 211946 | 430 | 594.7569 | 725.755
ClearSky | 1 | 024 | 2002-03-01 | 277206 | 861 | 276345 | 24.84% | 99.32% | 667.4401 | 100% | 277206 | 861 | 734.7842 | 739.8041
ClearSky | 1 | 025 | 2002-03-01 | 297250 | 374 | 296876 | 26.64% | 99.96% | 671.7389 | 100% | 297250 | 374 | 708.0597 | 708.335
ClearSky | 1 | 026 | 2002-03-01 | 317524 | 1045 | 316479 | 28.45% | 99.04% | 665.5774 | 100% | 317524 | 1045 | 732.8411 | 739.9127
ClearSky | 1 | 027 | 2002-03-01 | 280281 | 1385 | 278896 | 25.11% | 99.55% | 668.9886 | 100% | 280281 | 1385 | 736.5969 | 739.9127
ClearSky | 1 | 028 | 2002-03-01 | 268511 | 1525 | 266986 | 24.06% | 89.75% | 603.0938 | 100% | 268511 | 1525 | 663.9514 | 739.8108
ClearSky | 1 | 029 | 2002-03-01 | 272326 | 1181 | 271145 | 24.4% | 100% | 672 | 100% | 272326 | 1181 | 740.7422 | 739.9183
ClearSky | 1 | 030 | 2002-03-01 | 267201 | 806 | 266395 | 23.94% | 99.47% | 668.415 | 100% | 267201 | 806 | 719.7339 | 723.5941
ClearSky | 1 | 031 | 2002-03-01 | 274447 | 743 | 273704 | 24.59% | 99.3% | 667.3054 | 100% | 274447 | 743 | 734.75 | 739.9191
ClearSky | 1 | 032 | 2002-03-01 | 292849 | 689 | 292160 | 26.24% | 99.5% | 668.6074 | 100% | 290680 | 653 | 736.1836 | 739.9191 | 2169 | 36 | 0 | 0
ClearSky | 1 | 033 | 2002-03-01 | 266802 | 1041 | 265761 | 23.91% | 100% | 672 | 100% | 266802 | 1041 | 724.5817 | 721.8433
ClearSky | 1 | 034 | 2002-03-01 | 318028 | 650 | 317378 | 28.5% | 98.57% | 662.4043 | 100% | 318028 | 650 | 729.3536 | 739.9191
ClearSky | 1 | 035 | 2002-03-01 | 219062 | 814 | 218248 | 19.63% | 69.3% | 465.7093 | 100% | 219062 | 814 | 512.4281 | 739.4133
ClearSky | 1 | 036 | 2002-03-01 | 322417 | 780 | 321637 | 28.89% | 97.07% | 652.3427 | 100% | 322417 | 780 | 718.0283 | 739.665
ClearSky | 1 | 037 | 2002-03-01 | 263241 | 1024 | 262217 | 23.59% | 98.72% | 663.4107 | 100% | 263241 | 1024 | 730.2733 | 739.7283
ClearSky | 1 | 038 | 2002-03-01 | 241192 | 797 | 240395 | 21.61% | 90.21% | 606.204 | 100% | 241192 | 797 | 667.2592 | 739.6819
ClearSky | 1 | 039 | 2002-03-01 | 247904 | 887 | 247017 | 22.21% | 100% | 672 | 100% | 247904 | 887 | 742.1344 | 739.0563
ClearSky | 1 | 040 | 2002-03-01 | 274587 | 993 | 273594 | 24.6% | 98.82% | 664.0408 | 100% | 274587 | 993 | 730.8025 | 739.5619
ClearSky | 1 | 041 | 2002-03-01 | 215287 | 1482 | 213805 | 19.29% | 69.37% | 466.1547 | 100% | 215287 | 1482 | 501.3247 | 722.7005
ClearSky | 1 | 042 | 2002-03-01 | 271480 | 939 | 270541 | 24.33% | 92.95% | 624.6065 | 100% | 270402 | 886 | 687.4689 | 739.6322 | 1078 | 53
ClearSky | 1 | 043 | 2002-03-01 | 296739 | 1340 | 295399 | 26.59% | 99.95% | 671.6775 | 100% | 296739 | 1340 | 739.3744 | 739.7294
ClearSky | 1 | 044 | 2002-03-01 | 354682 | 872 | 353810 | 31.78% | 98% | 658.543 | 100% | -423986 | -2932 | 1304.6642 | 783.8425 | 778668 | 3804 | 582.1114 | 46.5247
ClearSky | 1 | 045 | 2002-03-01 | 338293 | 759 | 337534 | 30.31% | 99.39% | 667.9147 | 100% | 338293 | 759 | 731.6569 | 736.1322
ClearSky | 1 | 046 | 2002-03-01 | 300992 | 481 | 300511 | 26.97% | 94.74% | 636.6493 | 100% | 300992 | 481 | 680.505 | 718.2908
ClearSky | 1 | 047 | 2002-03-01 | 307500 | 778 | 306722 | 27.55% | 93.45% | 627.9626 | 100% | 307500 | 778 | 666.3228 | 713.0502
ClearSky | 1 | 049 | 2002-03-01 | 318738 | 257 | 318481 | 28.56% | 100% | 672 | 100% | 318738 | 257 | 739.2036 | 737.2061
ClearSky | 1 | 050 | 2002-03-01 | 306282 | 359 | 305923 | 27.44% | 98.65% | 662.8969 | 100% | 306282 | 359 | 729.7647 | 739.7861
ClearSky | 1 | 051 | 2002-03-01 | 218796 | 204 | 218592 | 19.61% | 86.38% | 580.4583 | 100% | 218796 | 204 | 632.5011 | 732.2502
ClearSky | 1 | 052 | 2002-03-01 | 322651 | 566 | 322085 | 28.91% | 94.4% | 634.3678 | 100% | 322651 | 566 | 684.2453 | 724.8363
ClearSky | 1 | 053 | 2002-03-01 | 282604 | 952 | 281652 | 25.32% | 81.46% | 547.4231 | 100% | 282604 | 952 | 583.4303 | 716.2013
ClearSky | 1 | 054 | 2002-03-01 | 315516 | 764 | 314752 | 28.27% | 94% | 631.6464 | 100% | 315516 | 764 | 691.6056 | 735.7897
ClearSky | 1 | 055 | 2002-03-01 | 318800 | 1004 | 317796 | 28.57% | 98.73% | 663.4381 | 100% | 318800 | 1004 | 727.3897 | 736.7769
ClearSky | 1 | 056 | 2002-03-01 | 287334 | 425 | 286909 | 25.75% | 99.39% | 667.8779 | 100% | 287334 | 425 | 732.1092 | 736.6277
ClearSky | 1 | 057 | 2002-03-01 | 296871 | 640 | 296231 | 26.6% | 97.92% | 657.9901 | 100% | 296871 | 640 | 720.6014 | 735.9444
ClearSky | 1 | 058 | 2002-03-01 | 284571 | 1197 | 283374 | 25.5% | 91.16% | 612.571 | 100% | 284571 | 1197 | 645.5939 | 708.2266
ClearSky | 1 | 059 | 2002-03-01 | 280523 | 1336 | 279187 | 25.14% | 97.34% | 654.1264 | 100% | -561535 | -4994 | 999.4092 | 893.2794 | 842058 | 6330 | 292.3825 | 166.9336
ClearSky | 1 | 060 | 2002-03-01 | 283096 | 262 | 282834 | 25.37% | 99.58% | 669.1475 | 100% | 283096 | 262 | 729.4153 | 732.5247
ClearSky | 1 | 061 | 2002-03-01 | 223100 | 953 | 222147 | 19.99% | 74.77% | 502.4557 | 100% | 223100 | 953 | 545.6769 | 729.8055
ClearSky | 1 | 062 | 2002-03-01 | 245416 | 671 | 244745 | 21.99% | 99.64% | 669.5827 | 100% | 245416 | 671 | 730.0219 | 732.6575
ClearSky | 1 | 063 | 2002-03-01 | 213288 | 1275 | 212013 | 19.11% | 88.03% | 591.5473 | 100% | 213288 | 1275 | 640.6942 | 727.8311
ClearSky | 1 | 064 | 2002-03-01 | 230054 | 1077 | 228977 | 20.61% | 99.07% | 665.7229 | 100% | 230054 | 1077 | 725.7953 | 732.6388
ClearSky | 1 | 065 | 2002-03-01 | 263289 | 827 | 262462 | 23.59% | 96.05% | 645.4261 | 100% | 263289 | 827 | 703.6619 | 732.6336
ClearSky | 1 | 066 | 2002-03-01 | 295867 | 768 | 295099 | 26.51% | 99.07% | 665.7702 | 100% | 295867 | 768 | 726.1044 | 732.8988
ClearSky | 1 | 067 | 2002-03-01 | 0 | 0 | 0 | 0% | 0% | 0
ClearSky | 1 | 068 | 2002-03-01 | 239844 | 1183 | 238661 | 21.49% | 97.64% | 656.1393 | 100% | 239844 | 1183 | 714.9808 | 732.2638
ClearSky | 1 | 069 | 2002-03-01 | 326094 | 792 | 325302 | 29.22% | 100% | 672 | 100% | 227590 | 463 | 732.6731 | 732.5088 | 98504 | 329
ClearSky | 1 | 070 | 2002-03-01 | 222388 | 1171 | 221217 | 19.93% | 87.15% | 585.6733 | 100% | 152506 | 718 | 638.4742 | 732.5836 | 69882 | 453
ClearSky | 1 | 071 | 2002-03-01 | 317014 | 721 | 316293 | 28.41% | 99.46% | 668.3728 | 100% | 219388 | 436 | 728.5564 | 732.5102 | 97626 | 285
ClearSky | 1 | 072 | 2002-03-01 | 349961 | 1558 | 348403 | 31.36% | 99.22% | 666.7704 | 100% | 267410 | 908 | 711.2258 | 716.8041 | 82551 | 650
ClearSky | 1 | 073 | 2002-03-01 | 281944 | 786 | 281158 | 25.26% | 98.07% | 659.0463 | 100% | 281944 | 786 | 719.0167 | 733.1491
ClearSky | 1 | 074 | 2002-03-01 | 250080 | 1132 | 248948 | 22.41% | 95.82% | 643.9071 | 100% | 250080 | 1132 | 702.4072 | 733.0525
ClearSky | 1 | 075 | 2002-03-01 | 302295 | 888 | 301407 | 27.09% | 98.82% | 664.0515 | 100% | 302295 | 888 | 724.5294 | 733.2019
ClearSky | 1 | 076 | 2002-03-01 | 218834 | 661 | 218173 | 19.61% | 88.39% | 593.9573 | 100% | 218834 | 661 | 647.5603 | 732.6461
ClearSky | 1 | 077 | 2002-03-01 | 225093 | 990 | 224103 | 20.17% | 99.61% | 669.3898 | 100% | 225093 | 990 | 729.8186 | 732.6644
ClearSky | 1 | 078 | 2002-03-01 | 214972 | 938 | 214034 | 19.26% | 96.08% | 645.6248 | 100% | 214972 | 938 | 703.7078 | 732.4558
ClearSky | 1 | 079 | 2002-03-01 | 257116 | 688 | 256428 | 23.04% | 97.63% | 656.081 | 100% | 257116 | 688 | 714.9753 | 732.3233
ClearSky | 1 | 080 | 2002-03-01 | 273371 | 801 | 272570 | 24.5% | 97.22% | 653.3149 | 100% | 273371 | 801 | 712.175 | 732.5436
ClearSky | 1 | 081 | 2002-03-01 | 240689 | 748 | 239941 | 21.57% | 73.91% | 496.6432 | 100% | 240689 | 748 | 541.075 | 732.12
ClearSky | 1 | 082 | 2002-03-01 | 275906 | 760 | 275146 | 24.72% | 99.86% | 671.0511 | 100% | 175982 | 468 | 731.4786 | 732.513 | 99924 | 292
ClearSky | 1 | 083 | 2002-03-01 | 284369 | 663 | 283706 | 25.48% | 99.64% | 669.5552 | 100% | 178634 | 434 | 729.4794 | 732.143 | 105735 | 229
ClearSky | 1 | 084 | 2002-03-01 | 224897 | 1013 | 223884 | 20.15% | 91.33% | 613.7534 | 100% | 153452 | 603 | 668.7314 | 732.1955 | 71445 | 410
ClearSky | 1 | 085 | 2002-03-01 | 275270 | 963 | 274307 | 24.67% | 97.4% | 654.5086 | 100% | 197546 | 508 | 713.3786 | 732.4433 | 77724 | 455
ClearSky | 1 | 086 | 2002-03-01 | 252837 | 944 | 251893 | 22.66% | 70.59% | 474.3598 | 100% | 145465 | 630 | 517.0767 | 732.5147 | 107372 | 314
ClearSky | 1 | 087 | 2002-03-01 | 346832 | 606 | 346226 | 31.08% | 99.59% | 669.212 | 100% | 237220 | 348 | 693.3503 | 696.2388 | 109612 | 258
ClearSky | 1 | 088 | 2002-03-01 | 317744 | 801 | 316943 | 28.47% | 98.85% | 664.2498 | 100% | 223304 | 454 | 721.1506 | 729.5647 | 94440 | 347
ClearSky | 1 | 089 | 2002-03-01 | 286083 | 786 | 285297 | 25.63% | 100% | 672 | 100% | 232893 | 403 | 732.9339 | 732.4238 | 53190 | 383
ClearSky | 1 | 090 | 2002-03-01 | 281519 | 829 | 280690 | 25.23% | 99.97% | 671.7717 | 100% | 233466 | 425 | 732.2478 | 732.4966 | 48053 | 404
ClearSky | 1 | 091 | 2002-03-01 | 236777 | 525 | 236252 | 21.22% | 95.1% | 639.0508 | 100% | 236777 | 525 | 697.2825 | 733.2341
ClearSky | 1 | 092 | 2002-03-01 | 258709 | 814 | 257895 | 23.18% | 99.18% | 666.5189 | 100% | 205677 | 455 | 726.3331 | 732.3061 | 53032 | 359
ClearSky | 1 | 093 | 2002-03-01 | 246906 | 942 | 245964 | 22.12% | 97.34% | 654.1072 | 100% | -323067 | -3188 | 1358.0758 | 800.9008 | 569973 | 4130 | 645.6303 | 68.9667
ClearSky | 1 | 096 | 2002-03-01 | 257523 | 1018 | 256505 | 23.08% | 99.93% | 671.5569 | 100% | 201737 | 563 | 732.0728 | 732.5558 | 55786 | 455
ClearSky | 1 | 100 | 2002-03-01 | 157543 | 740 | 156803 | 14.12% | 96.2% | 646.4696 | 100% | 157543 | 740 | 704.7542 | 732.5863
ClearSky | 1 | 102 | 2002-03-01 | 250943 | 1036 | 249907 | 22.49% | 100% | 672 | 100% | 186415 | 601 | 732.5703 | 732.4283 | 64528 | 435
ClearSky | 1 | 103 | 2002-03-01 | 283683 | 930 | 282753 | 25.42% | 99.9% | 671.2967 | 100% | 214821 | 502 | 731.6861 | 732.4527 | 68862 | 428
ClearSky | 1 | 104 | 2002-03-01 | 237964 | 830 | 237134 | 21.32% | 95.85% | 644.1218 | 100% | 169838 | 488 | 702.1297 | 732.5186 | 68126 | 342
ClearSky | 1 | 105 | 2002-03-01 | 266748 | 914 | 265834 | 23.9% | 84.83% | 570.0853 | 100% | 187124 | 569 | 621.1408 | 732.1827 | 79624 | 345
ClearSky | 1 | 106 | 2002-03-01 | 285311 | 727 | 284584 | 25.57% | 96.03% | 645.3281 | 100% | 197819 | 407 | 703.2689 | 732.3355 | 87492 | 320
ClearSky | 1 | 107 | 2002-03-01 | 271597 | 911 | 270686 | 24.34% | 94% | 631.6821 | 100% | 189062 | 535 | 688.5083 | 732.4533 | 82535 | 376
ClearSky | 1 | 108 | 2002-03-01 | 244191 | 1362 | 242829 | 21.88% | 87.58% | 588.5396 | 100% | 145820 | 898 | 641.5597 | 732.5388 | 98371 | 464
ClearSky | 1 | 109 | 2002-03-01 | 326719 | 705 | 326014 | 29.28% | 95.5% | 641.7748 | 100% | 226951 | 426 | 699.5483 | 732.4944 | 99768 | 279
ClearSky | 1 | 113 | 2002-03-01 | 317952 | 815 | 317137 | 28.49% | 95.96% | 644.8417 | 100% | 201978 | 497 | 703.0925 | 732.7041 | 115974 | 318
ClearSky | 1 | 114 | 2002-03-01 | 394079 | 227 | 393852 | 35.31% | 98.84% | 664.1777 | 100% | 261583 | 129 | 731.1514 | 739.7625 | 132496 | 98
ClearSky | 1 | 115 | 2002-03-01 | 379420 | 649 | 378771 | 34% | 99.59% | 669.2501 | 100% | 242448 | 398 | 732.4728 | 735.4825 | 136972 | 251
ClearSky | 1 | 116 | 2002-03-01 | 379152 | 1406 | 377746 | 33.97% | 83.16% | 558.8665 | 100% | 324963 | 1101 | 615.1722 | 739.7038 | 54189 | 305
ClearSky | 1 | 117 | 2002-03-01 | 396507 | 695 | 395812 | 35.53% | 95.2% | 639.7154 | 100% | 319871 | 622 | 697.2728 | 732.4622 | 76636 | 73
ClearSky | 1 | 118 | 2002-03-01 | 347329 | 791 | 346538 | 31.12% | 99.54% | 668.885 | 100% | 249225 | 453 | 729.0706 | 732.4658 | 98104 | 338
ClearSky | 1 | 119 | 2002-03-01 | 289078 | 801 | 288277 | 25.9% | 92.93% | 624.4613 | 100% | 158170 | 495 | 680.3264 | 732.118 | 130908 | 306
ClearSky | 1 | 120 | 2002-03-01 | 406045 | 538 | 405507 | 36.38% | 99.99% | 671.9132 | 100% | 269100 | 335 | 733.0742 | 733.1688 | 136945 | 203
ClearSky | 1 | 121 | 2002-03-01 | 332048 | 946 | 331102 | 29.75% | 86.87% | 583.7875 | 100% | 199164 | 632 | 621.0814 | 714.9291 | 132884 | 314
ClearSky | 1 | 122 | 2002-03-01 | 356150 | 917 | 355233 | 31.91% | 95.83% | 643.9936 | 100% | 228391 | 566 | 701.9053 | 732.4302 | 127759 | 351
|  | Project, Before line losses | 2002-03-01 | 29489635 | 94632 | 29395003 | 24.7% | 93.75% | 67411.2966
|  | Assumed 2% Line Loss | 2002-03-01 | 589792.7 | 1892.64 | 587900.06
|  | Project, After line losses | 2002-03-01 | 28899842.3 | 92739.36 | 28807102.94 | 24.2% | 93.75% | 67411.2966
|  | Project, After line losses | Year To Date | 80416663.6 | 256288.62 | 80160374.98 | 23.14% | 86.52% | 192870.3305
Notes:
1) Availability is based on Visupro Mon file instead of data displayed on Visupro screen. Turbines 17, 44, 59, & 93 corrected for meter resets.
2) Turbines 32 and 42 were corrected to compensate for communication losses at the beginning of the month and an improper id setting.
3) Turbines 69, 70, 71,77,82 - 93, 96, 100, 102 - 109, and 113-122 were corrected to compensate for comm losses at the end of the month.
CLEAR SKY
GRID VARIANCE
Month: |  |  |  | Reason: U=unscheduled outage, S= scheduled outage, F=fluctuation
Charge | Date off | Time off | Date on | Time on | Hrs. | Reason | Comments
E | 2002-03-20 | 0750 | 2002-03-20 | 1430 | 7.16 | S | Scheduled power outage on 69kV line for moving arrestors to the correct side of gang switch and repairing damaged gang switch blade.
Grid Availability = |  | 99.04%

## Summary
Summary Of Performance
Month | 2002-01-01 | 2002-02-01 | 2002-03-01
Production, kWh
Monthly Generated kWh, Before Line Loss | 28870473 | 23697712 | 29489635
Monthly Assumed Line Loss | 577409.46 | 473954.24 | 589792.7
Monthly Generated kWh, After Line Loss 2 | 28293063.54 | 23223757.76 | 28899842.3
Monthly Generated MWh, After Line Loss | 28293.0635 | 23223.7578 | 28899.8423
Projected MWh, After Line Loss 1 | Not avail | Not avail | Not avail
Production MWh Variance, From Projected | Not avail | Not avail | Not avail
YTD Generated kWh, After Line Loss | 28293063.54 | 51516821.3 | 80416663.6
YTD Generated MWh, After Line Loss | 28293.0635 | 51516.8213 | 80416.6636
Availability
Monthly Contractual Availability | 80.95% | 84.85% | 93.75%
YTD Contractual Availability | 80.95% | 82.9% | 86.52%
Projected Contractual Availability | Ramp Up | Ramp Up | Ramp Up
Notes:
1) Projections not provided to EWC. Therefore, no MWh Variance comparison is possible.
2) The January and March production are within 0.3% of the substation values assuming a 2% line loss. February is still being researched.