## Comparison
Turbine Comparison
2025-09-26 22:41 | [14 empty] | Initial Purchase
| Brownsville |  | Caledonia |  | New Albany |  | Calvert City |  | Wheatland |  | Wilton |  | Total GenCo |  | Analysis |  | Santee Cooper |  | UAE |  | Lincoln |  | Springfield |  | UAE |  | Rochester |  | Eastern KY. |  | Calpine |  | Austin |  | Michigan South Central |  | ElectriCities
Description:
Turbine Type | W 501 D5 |  | GE 7EA |  | GE 7B |  | WH 501F |  | W 501 D5A |  | GE 7EA |  | - |  | LM 6000 |  | LM 6000 |  | LM6000 |  | LM 6000 |  | LM 6000 |  | LM6000 |  | LM6000 |  | LM6000 |  | LM6000 |  | LM6000
No. of Turbines | 4 |  | 6 |  | 6 |  | 3 |  | 4 |  | 8 |  | 31 |  | 24 |  | 5 |  | 5 |  | 4 |  | 3 |  | 4 |  | 1 |  | 6 |  | 4 |  | 4
Gross Capacity @ ISO (MW) | 497.4 |  | 503.6 |  | 430.2 |  | 535.3 |  | 514.6 |  | 665.9 |  | 3147
Net Capacity @ ISO (MW) | 487.452 |  | 493.528 |  | 421.596 |  | 524.594 |  | 504.308 |  | 652.582 |  | 3084.06 |  | 0 |  | 0 |  |  |  | 0 |  | 0
Gross Capacity per Turbine @ 900 (MW) | [14 empty] | 48.5 |  | 46 |  | 47 |  | 48.5 |  | 46.1 |  | 47 |  | 47.5 |  | 47 |  | 47.5 |  | 44.75
Gross Capacity @ 900 (MW) | 458 |  | 442 |  | 367 |  | 510 |  | 470 |  | 608 |  | 2855 |  | 1164 |  | 230 |  | 235 |  | 194 |  | 138.3 |  | 188 |  | 47.5 |  | 282 |  | 190 |  | 179
Net Capacity @ 900 (MW) | 448.84 |  | 433.16 |  | 359.66 |  | 499.8 |  | 460.6 |  | 595.84 |  | 2797.9 | [9 empty] | 130.7
Heat Rate (HHV) | 11411 |  | 12064 |  | 12228 |  | 10904 |  | 11735 |  | 11973 |  | - |  | 9435 |  | 10915 |  | 10200 |  | 9332 |  | 10329 |  | 10200 |  | 10200 |  | 10300 |  | 10200 |  | 10400
Hard Cost: |  | % of Hard Cost |  | % of Hard Cost |  | % of Hard Cost |  | % of Hard Cost |  | % of Hard Cost |  | % of Hard Cost |  | % of Hard Cost |  | % of Hard Cost |  | % of Hard Cost |  | % of Hard Cost |  | % of Hard Cost |  | % of Hard Cost |  | % of Hard Cost |  | % of Hard Cost |  | % of Hard Cost |  | % of Hard Cost |  | % of Hard Cost |  | % of Hard Cost |  | % of Hard Cost
Turbines plus Fin Fans | 72614.406 | 61.44% | 101629.108 | 69.28% | 82754.59 | 59.56% | 93580 | 60.11% | 86219.301 | 58.61% | 142064.94 | 59.79% | 578865.4349 | 61.31% | 0 | 0% | 71300 | 64.75% | 71506 | 61.78% | 56048 | 57.41% | 43365 | 59.31% | 57290 | 57.18% | 14322 | 58.43% | 85608 | #DIV/0! | 56048 | 57.43% | 64800 | 69.86% |  | #DIV/0!
Transformer and Curcuit Breakers | 8885.247 | 7.518% | 10286.721 | 7.013% | 19228.133 | 13.84% | 5885.811 | 3.78% | 4440.534 | 3.019% | 5916.048 | 2.49% | 54642.8457 | 5.787% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% |  | 0% |  | 0% | 0 | 0% |  | #DIV/0!
BOP and Construction | 32943.416 | 27.87% | 29262.011 | 19.95% | 33531.644 | 24.13% | 30385.6 | 19.52% | 24230.498 | 16.47% | 46656.594 | 19.64% | 197010.8424 | 20.86% | 0 | 0% | 29280 | 26.59% | 27128 | 23.44% | 27189 | 27.85% | 20232.195 | 27.67% | 23128 | 23.08% | 6000 | 24.48% |  | 0% | 27189 | 27.86% | 18656 | 20.11% |  | #DIV/0!
Spare Parts | 1317.747 | 1.115% | 787.8 | 0.537% | 813.05 | 0.5851% | 1247.007 | 0.8009% | 1172.731 | 0.7972% | 1253.881 | 0.5277% | 6592.2544 | 0.6982% | 0 | 0% | 1543 | 1.401% | 1300 | 1.123% | 1320 | 1.352% | 0 | 0% | 1320 | 1.317% | 500 | 2.04% |  | 0% | 1300 | 1.332% |  | 0% |  | #DIV/0!
Gas Interconnection Costs | 0 | 0% | 981 | 0.6688% | 0 | 0% | 750 | 0.4817% | 1500 | 1.02% | 6500 | 2.736% | 9731.0217 | 1.031% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% |  | 0% | 0 | 0% |  | 0% |  | #DIV/0!
Electricity Interconnection Costs | 1972.489 | 1.669% | 3507.82 | 2.391% | 2150.807 | 1.548% | 2200 | 1.413% | 5000 | 3.399% | 1216.382 | 0.5119% | 16047.6022 | 1.7% | 0 | 0% | 1335 | 1.212% | 2000 | 1.728% | 2000 | 2.048% | 0 | 0% | 1135 | 1.133% | 935 | 3.815% |  | 0% | 1135 | 1.163% |  | 0% |  | #DIV/0!
Sales and Use Tax on Equipment | 225.949 | 0.1912% | 100 | 0.06817% | 100 | 0.07197% | 1750 | 1.124% | 50 | 0.03399% | 500 | 0.2104% | 2725.9639 | 0.2887% | 0 | 0% | 0 | 0% | 2044 | 1.766% | 0 | 0% | 0 | 0% | 2941 | 2.935% | 755 | 3.08% |  | 0% | 2352 | 2.41% |  | 0% |  | #DIV/0!
Mobilization Fuel | 228.051 | 0.193% | 136.036 | 0.09274% | 375.016 | 0.2699% | 1000 | 0.6423% | 1000 | 0.6798% | 1500 | 0.6313% | 4239.1218 | 0.4489% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% |  | 0% | 0 | 0% |  | 0% |  | #DIV/0!
Overhead & Fees - EECC | 0 | 0% | 0 | 0% | 0 | 0% | 929.8 | 0.5972% | 929.8 | 0.6321% | 940.2 | 0.3957% | 2799.8123 | 0.2965% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 989.78 | 1.354% | 0 | 0% | 0 | 0% |  | 0% | 0 | 0% |  | 0% |  | #DIV/0!
Overhead & Fees - NEPCO | 0 | 0% | 0 | 0% | 0 | 0% | 2840.7 | 1.825% | 2386.7 | 1.622% | 2824.8 | 1.189% | 8052.2345 | 0.8528% | 0 | 0% | 0 | 0% | 200 | 0.1728% | 0 | 0% | 3998.5915 | 5.469% | 200 | 0.1996% | 50 | 0.204% |  | 0% | 100 | 0.1025% | 3000 | 3.234% |  | #DIV/0!
Base Fee | 0 | 0% | 0 | 0% | 0 | 0% | 3066.7 | 1.97% | 3066.7 | 2.085% | 3066.7 | 1.291% | 9200.1405 | 0.9744% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% |  | 0% | 0 | 0% |  | 0% |  | #DIV/0!
Switchyard | 0 | 0% | 0 | 0% | 0 | 0% | 9230 | 5.928% | 8720.498 | 5.928% | 3355.857 | 1.412% | 21306.4736 | 2.256% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% |  | 0% | 0 | 0% |  | 0% |  | #DIV/0!
Union Adders/Others | 0 | 0% | 0 | 0% | 0 | 0% | 2125.8 | 1.365% | 6886 | 4.681% | 12328.422 | 5.189% | 21340.2825 | 2.26% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% |  | 0% | 0 | 0% |  | 0% |  | #DIV/0!
Sound Control | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 9479.08 | 3.989% | 9479.08 | 1.004% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% |  | 0% | 0 | 0% |  | 0% |  | #DIV/0!
Pipeline | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 400 | 0.3633% | 1500 | 1.296% | 5815 | 5.956% | 0 | 0% | 1500 | 1.497% | 0 | 0% |  | 0% | 0 | 0% |  | 0% |  | #DIV/0!
SCR | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 5000 | 4.32% | 0 | 0% | 0 | 0% | 8000 | 7.985% | 0 | 0% |  | 0% | 4800 | 4.918% | 4800 | 5.175% |  | #DIV/0!
Dual Fuel | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 720 | 0.9847% | 0 | 0% | 680 | 2.774% |  | 0% | 0 | 0% |  | 0% |  | #DIV/0!
Black Start | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% |  | 0% | 0 | 0% |  | 0% |  | #DIV/0!
Gas Compression | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 1000 | 0.864% | 1200 | 1.229% | 960 | 1.313% | 615 | 0.6138% | 268 | 1.093% |  | 0% | 615 | 0.6301% | 1500 | 1.617% |  | #DIV/0!
Demin Water Facility | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 1342 | 1.219% | 0 | 0% | 4061 | 4.159% | 0 | 0% | 0 | 0% | 0 | 0% |  | 0% | 0 | 0% |  | 0% |  | #DIV/0!
Chillers | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 4909 | 4.458% | 4061 | 3.509% | 0 | 0% | 2850 | 3.898% | 4061 | 4.053% | 1000 | 4.08% |  | 0% | 4061 | 4.161% |  | 0% |  | #DIV/0!
Water Interconnect | 0 | 0% | 0 | 0% | 0 | 0% | 700 | 0.4496% | 1500 | 1.02% | 0 | 0% | 2200.0147 | 0.233% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% |  | 0% | 0 | 0% |  | 0% |  | #DIV/0!
Total Hard Cost | 118187.305 | 100% | 146690.496 | 100% | 138953.24 | 100% | 155691.418 | 100% | 147102.762 | 100% | 237602.904 | 100% | 944233.125 | 100% | 508800 | 100% | 110109 | 100% | 115739 | 100% | 97633 | 100% | 73115.5665 | 100% | 100190 |  | 24510 |  | 85608 |  | 97600 |  | 92756 |  | 0
Soft Cost: |  | % of Soft Cost |  | % of Soft Cost |  | % of Soft Cost |  | % of Soft Cost |  | % of Soft Cost |  | % of Soft Cost |  | % of Soft Cost |  | % of Soft Cost |  | % of Soft Cost |  | % of Soft Cost |  | % of Soft Cost |  | % of Soft Cost |  | % of Soft Cost |  | % of Soft Cost |  | % of Soft Cost |  | % of Soft Cost |  | % of Soft Cost |  | % of Soft Cost
EE&CC Project Management | 734.722 | 8.26% | 785.954 | 11.44% | 1199.679 | 14.27% | 0 | 0% | 0 | 0% | 0 | 0% | 2720.6946 | 3.666% | 0 | 0% | 0 | 0% | 225 | 3.511% | 0 | 0% | 0 | #DIV/0! |  | #DIV/0! | 0 | 0% |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Mobilization of O&M | 698.29 | 7.851% | 568.579 | 8.274% | 786.609 | 9.355% | 908.786 | 5.082% | 908.786 | 6.516% | 908.786 | 4.992% | 4780.2068 | 6.441% | 0 | 0% | 2200 | 39.75% | 0 | 0% | 2174.325 | 45.28% | 0 | #DIV/0! |  | #DIV/0! | 0 | 0% |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Environmental Permitting | 865.37 | 9.729% | 237.353 | 3.454% | 354.903 | 4.221% | 378.549 | 2.117% | 313.82 | 2.25% | 349.955 | 1.922% | 2500.1677 | 3.369% | 0 | 0% | 0 | 0% | 1000 | 15.61% | 0 | 0% | 0 | #DIV/0! |  | #DIV/0! | 0 | 0% |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Insurance During Construction | 164.348 | 1.848% | 224.923 | 3.273% | 326.527 | 3.883% | 200 | 1.119% | 200 | 1.434% | 266.249 | 1.463% | 1382.1626 | 1.862% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | #DIV/0! |  | #DIV/0! | 0 | 0% |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Capitalized Salaries | 35.06 | 0.3942% | 53.204 | 0.7742% | 63.624 | 0.7566% | 178.016 | 0.9956% | 185.198 | 1.328% | 177.396 | 0.9744% | 692.5405 | 0.9332% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | #DIV/0! |  | #DIV/0! | 0 | 0% |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Resale Handling Fee | 69.936 | 0.7863% | 94.021 | 1.368% | 62.709 | 0.7457% | 256 | 1.432% | 0 | 0% | 0 | 0% | 482.7093 | 0.6504% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | #DIV/0! |  | #DIV/0! | 0 | 0% |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Owner's Engineer | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 1000 | 11.24% | 0 | #DIV/0! |  | #DIV/0! | 500 | 30.6% |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Land Acquisition | 461.44 | 5.188% | 557.693 | 8.115% | 172.609 | 2.053% | 453.841 | 2.538% | 1117.944 | 8.016% | 2305.818 | 12.67% | 5069.6041 | 6.831% | 0 | 0% | 100 | 1.807% | 1000 | 15.61% | 461 | 9.6% | 0 | #DIV/0! |  | #DIV/0! | 0 | 0% |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Development Expenses | 555.315 | 6.243% | 741.639 | 10.79% | 638.182 | 7.589% | 388.508 | 2.173% | 604.559 | 4.335% | 508.303 | 2.792% | 3436.8173 | 4.631% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | #DIV/0! |  | #DIV/0! | 0 | 0% |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Legal Expense | 1018.627 | 11.45% | 834 | 12.14% | 791 | 9.407% | 381.3 | 2.132% | 652.208 | 4.677% | 498.96 | 2.741% | 4176.493 | 5.628% | 0 | 0% | 500 | 9.033% | 150 | 2.341% | 150 | 3.123% | 0 | #DIV/0! |  | #DIV/0! | 0 | 0% |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Total Expensed Costs | 0 | 0% | 0 | 0% | 0 | 0% | 259.081 | 1.449% | 232.288 | 1.666% | 0 | 0% | 491.4001 | 0.6621% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | #DIV/0! |  | #DIV/0! | 0 | 0% |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
O&M Fee | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 200 | 2.249% | 0 | #DIV/0! |  | #DIV/0! | 0 | 0% |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Contingency: | 0 | 0% | 0 | 0% | 0 | 0% | 2981.791 | 16.68% | 0 | 0% | 0 | 0% | 2981.9578 | 4.018% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | #DIV/0! |  | #DIV/0! | 0 | 0% |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
IDC | 4291.62 | 48.25% | 2774.909 | 40.38% | 4013.026 | 47.72% | 11170.136 | 62.47% | 9716.579 | 69.67% | 12612.985 | 69.28% | 44581.9399 | 60.07% | 0 | 0% | 2735 | 49.41% | 4033 | 62.94% | 817 | 17.01% | 0 | #DIV/0! |  | #DIV/0! | 1134 | 69.4% |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
City Expenses | 0 | 0% | 0 | 0% | 0 | 0% | 325 | 1.818% | 15.1 | 0.1083% | 576.426 | 3.166% | 916.5453 | 1.235% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | #DIV/0! | 0 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Total Soft Cost | 8894.728 | 100% | 6872.275 | 100% | 8408.868 | 100% | 17881.008 | 100% | 13946.482 | 100% | 18204.878 | 100% | 74213.239 | 100% | 29673 | 100% | 5535 | 100% | 6408 | 100% | 4802.325 | 88.5% | 0 | #DIV/0! | 0 | #DIV/0! | 1634 | 100% | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0!
Financing Cost: |  | % of Fin.Cost |  | % of Fin.Cost |  | % of Fin.Cost |  | % of Fin.Cost |  | % of Fin.Cost |  | % of Fin.Cost |  | % of Fin.Cost |  | % of Fin.Cost |  | % of Fin.Cost |  | % of Fin.Cost |  | % of Fin.Cost |  | % of Fin.Cost |  | % of Fin.Cost |  | % of Fin.Cost |  | % of Fin.Cost |  | % of Fin.Cost |  | % of Fin.Cost |  | % of Fin.Cost
Lender's Engineer | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Lender's Counsel | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Debt Reserve |  | 0% |  | 0% |  | 0% |  | 0% |  | 0% |  | 0% |  | 0% | 0 | 0% | 4000 | 90.91% | 0 | 0% | 9394 | 86.23% |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Financing Fee | 1062 | 100% | 1243 | 100% | 1112 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 3420 | 100% | 0 | 0% | 400 | 9.091% | 1000 | 100% | 1500 | 13.77% | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Total Financing Cost | 1062 | 100% | 1243 | 100% | 1112 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 3420 | 100% | 0 | 0% | 4400 | 100% | 1000 | 100% | 10894 | 100% | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0!
Total Uses of Funds | 128144.033 |  | 154805.771 |  | 148474.108 |  | 173572.426 |  | 161049.244 |  | 255807.782 |  | 1021866.364 |  | 538473 |  | 120044 |  | 123147 |  | 113329.325 |  | 73115.5665 |  | 100190 |  | 26144 |  | 85608 |  | 97600 |  | 92756 |  | 0
Operating Expenses |  | % of Op. Exp |  | % of Op. Exp |  | % of Op. Exp |  | % of Op. Exp |  | % of Op. Exp |  | % of Op. Exp |  | % of Op. Exp |  | % of Op. Exp |  | % of Op. Exp |  | % of Op. Exp |  | % of Op. Exp |  | % of Op. Exp |  | % of Op. Exp |  | % of Op. Exp |  | % of Op. Exp |  | % of Op. Exp |  | % of Op. Exp |  | % of Op. Exp
Variable Operating Cost (per year) | 774.248 | 14.18% | 446.6 | 10.89% | 428.9978 | 8.991% | 744.673 | 13.91% | 656.2 | 13.13% | 629.48 | 12.27% | 623.5958 | 12.48% | 0 | 0% | 105 | 4.711% | 153.2 | 12.16% | 269.651 | 17.77% | 115.6098 | 11.29% | 153.2 | 12.16% | 60.6 | 8.97% |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
$/MWh | 1.4087 |  | 0.84201 |  | 1.0945 |  | 1.2168 |  | 1.1635 |  | 0.86277 |  | 1.0897 |  | 2.05 |  | 0.32 |  | 0.58 |  | 1.61 |  | 0.5 |  | 0.58 |  | 1.03
Major Maintenance & Accrual (per year) | 1973.16 | 36.14% | 1349.28 | 32.9% | 1349.28 | 28.28% | 2296.44 | 42.91% | 2078.4 | 41.57% | 1799.04 | 35.07% | 1834.369 | 36.72% | 0 | 0% | 398 | 17.86% | 576.9 | 45.78% | 0 | 0% | 358.3902 | 35% | 576.9 | 45.78% | 131 | 19.39% |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
$/MWh | 3.5902 |  | 2.5439 |  | 3.0638 |  | 3.7524 |  | 3.6851 |  | 2.4658 |  | 0.53543 |  | 0 |  | 1.26 |  | 1.64 |  |  |  | 1.55 |  | 1.64 |  | 1.99
Total VOM | 2747.408 | 50.32% | 1795.88 | 43.8% | 1778.2778 | 37.27% | 3041.113 | 56.82% | 2734.6 | 54.7% | 2428.52 | 47.34% | 2457.9648 | 49.2% | 0 | 0% | 503 | 22.57% | 730 | 100% | 269.651 | 17.77% | 474 | 46.29% | 730 | 100% | 192 | 100% |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
$/MWh | 4.9989 |  | 3.3859 |  | 4.1583 |  | 4.9691 |  | 4.8486 |  | 3.3286 |  | 1.6251 |  | 2.05 |  | 1.58 |  |  |  | 1.61 |  | 2.05 |  | 2.22 |  | 3.02 |  |  | 0 |  | 0 |  | 0 |  | 0
Fixed Operating Cost (per year) | 1469.3872 | 26.91% | 1054.3912 | 25.71% | 1707.5223 | 35.79% | 1423.4706 | 26.6% | 1577.6298 | 31.56% | 1457.3806 | 28.41% | 1442.8106 | 28.88% | 6565 | 100% | 1017 | 45.63% | 530 | 42.06% | 404 | 26.62% | 550 | 53.71% | 530 | 42.06% | 484 | 71.64% |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
$/kW-yr | 3.2083 |  | 2.3855 |  | 4.6526 |  | 2.7911 |  | 3.3567 |  | 2.397 |  | 3.0437 |  | 5.64 |  | 4.56 |  |  |  | 2.08 |  | 4.2
Other Fixed Expenses (per year) | 1242.778 | 22.76% | 1250.2744 | 30.49% | 1285.7435 | 26.95% | 887.5061 | 16.58% | 687 | 13.74% | 1244.4614 | 24.26% | 1094.8624 | 21.92% | 0 | 0% | 709 | 31.81% |  | 0% | 844 | 55.61% | 0 | 0% | 0 | 0% |  | 0% |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
$/kW-yr | 2.7135 |  | 2.8287 |  | 3.5034 |  | 1.7402 |  | 1.4617 |  | 2.0468 |  | 2.311 |  | 0 |  | 3.0826 |  |  |  | 4.35 |  | 0
Total Fixed Cost (per year) | 2712.1652 | 49.68% | 2304.6656 | 56.2% | 2993.2658 | 62.73% | 2310.9767 | 43.18% | 2264.6298 | 45.3% | 2701.8421 | 52.66% | 2537.673 | 50.8% | 6565 | 100% | 1726 | 77.43% |  | 0% | 1248 | 82.23% | 550 | 53.71% |  | 0% |  | 0% |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
$/kW-yr | 5.9218 |  | 5.2142 |  | 8.156 |  | 4.5313 |  | 4.8184 |  | 4.4438 |  | 5.3547 |  | 5.64 |  | 7.6426 |  |  |  | 6.43 |  | 4.2
Total Expenses (per year) | 5459.5732 | 100% | 4100.5456 | 100% | 4771.5436 | 100% | 5352.0897 | 100% | 4999.2298 | 100% | 5130.3621 | 100% | 4995.6378 | 100% | 6565 | 100% | 2229 | 100% | 730 | 100% | 1517.651 | 100% | 1024 | 100% | 730 | 100% | 192 | 100% | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0!
Summary ($/kW) |  | % of All-in-Cost |  | % of All-in-Cost |  | % of All-in-Cost |  | % of All-in-Cost |  | % of All-in-Cost |  | % of All-in-Cost |  | % of All-in-Cost |  | % of All-in-Cost |  | % of All-in-Cost |  | % of All-in-Cost |  | % of All-in-Cost |  | % of All-in-Cost |  | % of All-in-Cost |  | % of All-in-Cost |  | % of All-in-Cost |  | % of All-in-Cost |  | % of All-in-Cost |  | % of All-in-Cost
Turbine Cost | 158.5467 | 56.67% | 229.9301 | 65.65% | 225.4893 | 55.74% | 183.4902 | 53.91% | 183.4453 | 53.54% | 233.6594 | 55.54% | 202.7539 | 56.65% | 0 | 0% | 310 | 59.39% | 304.2809 | 58.07% | 288.9072 | 49.46% | 313.5575 | 59.31% | 304.734 | 57.18% | 301.5158 | 54.78% |  |  | 294.9895 | 57.43% | 362.0112 | 69.86% |  | #DIV/0!
EPC Cost | 99.5041 | 35.56% | 101.9488 | 29.11% | 153.1298 | 37.85% | 121.7871 | 35.78% | 129.5393 | 37.8% | 157.1348 | 37.35% | 127.974 | 35.75% | 437.1134 | 94.49% | 168.7348 | 32.33% | 188.2255 | 35.92% | 214.3557 | 36.69% | 215.1162 | 40.69% | 228.1915 | 42.82% | 214.4842 | 38.97% |  |  | 218.6947 | 42.57% | 156.1788 | 30.14% |  | #DIV/0!
Soft Cost | 19.4208 | 6.941% | 15.5481 | 4.439% | 22.9124 | 5.664% | 35.0608 | 10.3% | 29.6734 | 8.66% | 29.9422 | 7.117% | 25.9941 | 7.263% | 25.4923 | 5.511% | 24.0652 | 4.611% | 27.2681 | 5.204% | 24.7543 | 4.237% | 0 | 0% | 0 | 0% | 34.4 | 6.25% |  |  | 0 | 0% | 0 | 0% |  | #DIV/0!
Financing Cost | 2.3188 | 0.8288% | 2.8122 | 0.8029% | 3.03 | 0.749% | 0 | 0% | 0 | 0% | 0 | 0% | 1.1979 | 0.3347% | 0 | 0% | 19.1304 | 3.665% | 4.2553 | 0.812% | 56.1546 | 9.613% | 0 | 0% | 0 | 0% | 0 | 0% |  |  | 0 | 0% | 0 | 0% |  | #DIV/0!
All-in-Capital Cost | 279.7905 | 100% | 350.2393 | 100% | 404.5616 | 100% | 340.3381 | 100% | 342.658 | 100% | 420.7365 | 100% | 357.9199 | 100% | 462.6057 | 100% | 521.9304 | 100% | 524.0298 | 100% | 584.1718 | 100% | 528.6737 | 100% | 532.9255 | 100% | 550.4 | 100% |  |  | 513.6842 | 100% | 518.1899 | 100% | 0 | #DIV/0!
Term (Yrs.) | [24 empty] | 5/01 to 8/04 |  |  |  | 5/01 to 9/04 |  |  |  | 5/01 to 11/03
Avg. Pricing Received from the Desk | [24 empty] | 4.2 |  |  |  | 5.4 |  | 3.99 |  | 3 |  | 4.75
Note on AA93: Ben Rogers: Based on a 4 year average in Nypool at the UAE site