## Readme
Average Weighted Shift Factor Calculation
Exceptions implemented:
1 | Bosque Generation set to North2001 zone
2 | LCRA loads set to South2001 zone
3 | Self serve loads (TXU and Reliant/HLP) final values were calculated in the "SelfServeLoads" sheet.
- Effective Pl were entered as Pl in the "2CSC3ZONES_01sum1" sheet.
- Effective Pgen were entered as Pmax in the "2CSC3ZONES_01sum1" sheet.
|  |  | SUM{[Load(j) + GenOff(j) + Pmax(j)]*SHF1(j)} | j= bus number
|  | Average Weighted Shift Factor 1= | ----------------------------------------------------------------
SUM(Load + GenOff + Pmax)
|  |  | SUM{[Load(j) + GenOff(j) + Pmax(j)]*SHF2(j)} | j= bus number
|  | Average Weighted Shift Factor 2= | ----------------------------------------------------------------
SUM(Load + GenOff + Pmax)

## Average Weighted Shift Factors
To be loaded into ERCOT Congestion Management System
CM Zone Name | Total Number of Load Flow Buses | Number of Load Buses | Load Total MW | Number of Offline Generation Buses | Offline Generation Total Pmax MW | Number of Online Generation Buses | Online Generation Total Pmax MW | Summation of Individual Weighted Shift Factors for CSC #1 | Summation of Individual Weighted Shift Factors for CSC #2 | Average Weighted Shift Factor on Commercially Significant Constraint #1 - 1430 GRAHAM 345kV to 1436 PARKER 345kV ckt 1 | Average Weighted Shift Factor on Commercially Significant Constraint #2 - 46020 LIMESTONE 345 kV to 2428 WATERMILL 345 kV ckt1
South2001 | 2356 | 1419 | 33569.639 | 66 | 6331.7 | 226 | 40400.93 | 349.9973 | -1330.2593 | 0.0043585 | -0.016566
West2001 | 956 | 539 | 3729.443 | 22 | 1715 | 41 | 5323 | 2938.6536 | -1193.8383 | 0.27292 | -0.11087
North2001 | 1685 | 957 | 20692.081 | 19 | 1982 | 83 | 20009 | -552.1172 | -5320.7683 | -0.012935 | -0.12466
ERCOT | 4997 | 2915 | 57991.163 | 107 | 10028.7 | 350 | 65732.93
| Number of | Load Total |  | Gen Offline Total |  | Gen Online Total |  | Totals |  | Averaged Weigthed Shift Factor
Name | Buses | count | MW | count | Pmax | count | Pmax | Pinj*SHF1 | Pinj*SHF2 | awSF1 | awSF2
South2001 | 2356 | 1419 | 33569.639 | 66 | 6331.7 | 226 | 40400.93 | 349.9973 | -1330.2593 | 0.0043585 | -0.016566
West2001 | 956 | 539 | 3729.443 | 22 | 1715 | 41 | 5323 | 2938.6536 | -1193.8383 | 0.27292 | -0.11087
North2001 | 1685 | 957 | 20692.081 | 19 | 1982 | 83 | 20009 | -552.1172 | -5320.7683 | -0.012935 | -0.12466
ERCOT | 4997 | 2915 | 57991.163 | 107 | 10028.7 | 350 | 65732.93

## 2CSC3ZONES 01SUM1 BASE CASE
Corresponding ESCA Network Model Name | Corresponding Siemens Network Model Name | Load Flow Base Case Bus Number | Load Flow Base Case Bus Name | On Peak Load Flow Base Case Load MW | Load Flow Base Case Off Line Generation Pmax MW | Load Flow Base Case On Line Generation Pgen MW | Load Flow Base Case On Line Generation Pmax MW | Congestion Management Zone Location | County Location of Load Flow Bus | Individual Shift Factor on Commercially Significant Constraint #1 - 1430 GRAHAM 345kV to 1436 PARKER 345kV ckt 1 | Individual Shift Factor on Commercially Significant Constraint #2 - 46020 LIMESTONE 345 kV to 2428 WATERMILL 345 kV ckt1 | Individual Weighted Shift Factor on Commercially Significant Constraint #1 - 1430 GRAHAM 345kV to 1436 PARKER 345kV ckt 1 | Individual Weighted Shift Factor on Commercially Significant Constraint #2 - 46020 LIMESTONE 345 kV to 2428 WATERMILL 345 kV ckt1 | Self Serve Load | kV
RPR | RPR | 1 | ROANSPRA | 8.69 |  |  |  | SOUTH2001 | GRIMES | -0.0041328 | 0.015547 | -0.035914 | 0.13511 |  | 138
IOLA | IOLA | 4 | IOLA |  |  |  |  | SOUTH2001 | GRIMES | -0.0041053 | 0.013754 | 0 | 0 |  | 138
IOLA | IOLA | 5 | IOLA |  |  |  |  | SOUTH2001 | GRIMES | -0.0040238 | 0.0084358 | 0 | 0 |  | 69
BED | BED | 9 | BEDIAS | 5.59 |  |  |  | SOUTH2001 | GRIMES | -0.0040515 | 0.0048282 | -0.022648 | 0.026989 |  | 69
KEI | KEI | 13 | KEITH | 4.96 |  |  |  | SOUTH2001 | GRIMES | -0.0039243 | 0.0076914 | -0.019464 | 0.038149 |  | 69
CARLOSSW | CARLOSSW | 17 | CARLOSSW |  |  |  |  | SOUTH2001 | GRIMES | -0.0038646 | 0.0072452 | 0 | 0 |  | 69
CAR | CAR | 21 | CARLOS | 1.41 |  |  |  | SOUTH2001 | GRIMES | -0.0038646 | 0.0072452 | -0.0054491 | 0.010216 |  | 69
NZL | NZL | 25 | NTHZULCH | 4.15 |  |  |  | SOUTH2001 | MADISON | -0.0040959 | -0.00095406 | -0.016998 | -0.0039594 |  | 69
BVL | BVL | 29 | BOONVIL |  |  |  |  | SOUTH2001 | BRAZOS | -0.003707 | 0.0060663 | 0 | 0 |  | 69
HEARNCTY | HEARNCTY | 31 | HEARNCTY |  |  |  |  | SOUTH2001 | ROBERTSON | -0.0031723 | -0.012669 | 0 | 0 |  | 69
RBS | RBS | 32 | ROBERTSN |  |  |  |  | SOUTH2001 | ROBERTSON | -0.0024833 | -0.01109 | 0 | 0 |  | 138
WATSONCP | WATSONCP | 33 | WATSONCP |  |  |  |  | SOUTH2001 | LEON | -0.0045431 | -0.0076675 | 0 | 0 |  | 138
PHILLIPS | PHILLIPS | 34 | PHILLIPS | 2.82 |  |  |  | SOUTH2001 | ROBERTSON | -0.0024833 | -0.01109 | -0.007003 | -0.031275 |  | 138
HRN | HRN | 35 | HEARNE |  |  |  |  | SOUTH2001 | ROBERTSON | -0.0027166 | -0.0081381 | 0 | 0 |  | 138
HRN | HRN | 36 | HEARNE |  |  |  |  | SOUTH2001 | ROBERTSON | -0.0030785 | -0.015959 | 0 | 0 |  | 69
SUT | SUT | 38 | SUTTON | 3.63 |  |  |  | SOUTH2001 | ROBERTSON | -0.0033442 | -0.0066469 | -0.012139 | -0.024128 |  | 69
|  | 40 | JEWETT |  |  |  |  | SOUTH2001 | LEON | -0.0066607 | -0.0039974 | 0 | 0 |  | 138
HLTPLKSW | HLTPLKSW | 43 | HLTPLKSW |  |  |  |  | SOUTH2001 | ROBERTSON | -0.003687 | -0.020247 | 0 | 0 |  | 69
OLE | OLE | 45 | OLETHA | 3.8 |  |  |  | SOUTH2001 | LIMESTONE | -0.0054536 | -0.021292 | -0.020724 | -0.080909 |  | 138
FARRAR | FARRAR | 46 | FARRAR | 3.34 |  |  |  | SOUTH2001 | LEON | -0.0060246 | -0.013111 | -0.020122 | -0.043791 |  | 138
HLTPLKSW | HLTPLKSW | 47 | HLTOPLKS |  |  |  |  | SOUTH2001 | LEON | -0.004512 | -0.0077474 | 0 | 0 |  | 138
HLTPLKSW | HLTPLKSW | 48 | HLTOPLKS | 7.83 |  |  |  | SOUTH2001 | LEON | -0.0041551 | -0.0086654 | -0.032534 | -0.06785 |  | 69
SMG | SMG | 52 | SANMIGEL |  |  |  |  | SOUTH2001 | ATASCOSA | 0.012434 | -0.031231 | 0 | 0 |  | 345
ELT | ELT | 53 | ELLIOTT | 2.99 |  |  |  | SOUTH2001 | NAVARRO | -0.0033229 | -0.017681 | -0.0099354 | -0.052867 |  | 69
FRA | FRA | 57 | FRANKLIN | 8.47 |  |  |  | SOUTH2001 | LEON | -0.0036605 | -0.020061 | -0.031005 | -0.16991 |  | 69
BRANCHVL | BRANCHVL | 61 | BRANCHVL | 1.97 |  |  |  | SOUTH2001 | MILAM | -0.0025923 | -0.024544 | -0.0051069 | -0.048351 |  | 69
MILANO | MILANO | 64 | MILANO | 2.56 |  |  |  | SOUTH2001 | MILAM | 0.00053458 | -0.026988 | 0.0013685 | -0.069089 |  | 138
SVC | SVC | 65 | SILVRCTY | 2.04 |  |  |  | SOUTH2001 | MILAM | -0.0020884 | -0.033443 | -0.0042604 | -0.068224 |  | 69
BARCLAY | BARCLAY | 69 | BARCLAY | 5.24 |  |  |  | SOUTH2001 | FALLS | -0.00064946 | -0.042197 | -0.0034031 | -0.22111 |  | 69
CALVRTSW | CALVRTSW | 73 | CALVRTSW |  |  |  |  | SOUTH2001 | MILAM | -0.0023434 | -0.0363 | 0 | 0 |  | 69
PETTIBON | PETTIBON | 75 | PETTIBON | 0.22 |  |  |  | SOUTH2001 | MILAM | 0.0010379 | -0.038323 | 0.00022834 | -0.0084311 |  | 69
CALVERT | CALVERT | 77 | CALVERT | 1.31 |  |  |  | SOUTH2001 | MILAM | -0.0023434 | -0.0363 | -0.0030698 | -0.047552 |  | 69
PLSNTGRV | PLSNTGRV | 81 | PLSNTGRV | 2.45 |  |  |  | SOUTH2001 | FALLS | -0.0026214 | -0.039414 | -0.0064224 | -0.096565 |  | 69
KOSSESW | KOSSESW | 85 | KOSSESW |  |  |  |  | SOUTH2001 | LIMESTONE | -0.0040193 | -0.036577 | 0 | 0 |  | 69
BGS | BGS | 86 | BEARGRAS | 15.15 |  |  |  | SOUTH2001 | LEON | -0.0063774 | -0.0080565 | -0.096617 | -0.12206 |  | 138
KOSSE | KOSSE | 89 | KOSSE | 2.5 |  |  |  | SOUTH2001 | LIMESTONE | -0.0040193 | -0.036577 | -0.010048 | -0.091442 |  | 69
PRY | PRY | 91 | PERRY |  |  |  |  | SOUTH2001 | FALLS | -0.0032662 | -0.052582 | 0 | 0 |  | 138
PRY | PRY | 92 | PERRY | 3.08 |  |  |  | SOUTH2001 | FALLS | -0.0034905 | -0.04915 | -0.010751 | -0.15138 |  | 69
PETEWAY | PETEWAY | 93 | PETEWAY | 1.8 |  |  |  | SOUTH2001 | ROBERTSON | -0.0038366 | -0.027599 | -0.0069059 | -0.049679 |  | 69
HAL | HAL | 95 | HALSBURG | 3.85 |  |  |  | SOUTH2001 | MCLENNAN | -0.003189 | -0.055236 | -0.012278 | -0.21266 |  | 138
BHR | BHR | 99 | BENHUR | 2.17 |  |  |  | SOUTH2001 | LIMESTONE | -0.0042629 | -0.048547 | -0.0092504 | -0.10535 |  | 69
GRO | GRO | 103 | GROESBEK | 2.96 |  |  |  | SOUTH2001 | LIMESTONE | -0.0042629 | -0.048547 | -0.012618 | -0.1437 |  | 69
BUT | BUT | 104 | BUTLER | 4.18 |  |  |  | SOUTH2001 | FREESTONE | -0.0087338 | -0.047859 | -0.036507 | -0.20005 |  | 138
PRA | PRA | 107 | PRARIEHL | 3.77 |  |  |  | SOUTH2001 | LIMESTONE | -0.0051507 | -0.058387 | -0.019418 | -0.22012 |  | 69
BUCKHLTS | BUCKHLTS | 110 | BUCKHLTS | 3.76 |  |  |  | SOUTH2001 | MILAM | -0.0020884 | -0.033443 | -0.0078524 | -0.12575 |  | 69
BARTLTSW | BARTLTSW | 114 | BARTLTSW |  |  |  |  | SOUTH2001 | BELL | 0.0033443 | -0.047313 | 0 | 0 |  | 69
DINGDONG | DINGDONG | 115 | DINGDONG | 6.89 |  |  |  | SOUTH2001 | BELL | -0.00038689 | -0.051124 | -0.0026657 | -0.35225 |  | 138
SALTY11 | SALTY11 | 116 | SALTY | 3.09 |  |  |  | SOUTH2001 | MILAM | 0.0038543 | -0.039784 | 0.01191 | -0.12293 |  | 138
BARTLETT | BARTLETT | 118 | BARTLETT | 5.03 |  |  |  | SOUTH2001 | BELL | 0.0033443 | -0.047313 | 0.016822 | -0.23799 |  | 69
TLB | TLB | 120 | TALBTRDG | 5.19 |  |  |  | SOUTH2001 | MILAM | 0.001958 | -0.034106 | 0.010162 | -0.17701 |  | 138
SCHWRTNR | SCHWRTNR | 122 | SCHWRTNR | 3.22 |  |  |  | SOUTH2001 | WILLIAMSON | 0.0038842 | -0.046156 | 0.012507 | -0.14862 |  | 69
JARREL | JARREL | 123 | JARREL |  |  |  |  | SOUTH2001 | WILLIAMSON | 0.0043071 | -0.04525 | 0 | 0 |  | 69
TLV | TLV | 124 | TAYLRSVY |  |  |  |  | SOUTH2001 | BELL | 0.0017282 | -0.050776 | 0 | 0 |  | 69
STILHOUS | STILHOUS | 125 | STILHOSE | 0.02 |  |  |  | SOUTH2001 | BELL | 0.0026199 | -0.046082 | 5.2399e-05 | -0.00092163 |  | 138
PGE | PGE | 126 | POAGE |  |  |  |  | SOUTH2001 | BELL | 0.001468 | -0.051337 | 0 | 0 |  | 69
THRNDLNT | THRNDLNT | 127 | THRNDLNT | 0.23 |  |  |  | SOUTH2001 | MILAM | 0.0044921 | -0.039519 | 0.0010332 | -0.0090893 |  | 138
SEA | SEA | 130 | SEATON |  |  |  |  | SOUTH2001 | BELL | -3.2848e-05 | -0.049779 | 0 | 0 |  | 138
SEA | SEA | 131 | SEATON |  |  |  |  | SOUTH2001 | BELL | 0.00021578 | -0.047461 | 0 | 0 |  | 69
TRIMMIER | TRIMMIER | 136 | TRIMMIER | 3.75 |  |  |  | SOUTH2001 | BELL | -0.00038689 | -0.051124 | -0.0014509 | -0.19172 |  | 138
MOODY | MOODY | 137 | MOODY |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0007133 | -0.058703 | 0 | 0 |  | 138
BTN | BTN | 139 | BELTNBEC |  |  |  |  | SOUTH2001 | BELL | -0.0004494 | -0.053661 | 0 | 0 |  | 138
MOFFAT | MOFFAT | 141 | MOFFAT | 7.74 |  |  |  | SOUTH2001 | BELL | -0.000598 | -0.0565 | -0.0046285 | -0.43731 |  | 138
TUGSW | TUGSW | 142 | TUGSW |  |  |  |  | SOUTH2001 | CORYELL | 0.0018111 | -0.065723 | 0 | 0 |  | 69
|  | 144 | HARHHGTS | 5.51 |  |  |  | SOUTH2001 | CORYEL | -0.00037562 | -0.051321 | -0.0020697 | -0.28278 |  | 138
LEONJNCT | LEONJNCT | 145 | LEONJNCT | 4.58 |  |  |  | SOUTH2001 | CORYELL | 0.0017693 | -0.063974 | 0.0081036 | -0.293 |  | 69
SPV | SPV | 146 | SPRINGVL | 8.29 |  |  |  | SOUTH2001 | MCLENNAN | -0.0018377 | -0.053415 | -0.015234 | -0.44281 |  | 138
SANTFESW | SANTFESW | 149 | SANTFESW |  |  |  |  | SOUTH2001 | CORYELL | 0.0018202 | -0.066107 | 0 | 0 |  | 69
SANTAFE | SANTAFE | 153 | SANTAFE | 0.98 |  |  |  | SOUTH2001 | CORYELL | 0.0018202 | -0.066107 | 0.0017838 | -0.064785 |  | 69
GATESVIL | GATESVIL | 157 | GATESVIL | 7.55 |  |  |  | SOUTH2001 | CORYELL | 0.0019634 | -0.072112 | 0.014824 | -0.54445 |  | 69
MCGREGOR | MCGREGOR | 161 | MCGREGOR | 5.18 |  |  |  | SOUTH2001 | MCLENNAN | -0.00093243 | -0.062889 | -0.00483 | -0.32576 |  | 138
WINDSRSW | WINDSRSW | 165 | WINDSRSW |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0010082 | -0.064337 | 0 | 0 |  | 138
WINDSOR | WINDSOR | 169 | WINDSOR | 7.37 |  |  |  | SOUTH2001 | MCLENNAN | -0.0010082 | -0.064337 | -0.0074308 | -0.47416 |  | 138
CRAWFORD | CRAWFORD | 173 | CRAWFORD | 8.07 |  |  |  | SOUTH2001 | MCLENNAN | -0.0010576 | -0.06528 | -0.0085349 | -0.52681 |  | 138
CHINASPR | CHINASPR | 175 | CHINASPR | 3.36 |  |  |  | SOUTH2001 | MCLENNAN | -0.0012429 | -0.06882 | -0.0041763 | -0.23124 |  | 138
BOSQUE | BOSQUE | 177 | BOSQUE | 5.82 |  |  |  | SOUTH2001 | MCLENNAN | -0.0012429 | -0.06882 | -0.007234 | -0.40053 |  | 138
CAYOTE | CAYOTE | 181 | CAYOTE | 1.79 |  |  |  | SOUTH2001 | BOSQUE | -0.0014091 | -0.071993 | -0.0025222 | -0.12887 |  | 138
MIDWAY | MIDWAY | 185 | MIDWAY | 3.29 |  |  |  | SOUTH2001 | FALLS | -0.0030568 | -0.044292 | -0.010057 | -0.14572 |  | 69
FRE | FRE | 195 | FREESTON | 4.96 |  |  |  | SOUTH2001 | FREESTONE | -0.006661 | -0.004004 | -0.033038 | -0.01986 |  | 69
|  | 197 | OAKGROV | 0.4 |  |  |  | SOUTH2001 | FREESTONE | -0.0066607 | -0.0039974 | -0.0026643 | -0.001599 |  | 138
SIMSBORO | SIMSBORO | 207 | SIMSBORO | 1.7 |  |  |  | SOUTH2001 | FREESTONE | -0.006661 | -0.004004 | -0.011324 | -0.0068069 |  | 69
COTTONWD | COTTONWD | 230 | CTNWD | 2.04 |  |  |  | SOUTH2001 | MCLENNAN | -0.004352 | -0.07057 | -0.0088781 | -0.14396 |  | 69.6
|  | 240 | WHITNEY |  |  |  |  | SOUTH2001 | BOSQUE | -0.0030319 | -0.06581 | 0 | 0 |  | 345
BOSQUESW | BOSQUESW | 246 | BOSQUESW |  |  |  |  | SOUTH2001 | BOSQUE | -0.0030892 | -0.065528 | 0 | 0 |  | 345
RGH | RGH | 249 | ROGERSHL | 15.48 |  |  |  | SOUTH2001 | MCLENNAN | -0.0026296 | -0.064929 | -0.040706 | -1.0051 |  | 138
FRTGTSSW | FRTGTSSW | 250 | FRTGTSSW |  |  |  |  | SOUTH2001 | CORYELL | 0.0018694 | -0.068171 | 0 | 0 |  | 69
FRTGATES | FRTGATES | 254 | FRTGATES | 5.45 |  |  |  | SOUTH2001 | CORYELL | 0.0018694 | -0.068171 | 0.010188 | -0.37153 |  | 69
TAM | TAM | 798 | TAMUGEN1 |  |  | 28 | 32 | SOUTH2001 | BRAZOS | -0.0035855 | 0.0060613 | -0.11474 | 0.19396 |  | 12
TAMUSW | TAMUSW | 799 | TEXASAM | 60.65 |  |  |  | SOUTH2001 | BRAZOS | -0.0035855 | 0.0060613 | -0.21746 | 0.36762 |  | 138
MCCREE | MCCREE | 833 | MCCREE B |  |  |  |  | SOUTH2001 | DALLAS | 0 | 0 | 0 | 0 |  | 345
TAMUSW | TAMUSW | 860 | TAMUSW |  |  |  |  | SOUTH2001 | BRAZOS | -0.0035855 | 0.0060613 | 0 | 0 |  | 138
ATKINS | ATKINS | 862 | ATKIN138 |  |  |  |  | SOUTH2001 | BRAZOS | -0.0035915 | 0.006136 | 0 | 0 |  | 138
ATKINS | ATKINS | 864 | ATKINS69 |  |  |  |  | SOUTH2001 | BRAZOS | -0.0036837 | 0.0072821 | 0 | 0 |  | 69
SNOOK | SNOOK | 865 | SNOOK | 4.803 |  |  |  | SOUTH2001 | BURLESON | -0.0036837 | 0.0072821 | -0.017693 | 0.034976 |  | 69
STEELE_S | STEELE S | 866 | ST STORE | 4.242 |  |  |  | SOUTH2001 | BRAZOS | -0.0036837 | 0.0072821 | -0.015626 | 0.030891 |  | 69
ATKINS | ATKINS | 867 | ATKINS14 | 48.779 |  |  |  | SOUTH2001 | BRAZOS | -0.0036837 | 0.0072821 | -0.17969 | 0.35521 |  | 12.5
ANNEX | ANNEX | 868 | A&M ANEX | 4.242 |  |  |  | SOUTH2001 | BRAZOS | -0.0036837 | 0.0072821 | -0.015626 | 0.030891 |  | 69
NORTH11 | NORTH11 | 869 | NORTH | 19.011 |  |  |  | SOUTH2001 | BRAZOS | -0.0036602 | 0.0070142 | -0.069585 | 0.13335 |  | 69
TABOR | TABOR | 870 | TABOR | 23.329 |  |  |  | SOUTH2001 | BRAZOS | -0.003675 | 0.0072131 | -0.085735 | 0.16827 |  | 69
BUS_PARK | BUS PARK | 871 | BRBUSPRK | 6.404 |  |  |  | SOUTH2001 | BRAZOS | -0.0036281 | 0.0066102 | -0.023234 | 0.042332 |  | 69
NALL_LN | NALL LN | 872 | NALL | 44.925 |  |  |  | SOUTH2001 | BRAZOS | -0.0037526 | 0.0082181 | -0.16858 | 0.3692 |  | 69
SHADY_LN | SHADY LN | 873 | SHADY | 20.148 |  |  |  | SOUTH2001 | BRAZOS | -0.00378 | 0.009161 | -0.07616 | 0.18458 |  | 69
EAST | EAST | 874 | EAST69 | 18.11 |  |  |  | SOUTH2001 | BRAZOS | -0.0038542 | 0.010609 | -0.0698 | 0.19213 |  | 69
DANSBY | DANSBY | 875 | DANSBY69 |  |  |  |  | SOUTH2001 | BRAZOS | -0.0035977 | 0.0062294 | 0 | 0 |  | 69
IND_PARK | IND PARK | 876 | IND PARK | 23.313 |  |  |  | SOUTH2001 | BRAZOS | -0.0036746 | 0.0071775 | -0.085665 | 0.16733 |  | 69
BRIRCRT | BRIRCRT | 877 | BRCREST | 9.005 |  |  |  | SOUTH2001 | BRAZOS | -0.0037205 | 0.0071344 | -0.033503 | 0.064245 |  | 69
GREENS_P | GREENS P | 878 | BGRPR138 | 5.803 |  |  |  | SOUTH2001 | BRAZOS | -0.0040839 | 0.015661 | -0.023699 | 0.090878 |  | 138
STEEPHLW | STEEPHLW | 879 | STPHOL | 6.363 |  |  |  | SOUTH2001 | BRAZOS | -0.0038553 | 0.011568 | -0.024532 | 0.073609 |  | 138
SOUTH | SOUTH | 880 | BRYSOUTH | 7.404 |  |  |  | SOUTH2001 | BRAZOS | -0.0040742 | 0.015447 | -0.030166 | 0.11437 |  | 138
GREENS_P | GREENS P | 885 | BGRPR69 |  |  |  |  | SOUTH2001 | BRAZOS | -0.0040839 | 0.015661 | 0 | 0 |  | 69
ATKINS | ATKINS | 886 | ATKINS3 |  |  | 12 | 12 | SOUTH2001 | BRAZOS | -0.0036837 | 0.0072821 | -0.044205 | 0.087385 |  | 12.5
ATKINS | ATKINS | 887 | ATKINS6 |  |  | 46.177 | 50 | SOUTH2001 | BRAZOS | -0.0036837 | 0.0072821 | -0.18419 | 0.3641 |  | 13
ATKINS | ATKINS | 888 | ATKINS7 |  |  | 15.258 | 20 | SOUTH2001 | BRAZOS | -0.0036837 | 0.0072821 | -0.073675 | 0.14564 |  | 13
MILLICAN | MILLICAN | 889 | MILLICAN | 2.121 |  |  |  | SOUTH2001 | BRAZOS | -0.0040839 | 0.015661 | -0.008662 | 0.033216 |  | 69
ATKINS | ATKINS | 890 | ATKINS4 |  |  | 20.077 | 22 | SOUTH2001 | BRAZOS | -0.0036837 | 0.0072821 | -0.081042 | 0.16021 |  | 12
ATKINS | ATKINS | 891 | ATKINS5 |  |  | 25 | 25 | SOUTH2001 | BRAZOS | -0.0036837 | 0.0072821 | -0.092093 | 0.18205 |  | 12
DANSBY | DANSBY | 892 | DANSBY14 |  |  | 101.388 | 114 | SOUTH2001 | BRAZOS | -0.0035977 | 0.0062294 | -0.41014 | 0.71015 |  | 14
|  | 893 | BRSSWTCH |  |  |  |  | SOUTH2001 | BRAZOS | -0.0040737 | 0.015434 | 0 | 0 |  | 138
EAST | EAST | 959 | EAST138 |  |  |  |  | SOUTH2001 | BRAZOS | -0.0040466 | 0.014839 | 0 | 0 |  | 138
DANSBY | DANSBY | 960 | DANSBY |  |  |  |  | SOUTH2001 | BRAZOS | -0.0035239 | 0.0052951 | 0 | 0 |  | 138
BRY_E_C | BRY E C | 962 | BRY E C |  |  |  |  | SOUTH2001 | BRAZOS | -0.0040486 | 0.014884 | 0 | 0 |  | 138
GIBCRK | GIBCRK | 964 | GIBCRK C |  |  |  |  | SOUTH2001 | GRIMES | -0.0041603 | 0.01734 | 0 | 0 |  | 138
GIBCRK | GIBCRK | 967 | GIBCRK B |  |  |  |  | SOUTH2001 | GRIMES | -0.0042958 | 0.020428 | 0 | 0 |  | 345
GIBCRK | GIBCRK | 990 | GIBCRK |  |  | 462 | 462 | SOUTH2001 | GRIMES | -0.0042958 | 0.020428 | -1.9847 | 9.4378 |  | 22
|  | 1247 | WINK BET |  |  |  |  | SOUTH2001 | WINKLER | 0 | 0 | 0 | 0 |  | 69
TXCTY |  | 3087 | TXCTY1CG |  |  | 112 | 112 | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 4.256e-12 | 5.376e-12 |  | 13.8
TXCTY |  | 3088 | TXCTY2CG |  |  | 112 | 112 | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 4.256e-12 | 5.376e-12 |  | 13.8
TXCTY |  | 3089 | TXCTY3CG |  |  | 112 | 112 | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 4.256e-12 | 5.376e-12 |  | 13.8
TXCTY |  | 3090 | TXCTY4CG |  |  | 99 | 99 | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 3.762e-12 | 4.752e-12 |  | 13.8
|  | 3092 | CGNR |  |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 0 | 0 |  | 138
|  | 3133 | RICHLND1 |  |  |  |  | SOUTH2001 | FREESTONE | -0.0093613 | -0.069903 | 0 | 0 |  | 345
|  | 3134 | RICHLND2 |  |  |  |  | SOUTH2001 | FREESTONE | -0.0094979 | -0.069716 | 0 | 0 |  | 345
PLSTH | PLSTH | 3278 | LAKEVIEW |  |  |  |  | SOUTH2001 | ANDERSON | -0.0097618 | -0.068742 | 0 | 0 |  | 138
LLTSW | LLTSW | 3279 | LONGLK T |  |  |  |  | SOUTH2001 | LEON | -0.0093187 | -0.060233 | 0 | 0 |  | 138
LNGLK | LNGLK | 3280 | LONGLAKE | 6.992 |  |  |  | SOUTH2001 | FREESTONE | -0.0094185 | -0.062932 | -0.065855 | -0.44002 |  | 138
TNSCL | TNSCL | 3281 | TEN CLNY | 12.059 |  |  |  | SOUTH2001 | ANDERSON | -0.0097752 | -0.072572 | -0.11788 | -0.87515 |  | 138
BTLTP | BTLTP | 3283 | BUTLER M |  |  |  |  | SOUTH2001 | LEON | -0.0087338 | -0.047859 | 0 | 0 |  | 138
BETO | BETO_ | 3284 | BETO | 6.918 |  |  |  | SOUTH2001 | ANDERSON | -0.0096513 | -0.069222 | -0.066768 | -0.47888 |  | 138
ELKHR | ELKHR | 3285 | ELKHART | 4.623 |  |  |  | SOUTH2001 | ANDERSON | -0.0094057 | -0.062352 | -0.043483 | -0.28825 |  | 69.6
GPLND | GPLND | 3286 | GRAPELND | 6.443 |  |  |  | SOUTH2001 | HOUSTON | -0.0087725 | -0.048891 | -0.056521 | -0.315 |  | 69.6
CRKET | CRKET | 3289 | CROCKETT |  |  |  |  | SOUTH2001 | HOUSTON | -0.0083095 | -0.039049 | 0 | 0 |  | 69.6
EGFTP | EGFTP | 3290 | ELK GF T |  |  |  |  | SOUTH2001 | ANDERSON | -0.0091304 | -0.056499 | 0 | 0 |  | 69.6
SLCTP | SLCTP | 3291 | SLOCUM T |  |  |  |  | SOUTH2001 | ANDERSON | -0.0091304 | -0.056499 | 0 | 0 |  | 69.6
SLOCM | SLOCM | 3292 | SLOCUM |  |  |  |  | SOUTH2001 | ANDERSON | -0.0091304 | -0.056499 | 0 | 0 |  | 69.6
ELKGF | ELKGF | 3293 | ELK GULF | 1.096 |  |  |  | SOUTH2001 | ANDERSON | -0.0091304 | -0.056499 | -0.010007 | -0.061923 |  | 69.6
CRKET | CRKET | 3354 | CROCKETT | 30.852 |  |  |  | SOUTH2001 | HOUSTON | -0.007265 | -0.016844 | -0.22414 | -0.51968 |  | 138
GPMTP | GPMTP | 3355 | GRPLMG T |  |  |  |  | SOUTH2001 | HOUSTON | -0.007141 | -0.014209 | 0 | 0 |  | 138
GPLMG | GPLMG | 3356 | GRPLN MG | 3.187 |  |  |  | SOUTH2001 | HOUSTON | -0.007141 | -0.014209 | -0.022758 | -0.045285 |  | 138
PLSSP | PLSSP | 3357 | PLSNTSPG |  |  |  |  | SOUTH2001 | LEON | -0.0068879 | -0.0088288 | 0 | 0 |  | 138
CNI45 | CNI45 | 3358 | CENTVILL | 16.022 |  |  |  | SOUTH2001 | LEON | -0.0067692 | -0.0063041 | -0.10846 | -0.101 |  | 138
BBSES | BBSES | 3380 | BIGBRN |  |  |  |  | SOUTH2001 | FREESTONE | -0.008994 | -0.05764 | 0 | 0 |  | 345
BBSES | BBSES | 3381 | BBRN 1 G |  |  | 567 | 575 | SOUTH2001 | FREESTONE | -0.008994 | -0.05764 | -5.1715 | -33.1431 |  | 18
BBSES | BBSES | 3382 | BBRN 2 G |  |  | 587 | 595 | SOUTH2001 | FREESTONE | -0.008994 | -0.05764 | -5.3514 | -34.2959 |  | 18
JEWET | JEWET | 3390 | JEWETT S |  |  |  |  | SOUTH2001 | LEON | -0.0066915 | 0.0092452 | 0 | 0 |  | 345
JEWET | JEWET | 3391 | JEWETT N |  |  |  |  | SOUTH2001 | LEON | -0.0069155 | 0.018298 | 0 | 0 |  | 345
JEWET | JEWET | 3392 | JEWETT | 6.306 |  |  |  | SOUTH2001 | LEON | -0.0066607 | -0.0039974 | -0.042002 | -0.025208 |  | 138
JEWET | JEWET | 3393 | JEWETT |  |  |  |  | SOUTH2001 | LEON | -0.006661 | -0.004004 | 0 | 0 |  | 69
JEWET | JEWET | 3394 | JEWETT A |  |  |  |  | SOUTH2001 | LEON | -0.006661 | -0.004004 | 0 | 0 |  | 138
NUCOR | NUCOR | 3396 | NUCOR | 68.363 |  |  |  | SOUTH2001 | LEON | -0.0069155 | 0.018298 | -0.47276 | 1.2509 |  | 345
TOKSW | TOKSW | 3400 | TWIN OAK |  |  |  |  | SOUTH2001 | ROBERTSON | -0.0062568 | 0.032427 | 0 | 0 |  | 345
THSES | THSES | 3403 | THSE 1 G |  |  | 527 | 578 | SOUTH2001 | MCLENNAN | -0.004185 | -0.061091 | -2.4189 | -35.3104 |  | 18
THSES | THSES | 3404 | THSE 2 G |  |  | 755.249 | 818 | SOUTH2001 | MCLENNAN | -0.004185 | -0.061091 | -3.4233 | -49.9721 |  | 24
THSES | THSES | 3405 | T HOUSE |  |  |  |  | SOUTH2001 | MCLENNAN | -0.004185 | -0.061091 | 0 | 0 |  | 345
ELMOT | ELMOT | 3406 | ELM MOTT |  |  |  |  | SOUTH2001 | MCLENNAN | -0.003621 | -0.062909 | 0 | 0 |  | 345
ELMOT | ELMOT | 3407 | ELM MOTT |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0031031 | -0.061434 | 0 | 0 |  | 138
ELMOT | ELMOT | 3408 | ELM MOTT |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0038235 | -0.066182 | 0 | 0 |  | 69.6
LCSES | LCSES | 3409 | LAKE CRK |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0039147 | -0.054978 | 0 | 0 |  | 345
LCSES | LCSES | 3410 | LAKE CRK |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0032149 | -0.053368 | 0 | 0 |  | 138
LCSES | LCSES | 3411 | LKCK POD |  |  |  |  | SOUTH2001 | FALLS | -0.0032149 | -0.053368 | 0 | 0 |  | 69.6
TMPSW | TMPSW | 3413 | TEMPSSLT |  |  |  |  | SOUTH2001 | BELL | -0.00043023 | -0.05037 | 0 | 0 |  | 345
TMPSW | TMPSW | 3414 | TEMP SS |  |  |  |  | SOUTH2001 | BELL | -0.00044985 | -0.050409 | 0 | 0 |  | 345
TMPSW | TMPSW | 3415 | TEMP SS |  |  |  |  | SOUTH2001 | BELL | -4.575e-05 | -0.049899 | 0 | 0 |  | 138
LCSES | LCSES | 3416 | LCRK 1 G |  |  | 77 | 87 | SOUTH2001 | MCLENNAN | -0.0032149 | -0.053368 | -0.27969 | -4.643 |  | 13.8
LCSES | LCSES | 3417 | LCRK 2 G |  |  | 215 | 233 | SOUTH2001 | MCLENNAN | -0.0032149 | -0.053368 | -0.74906 | -12.4346 |  | 20
LCSES | LCSES | 3418 | LCTMOD 1 |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0032149 | -0.053368 | 0 | 0 |  | 69
LCSES | LCSES | 3419 | LCTMOD 2 |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0032149 | -0.053368 | 0 | 0 |  | 69
KLNSW | KLNSW | 3422 | KILL SS |  |  |  |  | SOUTH2001 | BELL | -0.00041542 | -0.050628 | 0 | 0 |  | 345
KLNSW | KLNSW | 3423 | KILL SS |  |  |  |  | SOUTH2001 | BELL | -0.00038689 | -0.051124 | 0 | 0 |  | 138
SDSES | SDSES | 3429 | SANDOW |  |  |  |  | SOUTH2001 | MILAM | 0.0030885 | -0.042932 | 0 | 0 |  | 345
SDSES | SDSES | 3430 | SANDOW | 109.7574 |  |  |  | SOUTH2001 | MILAM | 0.0032939 | -0.040017 | 0.36153 | -4.3922 | 2 | 138
SDSES | SDSES | 3431 | SANDOW | 74.2426 |  | 360 | 0 | SOUTH2001 | MILAM | 0.0032939 | -0.040017 | 0.24455 | -2.971 | 2 | 14.4
SDSES | SDSES | 3432 | SAND 4 G |  |  | 558 | 558 | SOUTH2001 | MILAM | 0.0032939 | -0.040017 | 1.838 | -22.3297 |  | 22
WWEST | WWEST | 3436 | WACO W | 40.896 |  |  |  | SOUTH2001 | MCLENNAN | -0.0028106 | -0.055052 | -0.11494 | -2.2514 |  | 138
WWEST | WWEST | 3437 | WACO W | 22.79 |  |  |  | SOUTH2001 | MCLENNAN | -0.0021065 | -0.053458 | -0.048008 | -1.2183 |  | 69
WEAST | WEAST | 3438 | WACO E | 62.539 |  |  |  | SOUTH2001 | MCLENNAN | -0.0030034 | -0.05584 | -0.18783 | -3.4922 |  | 138
WEAST | WEAST | 3439 | WACO E |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0033663 | -0.060417 | 0 | 0 |  | 69.6
MCGPH | MCGPH | 3440 | MCGREGPH |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0016876 | -0.053144 | 0 | 0 |  | 138
MCGPH | MCGPH | 3441 | MCGREGPH | 0.193 |  |  |  | SOUTH2001 | MCLENNAN | -0.0018184 | -0.053242 | -0.00035095 | -0.010276 |  | 69
SMBMG | SMBMG | 3489 | SIMSMAG | 0.092 |  |  |  | SOUTH2001 | FREESTONE | -0.006661 | -0.004004 | -0.00061281 | -0.00036837 |  | 69
FSREA | FSREA | 3492 | FRESTN |  |  |  |  | SOUTH2001 | FREESTONE | -0.006661 | -0.004004 | 0 | 0 |  | 69
|  | 3493 | TEAGUE |  |  |  |  | SOUTH2001 | FREESTONE | -0.006661 | -0.004004 | 0 | 0 |  | 69
FARAR | FARAR | 3500 | FARRAR M |  |  |  |  | SOUTH2001 | FREESTONE | -0.0060246 | -0.013111 | 0 | 0 |  | 138
SWTTP | SWTTP | 3501 | SEATEG T |  |  |  |  | SOUTH2001 | LEON | -0.0066607 | -0.0039974 | 0 | 0 |  | 138
SWYTG | SWYTG | 3502 | SEATEAG | 1.133 |  |  |  | SOUTH2001 | FREESTONE | -0.0066607 | -0.0039974 | -0.0075465 | -0.0045291 |  | 138
FRFWS | FRFWS | 3503 | FAIRWPOD |  |  |  |  | SOUTH2001 | FREESTONE | -0.0066607 | -0.0039974 | 0 | 0 |  | 138
WEST | WEST_ | 3525 | WEST | 10.159 |  |  |  | SOUTH2001 | MCLENNAN | -0.004352 | -0.07057 | -0.044212 | -0.71692 |  | 69.6
ROSTP | ROSTP | 3526 | ROSSSI T |  |  |  |  | SOUTH2001 | MCLENNAN | -0.004107 | -0.068536 | 0 | 0 |  | 69.6
ROSSN | ROSSN | 3527 | ROSSSINC | 1.598 |  |  |  | SOUTH2001 | MCLENNAN | -0.004107 | -0.068536 | -0.0065631 | -0.10952 |  | 69.6
TTPTP | TTPTP | 3528 | TOURS T |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0040637 | -0.068177 | 0 | 0 |  | 69.6
TTXPL | TTXPL | 3529 | TOURS | 1.1 |  |  |  | SOUTH2001 | MCLENNAN | -0.0040637 | -0.068177 | -0.0044701 | -0.074994 |  | 69.6
RGRHL | RGRHL | 3547 | ROGERS M |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0026296 | -0.064929 | 0 | 0 |  | 138
BLMED | BLMED | 3550 | BELLMEAD | 45.464 |  |  |  | SOUTH2001 | MCLENNAN | -0.0030251 | -0.058338 | -0.13753 | -2.6523 |  | 138
WNETP | WNETP | 3551 | WACO NE |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0029843 | -0.056716 | 0 | 0 |  | 138
WNRTH | WNRTH | 3552 | WACO N | 40.406 |  |  |  | SOUTH2001 | MCLENNAN | -0.0029466 | -0.056355 | -0.11906 | -2.2771 |  | 138
WNTHW | WNTHW | 3553 | WACO NW | 38.356 |  |  |  | SOUTH2001 | MCLENNAN | -0.002887 | -0.055784 | -0.11073 | -2.1396 |  | 138
LCSES | LCSES | 3554 | HALBRG M |  |  |  |  | SOUTH2001 | MCLENNAN | -0.003189 | -0.055236 | 0 | 0 |  | 138
THSTP | THSTP | 3555 | THOUSE T |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0031754 | -0.056215 | 0 | 0 |  | 138
THSES | THSES | 3556 | THOUSE | 6.703 |  |  |  | SOUTH2001 | MCLENNAN | -0.0031754 | -0.056215 | -0.021285 | -0.37681 |  | 138
WCOLO | WCOLO | 3559 | WACOCOLO | 49.221 |  |  |  | SOUTH2001 | MCLENNAN | -0.0029027 | -0.055428 | -0.14287 | -2.7282 |  | 138
WSOTH | WSOTH | 3560 | WACO S | 42.949 |  |  |  | SOUTH2001 | MCLENNAN | -0.0028676 | -0.055285 | -0.12316 | -2.3744 |  | 138
WMMMR | WMMMR | 3561 | WACOM1PT |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0028216 | -0.055097 | 0 | 0 |  | 138
WMMMR | WMMMR | 3562 | WACOM2PT |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0028289 | -0.054976 | 0 | 0 |  | 138
WMMT1 | WMMT1 | 3563 | WACOMM1T |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0028216 | -0.055097 | 0 | 0 |  | 138
WMMMR | WMMMR | 3564 | WACO MM1 | 26.373 |  |  |  | SOUTH2001 | MCLENNAN | -0.0028216 | -0.055097 | -0.074415 | -1.4531 |  | 138
WMMT2 | WMMT2 | 3565 | WACOMM2T |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0028289 | -0.054976 | 0 | 0 |  | 138
WMMMR | WMMMR | 3566 | WACO MM2 | 29.191 |  |  |  | SOUTH2001 | MCLENNAN | -0.0028289 | -0.054976 | -0.082578 | -1.6048 |  | 138
RBNSN | RBNSN | 3567 | ROBINSON | 27.886 |  |  |  | SOUTH2001 | MCLENNAN | -0.0029859 | -0.054322 | -0.083264 | -1.5148 |  | 138
WGNRL | WGNRL | 3570 | WACOTIRE | 0.546 |  |  |  | SOUTH2001 | MCLENNAN | -0.0034175 | -0.061062 | -0.0018659 | -0.03334 |  | 69.6
WKATY | WKATY | 3571 | WACOKATY | 8.51 |  |  |  | SOUTH2001 | MCLENNAN | -0.0034266 | -0.061177 | -0.02916 | -0.52061 |  | 69.6
WKYTP | WKYTP | 3572 | WACOKT T |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0034266 | -0.061177 | 0 | 0 |  | 69.6
NCRST | NCRST | 3574 | NCREST | 24.479 |  |  |  | SOUTH2001 | MCLENNAN | -0.0030585 | -0.059665 | -0.07487 | -1.4605 |  | 138
NCRTP | NCRTP | 3575 | NCREST T |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0030585 | -0.059665 | 0 | 0 |  | 138
LRENA | LRENA | 3578 | LORENA | 5.85 |  |  |  | SOUTH2001 | MCLENNAN | -0.0013345 | -0.051483 | -0.0078069 | -0.30117 |  | 69
EDDY | EDDY_ | 3580 | EDDY | 7.777 |  |  |  | SOUTH2001 | MCLENNAN | -0.000795 | -0.050103 | -0.0061827 | -0.38965 |  | 69.6
TROY | TROY_ | 3581 | TROY | 8.918 |  |  |  | SOUTH2001 | BELL | -0.00026932 | -0.048758 | -0.0024018 | -0.43482 |  | 69.6
GTVSW | GTVSW | 3583 | GATETDCT |  |  |  |  | SOUTH2001 | CORYELL | 0.0018111 | -0.065723 | 0 | 0 |  | 69
WATCO | WATCO | 3584 | WACOAT T |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0020154 | -0.05339 | 0 | 0 |  | 69
WATCO | WATCO | 3585 | WACOATLS | 2.502 |  |  |  | SOUTH2001 | MCLENNAN | -0.0020154 | -0.05339 | -0.0050424 | -0.13358 |  | 69
MCGRG | MCGRG | 3586 | MCGREG | 11.674 |  |  |  | SOUTH2001 | MCLENNAN | -0.0018636 | -0.053276 | -0.021755 | -0.62194 |  | 69
GTVAR | GTVAR | 3587 | GATESVIL | 1.985 |  |  |  | SOUTH2001 | CORYELL | 0.0018111 | -0.065723 | 0.0035949 | -0.13046 |  | 69
GRSBK | GRSBK | 3588 | GROESPOD |  |  |  |  | SOUTH2001 | LIMESTONE | -0.0044583 | -0.035551 | 0 | 0 |  | 69.6
WSANG | WSANG | 3590 | WACOSANG | 16.321 |  |  |  | SOUTH2001 | MCLENNAN | -0.0028435 | -0.055368 | -0.046409 | -0.90366 |  | 138
WWDWY | WWDWY | 3591 | WACOWOOD | 28.179 |  |  |  | SOUTH2001 | MCLENNAN | -0.0025838 | -0.054671 | -0.07281 | -1.5406 |  | 138
WATCO | WATCO | 3592 | WACOATCO | 29.177 |  |  |  | SOUTH2001 | MCLENNAN | -0.0024042 | -0.054368 | -0.070148 | -1.5863 |  | 138
SPVTP | SPVTP | 3593 | SPGVAL M |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0018377 | -0.053415 | 0 | 0 |  | 138
MPHTP | MPHTP | 3594 | MCGREG T |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0016681 | -0.053129 | 0 | 0 |  | 138
GRSBK | GRSBK | 3597 | GROESPOD |  |  |  |  | SOUTH2001 | LIMESTONE | -0.0044583 | -0.035551 | 0 | 0 |  | 138
BRGRS | BRGRS | 3598 | BEARGR M |  |  |  |  | SOUTH2001 | LEON | -0.0063774 | -0.0080565 | 0 | 0 |  | 138
AMGTP | AMGTP | 3599 | AMERGS T |  |  |  |  | SOUTH2001 | LEON | -0.0066103 | -0.0047188 | 0 | 0 |  | 138
AMGAS | AMGAS | 3600 | AMERIGAS | 8.906 |  |  |  | SOUTH2001 | LEON | -0.0066103 | -0.0047188 | -0.058871 | -0.042026 |  | 138
OLETHAM | OLETHAM | 3601 | OLETHA M |  |  |  |  | SOUTH2001 | LIMESTONE | -0.0054536 | -0.021292 | 0 | 0 |  | 138
BNMAG | BNMAG | 3603 | BROWN | 1.655 |  |  |  | SOUTH2001 | LEON | -0.006661 | -0.004004 | -0.011024 | -0.0066267 |  | 69
TMPLE | TMPLE | 3607 | TEMPL | 40.211 |  |  |  | SOUTH2001 | BELL | -0.00014814 | -0.050215 | -0.0059568 | -2.0192 |  | 138
TMNTH | TMNTH | 3608 | TEMP N | 56.609 |  |  |  | SOUTH2001 | BELL | -0.00043791 | -0.051108 | -0.02479 | -2.8932 |  | 138
TMPNW | TMPNW | 3609 | TEMP NW | 46.556 |  |  |  | SOUTH2001 | BELL | -0.00038742 | -0.051486 | -0.018037 | -2.397 |  | 138
BLTON | BLTON | 3610 | BELTON | 44.887 |  |  |  | SOUTH2001 | BELL | -0.00035012 | -0.051765 | -0.015716 | -2.3236 |  | 138
TMSTH | TMSTH | 3611 | TEMP S | 55.458 |  |  |  | SOUTH2001 | BELL | -0.00019022 | -0.050785 | -0.010549 | -2.8164 |  | 138
|  | 3612 | TEMP SE | 15.526 |  |  |  | SOUTH2001 | BELL | -0.00016606 | -0.050637 | -0.0025782 | -0.78619 |  | 138
NLNVL | NLNVL | 3617 | NOLANVIL | 14.607 |  |  |  | SOUTH2001 | BELL | -0.00035943 | -0.051603 | -0.0052502 | -0.75376 |  | 138
HKHTS | HKHTS | 3618 | HARKHT | 36.605 |  |  |  | SOUTH2001 | BELL | -0.00037326 | -0.051362 | -0.013663 | -1.8801 |  | 138
KLNTF | KLNTF | 3619 | KILLTAFT | 40.497 |  |  |  | SOUTH2001 | BELL | -0.00037717 | -0.051294 | -0.015274 | -2.0772 |  | 138
KLELM | KLELM | 3620 | KILELMRD | 35.487 |  |  |  | SOUTH2001 | BELL | -0.00038111 | -0.051225 | -0.013525 | -1.8178 |  | 138
KILEN | KILEN | 3621 | KILL | 34.758 |  |  |  | SOUTH2001 | BELL | -0.00037717 | -0.051294 | -0.01311 | -1.7829 |  | 138
|  | 3622 | KILLPK T |  |  |  |  | SOUTH2001 | BELL | -0.00037717 | -0.051294 | 0 | 0 |  | 138
KLNPS | KLNPS | 3623 | KILLPARK | 42.38 |  |  |  | SOUTH2001 | BELL | -0.00037717 | -0.051294 | -0.015985 | -2.1738 |  | 138
KLNFH | KLNFH | 3626 | KILLFTHD | 53.331 |  |  |  | SOUTH2001 | BELL | -0.00038689 | -0.051124 | -0.020633 | -2.7265 |  | 138
KFHSW | KFHSW | 3627 | KILLFH T |  |  |  |  | SOUTH2001 | BELL | -0.00038689 | -0.051124 | 0 | 0 |  | 138
KLNCC | KLNCC | 3628 | KILLCLCK | 42.461 |  |  |  | SOUTH2001 | BELL | -0.00038689 | -0.051124 | -0.016428 | -2.1708 |  | 138
KFHWS | KFHWS | 3629 | KILL FHW | 23.983 |  |  |  | SOUTH2001 | BELL | -0.00038689 | -0.051124 | -0.0092789 | -1.2261 |  | 138
CPRCV | CPRCV | 3630 | COPPERCV | 48.065 |  |  |  | SOUTH2001 | CORYELL | 0.015594 | -0.054463 | 0.74954 | -2.6177 |  | 138
HHSTH | HHSTH | 3633 | HARKHT S | 22.244 |  |  |  | SOUTH2001 | BELL | -0.00037562 | -0.051321 | -0.0083554 | -1.1416 |  | 138
BPSES | BPSES | 3635 | TUPOAG M |  |  |  |  | SOUTH2001 | BELL | 0.0014679 | -0.051334 | 0 | 0 |  | 69
TMPTV | TMPTV | 3636 | TEMPTAYV | 21.939 |  |  |  | SOUTH2001 | BELL | 0.0017282 | -0.050776 | 0.037916 | -1.114 |  | 69
SALDO | SALDO | 3640 | SALADO | 17.073 |  |  |  | SOUTH2001 | BELL | 0.0026199 | -0.046082 | 0.04473 | -0.78675 |  | 138
TMPSW | TMPSW | 3643 | TEMP SS |  |  |  |  | SOUTH2001 | BELL | 0.00038843 | -0.04694 | 0 | 0 |  | 69
TMPLE | TMPLE | 3644 | TEMP |  |  |  |  | SOUTH2001 | BELL | 0.00041051 | -0.047018 | 0 | 0 |  | 69
LTLRV | LTLRV | 3645 | LITRIVER | 3.24 |  |  |  | SOUTH2001 | BELL | 0.001088 | -0.045995 | 0.0035253 | -0.14902 |  | 69
HOLND | HOLND | 3646 | HOLLAND | 3.686 |  |  |  | SOUTH2001 | BELL | 0.0019381 | -0.044712 | 0.0071437 | -0.16481 |  | 69
BRTLT | BRTLT | 3647 | BARTLETT | 0.615 |  |  |  | SOUTH2001 | WILLIAMSON | 0.0025294 | -0.043819 | 0.0015556 | -0.026948 |  | 69
GRNGR | GRNGR | 3648 | GRANGER | 3.384 |  |  |  | SOUTH2001 | WILLIAMSON | 0.0029913 | -0.043121 | 0.010123 | -0.14592 |  | 69
TAYLR | TAYLR | 3649 | TAYLOR |  |  |  |  | SOUTH2001 | WILLIAMSON | 0.0041389 | -0.041388 | 0 | 0 |  | 69
ELGSW | ELGSW | 3650 | ELGIN SS |  |  |  |  | SOUTH2001 | WILLIAMSON | 0.00601 | -0.038563 | 0 | 0 |  | 138
ELGSW | ELGSW | 3651 | ELGIN SS |  |  |  |  | SOUTH2001 | WILLIAMSON | 0.0051493 | -0.039862 | 0 | 0 |  | 69
CPLND | CPLND | 3652 | COUPLAND | 2.197 |  |  |  | SOUTH2001 | WILLIAMSON | 0.0048339 | -0.040339 | 0.01062 | -0.088624 |  | 69
BRTLT | BRTLT | 3653 | BRTLT CB |  |  |  |  | SOUTH2001 | BELL | 0.0025294 | -0.043819 | 0 | 0 |  | 69
|  | 3654 | RNDRK SE | 52.343 |  |  |  | SOUTH2001 | WILLIAMSON | 0.0071903 | -0.038576 | 0.37636 | -2.0192 |  | 138
ELGIN | ELGIN | 3655 | ELGIN |  |  |  |  | SOUTH2001 | BASTROP | 0.0051493 | -0.039862 | 0 | 0 |  | 69
|  | 3656 | RR SE NT |  |  |  |  | SOUTH2001 | WILLIAMSON | 0.0071002 | -0.03865 | 0 | 0 |  | 138
|  | 3657 | RR SE ST |  |  |  |  | SOUTH2001 | WILLIAMSON | 0.0072803 | -0.038502 | 0 | 0 |  | 138
TAYLR | TAYLR | 3658 | TAYLOR | 39.076 |  |  |  | SOUTH2001 | WILLIAMSON | 0.0059156 | -0.038926 | 0.23116 | -1.5211 |  | 138
THRDN | THRDN | 3659 | THORNDAL | 4.729 |  |  |  | SOUTH2001 | MILAM | 0.0044921 | -0.039519 | 0.021243 | -0.18688 |  | 138
|  | 3661 | SALTY M |  |  |  |  | SOUTH2001 | MILAM | 0.0038543 | -0.039784 | 0 | 0 |  | 138
PFLGV | PFLGV | 3665 | PFLGRVIL | 67.207 |  |  |  | SOUTH2001 | TRAVIS | 0.0072393 | -0.038536 | 0.48653 | -2.5899 |  | 138
HUTTO | HUTTO | 3666 | HUTTO SS |  |  |  |  | SOUTH2001 | WILLIAMSON | 0.0070041 | -0.038729 | 0 | 0 |  | 138
RNDRK | RNDRK | 3668 | RNDRK | 101.691 |  |  |  | SOUTH2001 | WILLIAMSON | 0.0075619 | -0.038916 | 0.76898 | -3.9574 |  | 138
RRWES | RRWES | 3669 | RNDRK WH | 11.926 |  |  |  | SOUTH2001 | WILLIAMSON | 0.0072949 | -0.039321 | 0.086999 | -0.46895 |  | 138
RRNE | RRNE_ | 3670 | RNDRK NE | 24.701 |  |  |  | SOUTH2001 | WILLIAMSON | 0.007345 | -0.038843 | 0.18143 | -0.95947 |  | 138
RRSTH | RRSTH | 3672 | RNDRK S | 91.466 |  |  |  | SOUTH2001 | WILLIAMSON | 0.0079968 | -0.038479 | 0.73144 | -3.5195 |  | 138
|  | 3674 | ELGIN ET | 18.519 |  |  |  | SOUTH2001 | WILLIAMSON | 0.0077286 | -0.036566 | 0.14313 | -0.67717 |  | 138
ROGRS | ROGRS | 3675 | ROGERS | 4.191 |  |  |  | SOUTH2001 | MILAM | 0.001061 | -0.046625 | 0.0044465 | -0.1954 |  | 138
RKDLE | RKDLE | 3678 | ROCKDALE | 11.823 |  |  |  | SOUTH2001 | MILAM | 0.0022761 | -0.035514 | 0.026911 | -0.41988 |  | 138
TLBRT | TLBRT | 3679 | TALBER M |  |  |  |  | SOUTH2001 | MILAM | 0.001958 | -0.034106 | 0 | 0 |  | 138
MLANO | MLANO | 3682 | MILANO M |  |  |  |  | SOUTH2001 | MILAM | 0.00053458 | -0.026988 | 0 | 0 |  | 138
MNRVA | MNRVA | 3683 | MINERVA |  |  |  |  | SOUTH2001 | MILAM | 0.0015064 | -0.032107 | 0 | 0 |  | 138
MNRVA | MNRVA | 3684 | MINERVA | 2.115 |  |  |  | SOUTH2001 | MILAM | 0.0012534 | -0.035465 | 0.0026508 | -0.075008 |  | 69
CAMRN | CAMRN | 3685 | CAMERON | 18.91 |  |  |  | SOUTH2001 | MILAM | 0.0010379 | -0.038323 | 0.019627 | -0.72469 |  | 69
RKDLN | RKDLN | 3686 | ROCKDALN | 3.425 |  |  |  | SOUTH2001 | MILAM | 0.0012534 | -0.035465 | 0.0042927 | -0.12147 |  | 69
JREST |  | 3688 | JARRELLE | 4.058 |  |  |  | SOUTH2001 | WILLIAMSON | 0.0048607 | -0.042872 | 0.019725 | -0.17398 |  | 138
SOUWDCS | SOUWDCS | 3690 | SOUWD CS | 45.514 |  |  |  | SOUTH2001 | BRAZOS | -0.0040736 | 0.015433 | -0.18541 | 0.70243 |  | 138
CSSWCS | CSSWCS | 3691 | CSSW CS |  |  |  |  | SOUTH2001 | BRAZOS | -0.0040629 | 0.015198 | 0 | 0 |  | 138
POAKCS | POAKCS | 3692 | POAK CS | 71.69 |  |  |  | SOUTH2001 | BRAZOS | -0.0040665 | 0.015277 | -0.29153 | 1.0952 |  | 138
GRNPRCS | GRNPRCS | 3693 | GRNPR CS | 26.617 |  |  |  | SOUTH2001 | BRAZOS | -0.0040838 | 0.015657 | -0.1087 | 0.41675 |  | 138
NGATECS | NGATECS | 3694 | NGATE CS | 12.55 |  |  |  | SOUTH2001 | BRAZOS | -0.0035855 | 0.0060613 | -0.044998 | 0.076069 |  | 138
|  | 3695 | METER CS |  |  |  |  | SOUTH2001 | BRAZOS | -0.0040737 | 0.015436 | 0 | 0 |  | 138
WMMM2 | WMMM2 | 3697 | WACOMMP2 |  |  |  |  | SOUTH2001 | MCLENNAN | -0.0028289 | -0.054976 | 0 | 0 |  | 138
WMMMR | WMMMR | 3698 | WACOMMP1 | 11.933 |  |  |  | SOUTH2001 | MCLENNAN | -0.0028216 | -0.055097 | -0.03367 | -0.65748 |  | 138
ALAMOTP | ALAMOTP | 5000 | ALAMO TP |  |  |  |  | SOUTH2001 | BEXAR | 0.010752 | -0.030146 | 0 | 0 |  | 138
ALAMO_CM | ALAMO_CM | 5001 | ALAMO CM | 13.941 |  |  |  | SOUTH2001 | BEXAR | 0.010752 | -0.030146 | 0.1499 | -0.42027 |  | 138
AMD_SA | AMD-SA | 5002 | AMD-SA | 9.227 |  |  |  | SOUTH2001 | BEXAR | 0.011517 | -0.029991 | 0.10627 | -0.27673 |  | 138
ANDERSON | ANDERSON | 5003 | ANDERSON | 33.297 |  |  |  | SOUTH2001 | BEXAR | 0.011297 | -0.030028 | 0.37615 | -0.99984 |  | 138
ANDERSON | ANDERSON | 5005 | AUSTIN | 43.93 |  |  |  | SOUTH2001 | BEXAR | 0.011016 | -0.03001 | 0.48394 | -1.3183 |  | 138
AUSTIN2 | AUSTIN2 | 5006 | AUSTIN-2 |  |  |  |  | SOUTH2001 | BEXAR | 0.011021 | -0.030012 | 0 | 0 |  | 138
BALL_PRK | BALL_PRK | 5010 | BALL PK |  |  |  |  | SOUTH2001 | BEXAR | 0.011176 | -0.030031 | 0 | 0 |  | 69
BALL_PRK | BALL_PRK | 5011 | BALL PRK | 84.849 |  |  |  | SOUTH2001 | BEXAR | 0.011176 | -0.030031 | 0.94824 | -2.5481 |  | 138
BALL_PRK | BALL_PRK | 5013 | MRP3 |  | 100 |  |  | SOUTH2001 | BEXAR | 0.011176 | -0.030031 | 1.1176 | -3.0031 |  | 13.8
BANDERA | BANDERA | 5020 | BANDERA | 80.938 |  |  |  | SOUTH2001 | BEXAR | 0.011146 | -0.030024 | 0.90216 | -2.4301 |  | 138
BRAUNIG | BRAUNIG | 5025 | BRAUNIG |  |  |  |  | SOUTH2001 | BEXAR | 0.011865 | -0.030065 | 0 | 0 |  | 138
BRAUNIG | BRAUNIG | 5026 | VHB1 |  |  | 220 | 225 | SOUTH2001 | BEXAR | 0.011865 | -0.030065 | 2.6696 | -6.7647 |  | 20
BRAUNIG | BRAUNIG | 5027 | VHB2 |  |  | 230 | 240 | SOUTH2001 | BEXAR | 0.011865 | -0.030065 | 2.8476 | -7.2156 |  | 22
BRAUNIG | BRAUNIG | 5028 | VHB3 |  |  | 278.432 | 400 | SOUTH2001 | BEXAR | 0.011865 | -0.030065 | 4.746 | -12.0261 |  | 22
BECK_RD | BECK_RD | 5035 | BECK RD | 21.965 |  |  |  | SOUTH2001 | BEXAR | 0.011582 | -0.030093 | 0.2544 | -0.661 |  | 138
BROADVEW | BROADVEW | 5040 | BROADVEW | 117.947 |  |  |  | SOUTH2001 | BEXAR | 0.011111 | -0.030001 | 1.3106 | -3.5385 |  | 138
BROOKS | BROOKS | 5045 | BROOKS | 42.024 |  |  |  | SOUTH2001 | BEXAR | 0.012141 | -0.030121 | 0.51022 | -1.2658 |  | 138
BUCKEYE | BUCKEYE | 5050 | BUCKEYE | 28.584 |  |  |  | SOUTH2001 | BEXAR | 0.011013 | -0.029981 | 0.3148 | -0.85698 |  | 138
CAGNON | CAGNON | 5055 | CAGNON | 51.552 |  |  |  | SOUTH2001 | BEXAR | 0.011266 | -0.029915 | 0.58076 | -1.5422 |  | 138
CAGNON | CAGNON | 5056 | CAGNON |  |  |  |  | SOUTH2001 | BEXAR | 0.010638 | -0.029527 | 0 | 0 |  | 345
CAPITOL | CAPITOL | 5075 | CAPITOL | 16.749 |  |  |  | SOUTH2001 | BEXAR | 0.010945 | -0.029973 | 0.18331 | -0.50201 |  | 138
CASTLE | CASTLE | 5080 | CASTLEHL | 59.174 |  |  |  | SOUTH2001 | BEXAR | 0.010831 | -0.029912 | 0.64094 | -1.77 |  | 138
CHAVANEA | CHAVANEA | 5085 | CHAVANEA | 54.159 |  |  |  | SOUTH2001 | BEXAR | 0.012294 | -0.030151 | 0.66584 | -1.633 |  | 138
CHULIE | CHULIE | 5090 | CHULIE | 119.952 |  |  |  | SOUTH2001 | BEXAR | 0.010945 | -0.029985 | 1.3128 | -3.5968 |  | 138
COLISEUM | COLISEUM | 5095 | COLISEUM | 49.446 |  |  |  | SOUTH2001 | BEXAR | 0.011258 | -0.030097 | 0.55666 | -1.4882 |  | 138
DEELY | DEELY | 5110 | JT DEELY |  |  |  |  | SOUTH2001 | BEXAR | 0.011032 | -0.029975 | 0 | 0 |  | 138
DEELY | DEELY | 5111 | JTD1 |  |  | 405 | 415 | SOUTH2001 | BEXAR | 0.011032 | -0.029975 | 4.5784 | -12.4398 |  | 24
DEELY | DEELY | 5112 | JTD2 |  |  | 405 | 415 | SOUTH2001 | BEXAR | 0.011032 | -0.029975 | 4.5784 | -12.4398 |  | 24
DEZAVALA | DEZAVALA | 5125 | DEZAVALA | 135.9 |  |  |  | SOUTH2001 | BEXAR | 0.010824 | -0.029878 | 1.471 | -4.0604 |  | 138
DRESDEN | DRESDEN | 5130 | DRESDEN | 55.362 |  |  |  | SOUTH2001 | BEXAR | 0.010786 | -0.029889 | 0.59716 | -1.6547 |  | 138
ELMENDRF | ELMENDRF | 5135 | ELMENDRF | 23.469 |  |  |  | SOUTH2001 | BEXAR | 0.01197 | -0.02986 | 0.28092 | -0.70078 |  | 138
ENCINO | ENCINO | 5140 | ENCINO | 116.442 |  |  |  | SOUTH2001 | BEXAR | 0.01071 | -0.029838 | 1.2471 | -3.4744 |  | 138
ENCINO | ENCINO | 5145 | FALLSCTY | 3.912 |  |  |  | SOUTH2001 | WILSON | 0.012518 | -0.028788 | 0.048971 | -0.11262 |  | 138
FERN | FERN | 5147 | FERN |  |  |  |  | SOUTH2001 | BEXAR | 0.011219 | -0.030043 | 0 | 0 |  | 138
FIVE_PTS | FIVE_PTS | 5150 | FIVE PTS | 88.861 |  |  |  | SOUTH2001 | BEXAR | 0.011314 | -0.030001 | 1.0053 | -2.666 |  | 138
FLORESVI | FLORESVI | 5155 | FLORESVI | 29.988 |  |  |  | SOUTH2001 | WILSON | 0.012235 | -0.029342 | 0.3669 | -0.8799 |  | 138
FORT_SAM | FORT_SAM | 5160 | FT SAM | 34.402 |  |  |  | SOUTH2001 | BEXAR | 0.011244 | -0.030105 | 0.3868 | -1.0357 |  | 138
FRATT | FRATT | 5165 | FRATT | 82.743 |  |  |  | SOUTH2001 | BEXAR | 0.010908 | -0.030515 | 0.90257 | -2.5249 |  | 138
FRED_RD | FRED_RD | 5170 | FRED RD | 58.271 |  |  |  | SOUTH2001 | BEXAR | 0.011019 | -0.029972 | 0.6421 | -1.7465 |  | 138
GRANDVEW | GRANDVEW | 5175 | GRANDVEW | 55.463 |  |  |  | SOUTH2001 | BEXAR | 0.011306 | -0.030068 | 0.62708 | -1.6677 |  | 138
GREEN_MT | GREEN_MT | 5180 | GREEN MT | 34.702 |  |  |  | SOUTH2001 | BEXAR | 0.01075 | -0.03028 | 0.37304 | -1.0508 |  | 138
GRISSOM | GRISSOM | 5185 | GRISSOM | 102.802 |  |  |  | SOUTH2001 | BEXAR | 0.011247 | -0.030015 | 1.1562 | -3.0856 |  | 138
HARLANDA | HARLANDA | 5190 | HARLANDA | 46.336 |  |  |  | SOUTH2001 | BEXAR | 0.01218 | -0.03014 | 0.56439 | -1.3966 |  | 138
HARMONY | HARMONY | 5195 | HARMONY | 111.026 |  |  |  | SOUTH2001 | BEXAR | 0.010793 | -0.029907 | 1.1983 | -3.3204 |  | 138
HELOTES | HELOTES | 5200 | HELOTES | 99.994 |  |  |  | SOUTH2001 | BEXAR | 0.011338 | -0.030179 | 1.1337 | -3.0177 |  | 138
HIGHLAND | HIGHLAND | 5205 | HIGHLAND | 50.348 |  |  |  | SOUTH2001 | BEXAR | 0.011519 | -0.030067 | 0.57996 | -1.5138 |  | 138
HILLCTRY | HILLCTRY | 5210 | HILL CTY |  |  |  |  | SOUTH2001 | BEXAR | 0.010728 | -0.029832 | 0 | 0 |  | 138
HILLCTRY | HILLCTRY | 5211 | HILL CTY |  |  |  |  | SOUTH2001 | BEXAR | 0.010323 | -0.029578 | 0 | 0 |  | 345
HOLLYWD | HOLLYWD | 5220 | HOLLYWD | 130.583 |  |  |  | SOUTH2001 | BEXAR | 0.010746 | -0.029924 | 1.4033 | -3.9076 |  | 138
HONDO | HONDO | 5225 | HONDO | 15.044 |  |  |  | SOUTH2001 | MEDINA | 0.022508 | -0.032834 | 0.3386 | -0.49396 |  | 138
HOWARD | HOWARD | 5230 | HOWARD |  |  |  |  | SOUTH2001 | BEXAR | 0.012797 | -0.030283 | 0 | 0 |  | 138
KO2_M0 | KO2_M0 | 5240 | K - O #2 | 5.115 |  |  |  | SOUTH2001 | BEXAR | 0.012446 | -0.030183 | 0.063662 | -0.15439 |  | 138
KELLY | KELLY | 5245 | KELLY | 32.094 |  |  |  | SOUTH2001 | BEXAR | 0.011729 | -0.030053 | 0.37643 | -0.96451 |  | 138
KIRBY2 | KIRBY2 | 5249 | KIRBY-2 |  |  |  |  | SOUTH2001 | BEXAR | 0.011118 | -0.030063 | 0 | 0 |  | 138
KIRBY | KIRBY | 5250 | KIRBY | 81.038 |  |  |  | SOUTH2001 | BEXAR | 0.011222 | -0.030118 | 0.90945 | -2.4407 |  | 138
|  | 5255 | LAREDO | 88.259 |  |  |  | SOUTH2001 | BEXAR | 0.011278 | -0.029998 | 0.99536 | -2.6476 |  | 138
LASIERRA | LASIERRA | 5257 | LASIERRA | 72.914 |  |  |  | SOUTH2001 | BEXAR | 0.010869 | -0.029912 | 0.79249 | -2.181 |  | 138
LEON_CRK | LEON_CRK | 5260 | LEON |  |  |  |  | SOUTH2001 | BEXAR | 0.012483 | -0.030189 | 0 | 0 |  | 138
LEON_CRK | LEON_CRK | 5264 | LCP3 |  | 65 |  |  | SOUTH2001 | BEXAR | 0.012483 | -0.030189 | 0.81141 | -1.9623 |  | 13.8
LEON_CRK | LEON_CRK | 5265 | LCP4 |  | 95 |  |  | SOUTH2001 | BEXAR | 0.012483 | -0.030189 | 1.1859 | -2.868 |  | 13.8
L_A_HTS | L_A_HTS | 5285 | L A HT-A | 47.54 |  |  |  | SOUTH2001 | BEXAR | 0.011013 | -0.029981 | 0.52356 | -1.4253 |  | 138
L_A_HTS | L_A_HTS | 5286 | L A HT-B | 23.369 |  |  |  | SOUTH2001 | BEXAR | 0.010786 | -0.029889 | 0.25207 | -0.69847 |  | 138
LYTLE | LYTLE | 5290 | LYTLE | 23.569 |  |  |  | SOUTH2001 | BEXAR | 0.017182 | -0.031412 | 0.40497 | -0.74035 |  | 138
MARBACH | MARBACH | 5295 | MARBACH | 68.501 |  |  |  | SOUTH2001 | BEXAR | 0.011517 | -0.029991 | 0.78894 | -2.0544 |  | 138
MED_CTR | MED_CTR | 5300 | MED CTR | 147.835 |  |  |  | SOUTH2001 | BEXAR | 0.010945 | -0.029943 | 1.6181 | -4.4266 |  | 138
MEDINABS | MEDINABS | 5305 | MEDINABS | 52.956 |  |  |  | SOUTH2001 | BEXAR | 0.01196 | -0.030086 | 0.63336 | -1.5932 |  | 138
MERIDA | MERIDA | 5310 | MERIDA | 67.599 |  |  |  | SOUTH2001 | BEXAR | 0.011626 | -0.030038 | 0.78593 | -2.0305 |  | 138
NACDCHES | NACDCHES | 5315 | NACDCH | 103.204 |  |  |  | SOUTH2001 | BEXAR | 0.010929 | -0.029964 | 1.1279 | -3.0925 |  | 138
OLMOS | OLMOS | 5325 | OLMOS | 53.056 |  |  |  | SOUTH2001 | BEXAR | 0.011007 | -0.02999 | 0.58397 | -1.5912 |  | 138
PARSONS | PARSONS | 5332 | PARSONS | 15.746 |  |  |  | SOUTH2001 | BEXAR | 0.011219 | -0.030043 | 0.17665 | -0.47306 |  | 138
PEARSAL | PEARSAL | 5335 | PEARSALL | 29.687 |  |  |  | SOUTH2001 | BEXAR | 0.012287 | -0.030151 | 0.36476 | -0.89508 |  | 138
PINN_RD | PINN_RD | 5345 | PINN RD | 46.637 |  |  |  | SOUTH2001 | BEXAR | 0.011506 | -0.029997 | 0.5366 | -1.399 |  | 138
QUINTANA | QUINTANA | 5350 | QUINTANA | 38.212 |  |  |  | SOUTH2001 | BEXAR | 0.012217 | -0.030141 | 0.46683 | -1.1518 |  | 138
RANDOLPH | RANDOLPH | 5360 | RANDOLPH | 45.233 |  |  |  | SOUTH2001 | BEXAR | 0.010851 | -0.029924 | 0.49083 | -1.3535 |  | 138
SKYLINE | SKYLINE | 5369 | SKYLIN-N |  |  |  |  | SOUTH2001 | BEXAR | 0.010756 | -0.02997 | 0 | 0 |  | 138
SKYLINE | SKYLINE | 5370 | SKYLIN-S | 113.835 |  |  |  | SOUTH2001 | BEXAR | 0.010697 | -0.029843 | 1.2177 | -3.3972 |  | 138
SKYLINE | SKYLINE | 5371 | SKYLINE |  |  |  |  | SOUTH2001 | BEXAR | 0.010215 | -0.029619 | 0 | 0 |  | 345
SOUTHSAN | SOUTHSAN | 5385 | SO SAN | 53.658 |  |  |  | SOUTH2001 | BEXAR | 0.012262 | -0.030151 | 0.65796 | -1.6178 |  | 138
SOMERSET | SOMERSET | 5390 | SOMERSET | 25.074 |  |  |  | SOUTH2001 | BEXAR | 0.015001 | -0.030829 | 0.37614 | -0.77302 |  | 138
SOMMERS | SOMMERS | 5395 | SOMMERS |  |  |  |  | SOUTH2001 | BEXAR | 0.011748 | -0.030082 | 0 | 0 |  | 138
SOMMERS | SOMMERS | 5396 | OWS1 |  |  | 440 | 445 | SOUTH2001 | BEXAR | 0.011748 | -0.030082 | 5.2277 | -13.3865 |  | 22
SOMMERS | SOMMERS | 5397 | OWS2 |  |  | 430 | 435 | SOUTH2001 | BEXAR | 0.011748 | -0.030082 | 5.1102 | -13.0857 |  | 24
SPRUCE | SPRUCE | 5400 | SPRUCE |  |  |  |  | SOUTH2001 | BEXAR | 0.01039 | -0.029117 | 0 | 0 |  | 345
SPRUCE | SPRUCE | 5401 | JKS1 |  |  | 530 | 555 | SOUTH2001 | BEXAR | 0.01039 | -0.029117 | 5.7662 | -16.1599 |  | 24
ST_HEDWG | ST_HEDWG | 5410 | ST HEDWG | 44.431 |  |  |  | SOUTH2001 | BEXAR | 0.011255 | -0.030098 | 0.50009 | -1.3373 |  | 138
STCKDALE | STCKDALE | 5412 | STCKDALE |  |  |  |  | SOUTH2001 | WILSON | 0.012267 | -0.029279 | 0 | 0 |  | 138
STREICH | STREICH | 5417 | STREICH | 12.135 |  |  |  | SOUTH2001 | BEXAR | 0.011836 | -0.030069 | 0.14363 | -0.36489 |  | 138
SUTHRLND | SUTHRLND | 5418 | SUTHRLND | 7.823 |  |  |  | SOUTH2001 | BEXAR | 0.012267 | -0.029279 | 0.095963 | -0.22905 |  | 138
TENTH_ST | TENTH_ST | 5420 | TENTH ST | 117.445 |  |  |  | SOUTH2001 | BEXAR | 0.011269 | -0.03009 | 1.3235 | -3.5339 |  | 138
TERRELL | TERRELL | 5425 | TERREL-A | 34.2 |  |  |  | SOUTH2001 | BEXAR | 0.011016 | -0.03001 | 0.37675 | -1.0263 |  | 138
TERRELL | TERRELL | 5426 | TERREL-B | 41.823 |  |  |  | SOUTH2001 | BEXAR | 0.011016 | -0.03001 | 0.46073 | -1.2551 |  | 138
TUTTLE | TUTTLE | 5435 | TUTTLE |  |  |  |  | SOUTH2001 | BEXAR | 0.010945 | -0.029973 | 0 | 0 |  | 138
TUTTLE | TUTTLE | 5436 | WBT1 |  | 65 |  |  | SOUTH2001 | BEXAR | 0.010945 | -0.029973 | 0.7114 | -1.9482 |  | 13.8
TUTTLE | TUTTLE | 5437 | WBT2 |  | 100 |  |  | SOUTH2001 | BEXAR | 0.010945 | -0.029973 | 1.0945 | -2.9973 |  | 13.8
TUTTLE | TUTTLE | 5438 | WBT3 |  | 100 |  |  | SOUTH2001 | BEXAR | 0.010945 | -0.029973 | 1.0945 | -2.9973 |  | 13.8
TUTTLE | TUTTLE | 5439 | WBT4 |  | 160 |  |  | SOUTH2001 | BEXAR | 0.010945 | -0.029973 | 1.7511 | -4.7956 |  | 18
USAATP | USAATP | 5450 | USAA-ATP |  |  |  |  | SOUTH2001 | BEXAR | 0.010924 | -0.029932 | 0 | 0 |  | 138
USAA_A | USAA-A | 5451 | USAA-A |  |  |  |  | SOUTH2001 | BEXAR | 0.010924 | -0.029932 | 0 | 0 |  | 138
USAA_B | USAA-B | 5452 | USAA-BTP |  |  |  |  | SOUTH2001 | BEXAR | 0.010918 | -0.029923 | 0 | 0 |  | 138
USAA_B | USAA-B | 5453 | USAA-B | 15.346 |  |  |  | SOUTH2001 | BEXAR | 0.010918 | -0.029923 | 0.16755 | -0.4592 |  | 138
USAA2 | USAA2 | 5455 | USAA#2TP |  |  |  |  | SOUTH2001 | BEXAR | 0.010932 | -0.029939 | 0 | 0 |  | 138
USAA2 | USAA2 | 5456 | USAA #2 | 5.215 |  |  |  | SOUTH2001 | BEXAR | 0.010932 | -0.029939 | 0.057011 | -0.15613 |  | 138
UTSA | UTSA | 5460 | UTSA | 35.805 |  |  |  | SOUTH2001 | BEXAR | 0.011 | -0.029987 | 0.39386 | -1.0737 |  | 138
UTSA_ATP | UTSA-ATP | 5461 | UTSA-ATP |  |  |  |  | SOUTH2001 | BEXAR | 0.010999 | -0.029986 | 0 | 0 |  | 138
UTSA_BTP | UTSA-BTP | 5462 | UTSA-BTP |  |  |  |  | SOUTH2001 | BEXAR | 0.011002 | -0.029988 | 0 | 0 |  | 138
VALLEY | VALLEY | 5465 | VALLEY | 27.28 |  |  |  | SOUTH2001 | BEXAR | 0.01181 | -0.030054 | 0.32218 | -0.81986 |  | 138
VLSI | VLSI | 5467 | VLSI | 11.634 |  |  |  | SOUTH2001 | BEXAR | 0.011343 | -0.030007 | 0.13197 | -0.3491 |  | 138
VONROSE | VONROSE | 5475 | VON ROSE |  |  |  |  | SOUTH2001 | BEXAR | 0.010485 | -0.029274 | 0 | 0 |  | 345
VONROSE | VONROSE | 5476 | AVR1-CT1 |  |  | 155 | 175 | SOUTH2001 | BEXAR | 0.010485 | -0.029274 | 1.8349 | -5.123 |  | 18
VONROSE | VONROSE | 5477 | AVR1-ST1 |  |  | 159 | 197 | SOUTH2001 | BEXAR | 0.010485 | -0.029274 | 2.0655 | -5.767 |  | 18
VONROSE | VONROSE | 5478 | AVR1-CT2 |  |  | 155 | 175 | SOUTH2001 | BEXAR | 0.010485 | -0.029274 | 1.8349 | -5.123 |  | 18
|  | 5479 | AVR1-M |  |  |  |  | SOUTH2001 | BEXAR | 0.010485 | -0.029274 | 0 | 0 |  | 345
WALZEM | WALZEM | 5485 | WALZEM | 144.941 |  |  |  | SOUTH2001 | BEXAR | 0.010809 | -0.029887 | 1.5666 | -4.3319 |  | 138
WSTSIDE | WSTSIDE | 5490 | WESTSIDE | 71.008 |  |  |  | SOUTH2001 | BEXAR | 0.011483 | -0.03001 | 0.81537 | -2.131 |  | 138
RAYBURN | RAYBURN | 5500 | RAYBRN 9 |  |  |  |  | SOUTH2001 | VICTORIA | 0.0095703 | -0.022983 | 0 | 0 |  | 69
RAYBURN | RAYBURN | 5501 | RAYGEN12 |  |  |  |  | SOUTH2001 | VICTORIA | 0.0095703 | -0.022983 | 0 | 0 |  | 13
RAYBURN | RAYBURN | 5502 | RAYBRN 8 |  |  |  |  | SOUTH2001 | VICTORIA | 0.0091804 | -0.02284 | 0 | 0 |  | 138
RAYBURN | RAYBURN | 5503 | RAYGEN3 |  |  | 15 | 25 | SOUTH2001 | VICTORIA | 0.0095703 | -0.022983 | 0.23926 | -0.57457 |  | 13
NURSRYS | NURSRYS | 5504 | NURSRY 8 | 7.369 |  |  |  | SOUTH2001 | VICTORIA | 0.0090419 | -0.022239 | 0.06663 | -0.16388 |  | 69
RAYBURN |  | 5505 | RAYGEN1 |  |  | 7 | 10 | SOUTH2001 | VICTORIA | 0.0095703 | -0.022983 | 0.095703 | -0.22983 |  | 13
RAYBURN |  | 5506 | RAYGEN2 |  |  | 12 | 12 | SOUTH2001 | VICTORIA | 0.0095703 | -0.022983 | 0.11484 | -0.27579 |  | 13
FORTRSW | FORTRSW | 5510 | FDTRNSW9 |  |  |  |  | SOUTH2001 | VICTORIA | 0.0087222 | -0.021788 | 0 | 0 |  | 69
INEZS | INEZS | 5514 | INEZ 9 | 4.999 |  |  |  | SOUTH2001 | VICTORIA | 0.0081106 | -0.020927 | 0.040545 | -0.10461 |  | 69
ELTORSS | ELTORSS | 5516 | ELTORSW9 |  |  |  |  | SOUTH2001 | VICTORIA | 0.0078163 | -0.020513 | 0 | 0 |  | 69
ELTORSW | ELTORSW | 5518 | ELTOROS9 |  |  |  |  | SOUTH2001 | VICTORIA | 0.0077817 | -0.02048 | 0 | 0 |  | 69
ELTORS | ELTORS | 5520 | ELTORO 9 | 2.146 |  |  |  | SOUTH2001 | VICTORIA | 0.0077817 | -0.02048 | 0.0167 | -0.043949 |  | 69
EDNAS | EDNAS | 5522 | EDNA 9 | 4.452 |  |  |  | SOUTH2001 | JACKSON | 0.0075624 | -0.020269 | 0.033668 | -0.090239 |  | 69
GANADSW | GANADSW | 5525 | GANADSW9 |  |  |  |  | SOUTH2001 | JACKSON | 0.0071092 | -0.019835 | 0 | 0 |  | 69
GANADOS | GANADOS | 5526 | GANADO 9 | 3.067 |  |  |  | SOUTH2001 | JACKSON | 0.0071092 | -0.019835 | 0.021804 | -0.060833 |  | 69
LOUISES | LOUISES | 5528 | LOUISE 9 | 1.157 |  |  |  | SOUTH2001 | WHARTON | 0.0070035 | -0.019733 | 0.008103 | -0.022832 |  | 69
RMOTTSW | RMOTTSW | 5530 | RMOTTSW9 |  |  |  |  | SOUTH2001 | WHARTON | 0.006579 | -0.019326 | 0 | 0 |  | 69
RMOTTS | RMOTTS | 5534 | RMOTT 9 | 1.806 |  |  |  | SOUTH2001 | WHARTON | 0.006579 | -0.019326 | 0.011882 | -0.034904 |  | 69
NADAS | NADAS | 5536 | NADA 9 | 2.405 |  |  |  | SOUTH2001 | LAVACA | 0.0063269 | -0.020866 | 0.015216 | -0.050183 |  | 69
ELCMPOS | ELCMPOS | 5538 | ELCP 9 | 7.687 |  |  |  | SOUTH2001 | WHARTON | 0.0063888 | -0.019144 | 0.04911 | -0.14716 |  | 69
PLANVWS | PLANVWS | 5540 | PLANVW 9 | 3.115 |  |  |  | SOUTH2001 | WHARTON | 0.006127 | -0.018041 | 0.019085 | -0.056198 |  | 69
INDPKSW | INDPKSW | 5542 | INDPKSW9 |  |  |  |  | SOUTH2001 | WHARTON | 0.0063156 | -0.018836 | 0 | 0 |  | 69
INDPK9 | INDPK9 | 5543 | INDPK 9 | 4.225 |  |  |  | SOUTH2001 | WHARTON | 0.0063156 | -0.018836 | 0.026684 | -0.079582 |  | 69
DANEVA | DANEVA | 5544 | DNVG 9 |  |  |  |  | SOUTH2001 | WHARTON | 0.0059505 | -0.017298 | 0 | 0 |  | 69
|  | 5545 | USRSTEC1 |  | 85 |  |  | SOUTH2001 | WHARTON | 0.0059505 | -0.017298 | 0.50579 | -1.4703 |  | 69
DANEVA | DANEVA | 5546 | DNVG 8 |  |  |  |  | SOUTH2001 | WHARTON | 0.0059207 | -0.016839 | 0 | 0 |  | 138
DANEVAS | DANEVAS | 5548 | DNVNG 9 | 3.193 |  |  |  | SOUTH2001 | WHARTON | 0.0058831 | -0.017077 | 0.018785 | -0.054527 |  | 69
CLEMVSW | CLEMVSW | 5549 | CLMVLSW9 |  |  |  |  | SOUTH2001 | MATAGORDA | 0.005711 | -0.016514 | 0 | 0 |  | 69
NCLMVLS | NCLMVLS | 5550 | CLMVLN 9 | 3.937 |  |  |  | SOUTH2001 | MATAGORDA | 0.005711 | -0.016514 | 0.022484 | -0.065016 |  | 69
TXBRINS | TXBRINS | 5551 | TEXBRIN |  |  |  |  | SOUTH2001 | MATAGORDA | 0.005711 | -0.016514 | 0 | 0 |  | 69
S_CLMVS | S-CLMVS | 5552 | CLMVLS 9 | 2.128 |  |  |  | SOUTH2001 | MATAGORDA | 0.005711 | -0.016514 | 0.012153 | -0.035142 |  | 69
MRKHMSW | MRKHMSW | 5554 | MRKHAM 9 |  |  |  |  | SOUTH2001 | MATAGORDA | 0.0055226 | -0.015898 | 0 | 0 |  | 69
VNVLKSW | VNVLKSW | 5556 | VNVLKSW9 |  |  |  |  | SOUTH2001 | MATAGORDA | 0.0052215 | -0.014912 | 0 | 0 |  | 69
VNVLKS | VNVLKS | 5558 | VNVLK 9 | 6.073 |  |  |  | SOUTH2001 | MATAGORDA | 0.0052215 | -0.014912 | 0.03171 | -0.090562 |  | 69
BAYCTYS | BAYCTYS | 5560 | BACT 9 | 4.805 |  |  |  | SOUTH2001 | MATAGORDA | 0.0051526 | -0.014687 | 0.024758 | -0.07057 |  | 69
SARGNTS | SARGNTS | 5564 | SARGNT 9 | 6.074 |  |  |  | SOUTH2001 | MATAGORDA | 0.0037174 | -0.01092 | 0.02258 | -0.066331 |  | 69
FRANKC | FRANKC | 5566 | FRNCP 9 | 4.932 |  |  |  | SOUTH2001 | BRAZORIA | 0.0030935 | -0.0092829 | 0.015257 | -0.045783 |  | 69
FRANKC | FRANKC | 5568 | FRKCMP8 |  |  |  |  | SOUTH2001 | BRAZORIA | 0.0022813 | -0.0071516 | 0 | 0 |  | 138
TINTOPS | TINTOPS | 5569 | TINTOP 9 | 2.408 |  |  |  | SOUTH2001 | MATAGORDA | 0.0060719 | -0.016641 | 0.014621 | -0.040072 |  | 69
PLACIOS | PLACIOS | 5570 | PALACI 9 | 0.895 |  |  |  | SOUTH2001 | MATAGORDA | 0.0063235 | -0.017176 | 0.0056595 | -0.015373 |  | 69
STRU235 | STRU235 | 5571 | STRU235 |  |  |  |  | SOUTH2001 | MATAGORDA | 0.00636 | -0.017254 | 0 | 0 |  | 69
CARANCS | CARANCS | 5573 | CARANC 9 | 2.464 |  |  |  | SOUTH2001 | JACKSON | 0.0066413 | -0.017852 | 0.016364 | -0.043987 |  | 69
OVILASW | OVILASW | 5574 | OLIVSW 9 |  |  |  |  | SOUTH2001 | JACKSON | 0.0070235 | -0.018665 | 0 | 0 |  | 69
OLIVIAS | OLIVIAS | 5576 | OLIVIA 9 | 1.956 |  |  |  | SOUTH2001 | CALHOUN | 0.0070235 | -0.018665 | 0.013738 | -0.036508 |  | 69
LOLITAS | LOLITAS | 5578 | LOLITA 9 | 2.733 |  |  |  | SOUTH2001 | JACKSON | 0.0072964 | -0.019245 | 0.019941 | -0.052596 |  | 69
VNHUMBS | VNHUMBS | 5580 | VANHUM 9 | 0.355 |  |  |  | SOUTH2001 | JACKSON | 0.0076552 | -0.020008 | 0.0027176 | -0.0071027 |  | 69
VANBLT | VANBLT | 5582 | VAND 9 |  |  |  |  | SOUTH2001 | JACKSON | 0.0076977 | -0.020098 | 0 | 0 |  | 69
VANBLT | VANBLT | 5584 | VAND 8 |  |  |  |  | SOUTH2001 | JACKSON | 0.0076029 | -0.019932 | 0 | 0 |  | 138
VNDBLTS | VNDBLTS | 5586 | VANDR 9 | 2.804 |  |  |  | SOUTH2001 | JACKSON | 0.0076996 | -0.020101 | 0.02159 | -0.056364 |  | 69
PLCEDOS | PLCEDOS | 5590 | PLACDO 9 | 3.078 |  |  |  | SOUTH2001 | VICTORIA | 0.0082871 | -0.021145 | 0.025508 | -0.065085 |  | 69
KAMEYS | KAMEYS | 5591 | KAMEY 9 | 0.009 |  |  |  | SOUTH2001 | VICTORIA | 0.0082639 | -0.021214 | 7.4375e-05 | -0.00019092 |  | 69
PRTLAVS | PRTLAVS | 5592 | PTLAV 9 | 8.832 |  |  |  | SOUTH2001 | CALHOUN | 0.0082414 | -0.02128 | 0.072788 | -0.18795 |  | 69
PORTOCS | PORTOCS | 5596 | PTOCNR 9 | 7.069 |  |  |  | SOUTH2001 | CALHOUN | 0.0082414 | -0.02128 | 0.058259 | -0.15043 |  | 69
LONETRS | LONETRS | 5600 | LONTRE 9 | 6.293 |  |  |  | SOUTH2001 | CALHOUN | 0.0085978 | -0.02159 | 0.054106 | -0.13587 |  | 69
TWNPNSW | TWNPNSW | 5602 | TWNPNSW9 |  |  |  |  | SOUTH2001 | VICTORIA | 0.0089095 | -0.022036 | 0 | 0 |  | 69
TWNPINS | TWNPINS | 5603 | TWNPNS 9 | 2.22 |  |  |  | SOUTH2001 | VICTORIA | 0.0089095 | -0.022036 | 0.019779 | -0.048921 |  | 69
HIGHLAS | HIGHLAS | 5604 | HILAND 9 | 7.562 |  |  |  | SOUTH2001 | VICTORIA | 0.009061 | -0.022253 | 0.068519 | -0.16828 |  | 69
ALOES | ALOES | 5606 | ALOE 9 | 5.538 |  |  |  | SOUTH2001 | VICTORIA | 0.0096639 | -0.02308 | 0.053519 | -0.12782 |  | 69
MCFADIS | MCFADIS | 5608 | MCFADN 9 | 1.424 |  |  |  | SOUTH2001 | VICTORIA | 0.0098204 | -0.023244 | 0.013984 | -0.0331 |  | 69
RFUGIOS | RFUGIOS | 5610 | REFU 9 | 0.292 |  |  |  | SOUTH2001 | REFUGIO | 0.010045 | -0.023479 | 0.002933 | -0.0068558 |  | 69
BONNIES | BONNIES | 5614 | BONEVW 9 | 0.687 |  |  |  | SOUTH2001 | REFUGIO | 0.010174 | -0.023614 | 0.0069897 | -0.016223 |  | 69
TAFT_S | TAFT-S | 5616 | TAFT 9 | 0.999 |  |  |  | SOUTH2001 | SAN PATRI | 0.010305 | -0.023751 | 0.010295 | -0.023727 |  | 69
SODVILS | SODVILS | 5618 | SODVIL 9 | 1.227 |  |  |  | SOUTH2001 | SAN PATRI | 0.0104 | -0.02385 | 0.012761 | -0.029264 |  | 69
WSINTSW | WSINTSW | 5620 | WSINTSW9 |  |  |  |  | SOUTH2001 | SAN PATRI | 0.01051 | -0.023965 | 0 | 0 |  | 69
WSINTOS | WSINTOS | 5622 | WSINT 9 | 5.809 |  |  |  | SOUTH2001 | SAN PATRI | 0.01051 | -0.023965 | 0.061052 | -0.13921 |  | 69
CALALS | CALALS | 5626 | CALALN 9 | 7.71 |  |  |  | SOUTH2001 | NUECES | 0.010615 | -0.024075 | 0.081842 | -0.18562 |  | 69
RVRSDSW | RVRSDSW | 5630 | RVRSDSW9 |  |  |  |  | SOUTH2001 | NUECES | 0.010624 | -0.024085 | 0 | 0 |  | 69
RVRSDS | RVRSDS | 5632 | RVRSD 9 | 6.835 |  |  |  | SOUTH2001 | NUECES | 0.010624 | -0.024085 | 0.072612 | -0.16462 |  | 69
ROBSTOS | ROBSTOS | 5634 | ROBSTN 9 | 4.023 |  |  |  | SOUTH2001 | NUECES | 0.010698 | -0.024168 | 0.043038 | -0.097228 |  | 69
CORPSSW | CORPSSW | 5636 | CCSW 9 |  |  |  |  | SOUTH2001 | NUECES | 0.010749 | -0.024226 | 0 | 0 |  | 69
CORPUS | CORPUS | 5638 | CORCHR 9 | 1.548 |  |  |  | SOUTH2001 | NUECES | 0.010749 | -0.024226 | 0.01664 | -0.037501 |  | 69
DRSCOLS | DRSCOLS | 5640 | DRISCL 9 | 2.904 |  |  |  | SOUTH2001 | NUECES | 0.010909 | -0.024406 | 0.031681 | -0.070874 |  | 69
RICRDOS | RICRDOS | 5645 | RICRDO 9 | 0.183 |  |  |  | SOUTH2001 | KLEBERG | 0.010901 | -0.024288 | 0.0019949 | -0.0044448 |  | 69
RVIERAS | RVIERAS | 5646 | RIVERA 9 | 4.526 |  |  |  | SOUTH2001 | KLEBERG | 0.010898 | -0.024247 | 0.049324 | -0.10974 |  | 69
LOYOLA | LOYOLA | 5648 | LOYOLA8 |  |  |  |  | SOUTH2001 | KLEBERG | 0.010891 | -0.024154 | 0 | 0 |  | 138
LOYOLA | LOYOLA | 5650 | LOYOLA69 |  |  |  |  | SOUTH2001 | KLEBERG | 0.010897 | -0.024231 | 0 | 0 |  | 69
CNTRALS | CNTRALS | 5652 | CENTRL 9 | 2.461 |  |  |  | SOUTH2001 | NUECES | 0.011055 | -0.024642 | 0.027205 | -0.060645 |  | 69
SNDIEGS | SNDIEGS | 5654 | SNDEGO 9 | 5.847 |  |  |  | SOUTH2001 | DUVAL | 0.011355 | -0.025131 | 0.066391 | -0.14694 |  | 69
ORNGROV | ORNGROV | 5658 | ORNGRV 9 |  |  |  |  | SOUTH2001 | JIM WELLS | 0.011643 | -0.0256 | 0 | 0 |  | 69
|  | 5659 | USRSTEC2 |  | 30 |  |  | SOUTH2001 | JIM WELLS | 0.011643 | -0.0256 | 0.34929 | -0.76801 |  | 69
ORNGROV | ORNGROV | 5660 | ORNGRV 8 |  |  |  |  | SOUTH2001 | JIM WELLS | 0.0116 | -0.025578 | 0 | 0 |  | 138
ORNGRVS | ORNGRVS | 5662 | OG 9 | 8.419 |  |  |  | SOUTH2001 | JIM WELLS | 0.011647 | -0.025606 | 0.098056 | -0.21557 |  | 69
SANDIAS | SANDIAS | 5666 | SANDIA 9 | 2.705 |  |  |  | SOUTH2001 | JIM WELLS | 0.01185 | -0.025864 | 0.032054 | -0.069961 |  | 69
MATHIS | MATHIS | 5668 | MATHIS 9 | 2.636 |  |  |  | SOUTH2001 | LIVE OAK | 0.012037 | -0.026101 | 0.03173 | -0.068803 |  | 69
OLMOS_S | OLMOS-S | 5672 | OLMOS 9 | 3.308 |  |  |  | SOUTH2001 | OLMOS | 0.01177 | -0.025763 | 0.038935 | -0.085225 |  | 69
BEPRISS | BEPRISS | 5673 | BEEPRIS | 2.795 |  |  |  | SOUTH2001 | BEE | 0.01167 | -0.025637 | 0.032616 | -0.071654 |  | 69
BEEVLES | BEEVLES | 5674 | BEEVIL 9 | 6.624 |  |  |  | SOUTH2001 | BEE | 0.011456 | -0.025367 | 0.075885 | -0.16803 |  | 69
SCHRODS | SCHRODS | 5678 | SCHRDR 9 | 4.05 |  |  |  | SOUTH2001 | GOLIAD | 0.0098478 | -0.023333 | 0.039884 | -0.094501 |  | 69
L_463S | L-463S | 5680 | L-463 | 2.932 |  |  |  | SOUTH2001 | VICTORIA | 0.0089629 | -0.022795 | 0.026279 | -0.066834 |  | 138
GEOWSTS | GEOWSTS | 5684 | GWEST 9 | 3.739 |  |  |  | SOUTH2001 | LIVE OAK | 0.013054 | -0.027388 | 0.048807 | -0.1024 |  | 69
|  | 5685 | WGWTAP9 |  |  |  |  | SOUTH2001 | LIVE OAK | 0.01341 | -0.027839 | 0 | 0 |  | 69
GEOWEST | GEOWEST | 5686 | GEOWST 9 |  |  |  |  | SOUTH2001 | LIVE OAK | 0.013599 | -0.028079 | 0 | 0 |  | 69
GEOWEST | GEOWEST | 5688 | GEOWST 8 |  |  |  |  | SOUTH2001 | LIVE OAK | 0.013497 | -0.028121 | 0 | 0 |  | 138
WGWSTS | WGWSTS | 5690 | WGWST 9 | 2.017 |  |  |  | SOUTH2001 | LIVE OAK | 0.01341 | -0.027839 | 0.027048 | -0.056152 |  | 69
SIMMONS | SIMMONS | 5695 | SIMMONS | 0.145 |  |  |  | SOUTH2001 | LIVE OAK | 0.013875 | -0.028359 | 0.0020118 | -0.0041121 |  | 69
CALHSW | CALHSW | 5696 | CALHMSW9 |  |  |  |  | SOUTH2001 | LIVE OAK | 0.014081 | -0.028569 | 0 | 0 |  | 69
S_CALHS | S-CALHS | 5697 | CALHMS 9 | 1.98 |  |  |  | SOUTH2001 | MCMULLEN | 0.014081 | -0.028569 | 0.027881 | -0.056567 |  | 69
NCALHMS | NCALHMS | 5698 | CALHMN 9 | 1.087 |  |  |  | SOUTH2001 | MCMULLEN | 0.014848 | -0.029348 | 0.01614 | -0.031902 |  | 69
CHKPRIS | CHKPRIS | 5699 | CHOKCN 9 | 1.942 |  |  |  | SOUTH2001 | LIVE OAK | 0.014081 | -0.028569 | 0.027346 | -0.055481 |  | 69
TILDENS | TILDENS | 5700 | TILDEN 9 | 2.222 |  |  |  | SOUTH2001 | MCMULLEN | 0.014081 | -0.028569 | 0.031289 | -0.063481 |  | 69
|  | 5701 | USRSTEC3 |  | 30 |  |  | SOUTH2001 | ATASCOSA | 0.016119 | -0.030641 | 0.48358 | -0.91922 |  | 69
SANMGSW | SANMGSW | 5702 | SMIGL 9 |  |  |  |  | SOUTH2001 | ATASCOSA | 0.016119 | -0.030641 | 0 | 0 |  | 69
SANMGSW | SANMGSW | 5704 | SMIGL 8 |  |  |  |  | SOUTH2001 | ATASCOSA | 0.015386 | -0.031028 | 0 | 0 |  | 138
SANMGL8 | SANMGL8 | 5706 | SMDB 8 |  |  |  |  | SOUTH2001 | ATASCOSA | 0.015318 | -0.031006 | 0 | 0 |  | 138
CHARLTS | CHARLTS | 5708 | CHARLT 9 | 3.299 |  |  |  | SOUTH2001 | ATASCOSA | 0.019849 | -0.031759 | 0.065481 | -0.10477 |  | 69
POTEETS | POTEETS | 5710 | POTEET 9 | 6.678 |  |  |  | SOUTH2001 | ATASCOSA | 0.017872 | -0.031146 | 0.11935 | -0.20799 |  | 69
OAKS9 | OAKS9 | 5712 | OAKS 9 | 8.841 |  |  |  | SOUTH2001 | ATASCOSA | 0.016843 | -0.031032 | 0.14891 | -0.27436 |  | 69
OAKS9 | OAKS9 | 5713 | OAKS 8 |  |  |  |  | SOUTH2001 | ATASCOSA | 0.015353 | -0.030868 | 0 | 0 |  | 138
PLSNTOS | PLSNTOS | 5714 | PLSNTN 9 | 9.825 |  |  |  | SOUTH2001 | ATASCOSA | 0.017057 | -0.03058 | 0.16758 | -0.30045 |  | 69
FASHNGS | FASHNGS | 5716 | FASHNG 9 | 4.053 |  |  |  | SOUTH2001 | ATASCOSA | 0.015742 | -0.029668 | 0.063804 | -0.12025 |  | 69
COYCTYS | COYCTYS | 5718 | ROSSVILL | 5.002 |  |  |  | SOUTH2001 | ATASCOSA | 0.015132 | -0.030844 | 0.075691 | -0.15428 |  | 138
COYCTYS | COYCTYS | 5720 | COYCTY 9 | 3.216 |  |  |  | SOUTH2001 | KARNES | 0.014679 | -0.028517 | 0.047208 | -0.09171 |  | 69
KENEDYS | KENEDYS | 5722 | KENEDY 9 | 4.312 |  |  |  | SOUTH2001 | KARNES | 0.013793 | -0.027557 | 0.059475 | -0.11882 |  | 69
FORCRNS | FORCRNS | 5730 | FRCRNR 8 | 3.134 |  |  |  | SOUTH2001 | VICTORIA | 0.0093129 | -0.023018 | 0.029187 | -0.072139 |  | 138
CHARCOS | CHARCOS | 5732 | CHARCO 9 | 1.53 |  |  |  | SOUTH2001 | GOLIAD | 0.012367 | -0.026012 | 0.018922 | -0.039799 |  | 69
MIDWESTS | MIDWESTS | 5735 | MIDWEST | 0.009 |  |  |  | SOUTH2001 | WHARTON | 0.0056208 | -0.017145 | 5.0587e-05 | -0.00015431 |  | 69
FANNINS | FANNINS | 5736 | FAN.CPL2 | 5.843 |  |  |  | SOUTH2001 | GOLIAD | 0.0096205 | -0.023628 | 0.056213 | -0.13806 |  | 69
QUIHIS | QUIHIS | 5804 | QUIHI 9 |  |  |  |  | SOUTH2001 | MEDINA | 0.024562 | -0.033383 | 0 | 0 |  | 69
QUIHISW | QUIHISW | 5805 | QUIHSW9 |  |  |  |  | SOUTH2001 | MEDINA | 0.024562 | -0.033383 | 0 | 0 |  | 69
CASTRSW | CASTRSW | 5807 | CSTRSW9 |  |  |  |  | SOUTH2001 | MEDINA | 0.024562 | -0.033383 | 0 | 0 |  | 69
CASTROS | CASTROS | 5808 | CSTRVL9 | 2.16 |  |  |  | SOUTH2001 | MEDINA | 0.024562 | -0.033383 | 0.053054 | -0.072107 |  | 69
|  | 5810 | BADER | 8.024 |  |  |  | SOUTH2001 | MEDINA | 0.024562 | -0.033383 | 0.19708 | -0.26786 |  | 69
SABINLS | SABINLS | 5812 | SABNAL9 | 2.162 |  |  |  | SOUTH2001 | UVALDE | 0.024562 | -0.033383 | 0.053103 | -0.072173 |  | 69
DHANIS | DHANIS | 5814 | DHANIS9 | 5.011 |  |  |  | SOUTH2001 | MEDINA | 0.024562 | -0.033383 | 0.12308 | -0.16728 |  | 69
HONDOCS | HONDOCS | 5816 | HONDO 9 | 4.252 |  |  |  | SOUTH2001 | MEDINA | 0.024562 | -0.033383 | 0.10444 | -0.14194 |  | 69
FERRISW | FERRISW | 5817 | FERRSW9 |  |  |  |  | SOUTH2001 | UVALDE | 0.04185 | -0.038303 | 0 | 0 |  | 69
FERRIS | FERRIS | 5818 | FERSUB9 | 4.378 |  |  |  | SOUTH2001 | UVALDE | 0.04185 | -0.038303 | 0.18322 | -0.16769 |  | 69
HONDOCK | HONDOCK | 5819 | HNC1388 |  |  |  |  | SOUTH2001 | MEDINA | 0.024562 | -0.033383 | 0 | 0 |  | 138
UVLDES | UVLDES | 5820 | UVALDE9 | 1.893 |  |  |  | SOUTH2001 | UVALDE | 0.04185 | -0.038303 | 0.079221 | -0.072508 |  | 69
HONDOCK | HONDOCK | 5821 | HNCK699 |  |  |  |  | SOUTH2001 | MEDINA | 0.024562 | -0.033383 | 0 | 0 |  | 69
LEONAS | LEONAS | 5822 | LEONA 9 | 1.946 |  |  |  | SOUTH2001 | UVALDE | 0.04185 | -0.038303 | 0.081439 | -0.074538 |  | 69
UVALDSW | UVALDSW | 5823 | UVLDSW9 |  |  |  |  | SOUTH2001 | UVALDE | 0.04185 | -0.038303 | 0 | 0 |  | 69
W_UVALS | W.UVALS | 5824 | W.UVAL9 | 1.024 |  |  |  | SOUTH2001 | UVALDE | 0.04185 | -0.038303 | 0.042854 | -0.039222 |  | 69
MOORES | MOORES | 5827 | MOORE138 |  |  |  |  | SOUTH2001 | FRIO | 0.028105 | -0.034329 | 0 | 0 |  | 138
DEVNES | DEVNES | 5828 | DEVINE9 | 6.969 |  |  |  | SOUTH2001 | MEDINA | 0.025202 | -0.033364 | 0.17563 | -0.23251 |  | 69
MOORES | MOORES | 5830 | MOORE 9 | 1.77 |  |  |  | SOUTH2001 | MEDINA | 0.025202 | -0.033364 | 0.044607 | -0.059054 |  | 69
FRIOTOS | FRIOTOS | 5832 | FRIOTW9 | 2.625 |  |  |  | SOUTH2001 | FRIO | 0.025202 | -0.033364 | 0.066155 | -0.08758 |  | 69
NBATSVS | NBATSVS | 5836 | N.BATS9 | 3.349 |  |  |  | SOUTH2001 | ZAVALA | 0.04185 | -0.038303 | 0.14015 | -0.12828 |  | 69
DERBYS | DERBYS | 5842 | DERBY 9 | 2.948 |  |  |  | SOUTH2001 | FRIO | 0.026873 | -0.033698 | 0.079222 | -0.099343 |  | 69
S_BATES | S-BATES | 5848 | S.BATS9 | 2.785 |  |  |  | SOUTH2001 | ZAVALA | 0.04185 | -0.038303 | 0.11655 | -0.10667 |  | 69
BATESVL | BATESVL | 5849 | BATS699 |  |  |  |  | SOUTH2001 | ZAVALA | 0.04185 | -0.038303 | 0 | 0 |  | 69
BATESVL | BATESVL | 5851 | BATS388 |  |  |  |  | SOUTH2001 | ZAVALA | 0.04185 | -0.038303 | 0 | 0 |  | 138
BIGFOTS | BIGFOTS | 5852 | BIGFOT9 | 2.809 |  |  |  | SOUTH2001 | FRIO | 0.022244 | -0.032477 | 0.062484 | -0.091228 |  | 69
CRSTLSW | CRSTLSW | 5855 | CRCTSW9 |  |  |  |  | SOUTH2001 | ZAVALA | 0.04185 | -0.038303 | 0 | 0 |  | 69
CRSTLS | CRSTLS | 5856 | CRYSUB9 | 0.439 |  |  |  | SOUTH2001 | ZAVALA | 0.04185 | -0.038303 | 0.018372 | -0.016815 |  | 69
DEVINESW | DEVINESW | 5857 | DEVINESW |  |  |  |  | SOUTH2001 | MEDINA | 0.024562 | -0.033383 | 0 | 0 |  | 69
NATALISS | NATALISS | 5858 | NATLSW9 | 3.749 |  |  |  | SOUTH2001 | MEDINA | 0.024562 | -0.033383 | 0.092083 | -0.12515 |  | 69
|  | 5859 | TURTLECK |  |  |  |  | SOUTH2001 | ZAVALA | 0.04185 | -0.038303 | 0 | 0 |  | 69
DILLEYS | DILLEYS | 5860 | DILSUB9 | 4.462 |  |  |  | SOUTH2001 | FRIO | 0.02781 | -0.033886 | 0.12409 | -0.1512 |  | 69
DILLYSTE | DILLYSTE | 5861 | DILLEY8 |  |  |  |  | SOUTH2001 | FRIO | 0.029139 | -0.034152 | 0 | 0 |  | 138
DILLYSTE | DILLYSTE | 5863 | DILLEY9 | 1.617 |  |  |  | SOUTH2001 | FRIO | 0.027911 | -0.033906 | 0.045132 | -0.054826 |  | 69
WCRYSTS | WCRYSTS | 5864 | W.CRYS9 | 1.407 |  |  |  | SOUTH2001 | ZAVALA | 0.04185 | -0.038303 | 0.058882 | -0.053892 |  | 69
BIGWELS | BIGWELS | 5868 | BIGWLS9 | 1.192 |  |  |  | SOUTH2001 | DIMMIT | 0.04185 | -0.038303 | 0.049885 | -0.045657 |  | 69
BRUNDGS | BRUNDGS | 5870 | BRUND 9 | 0.819 |  |  |  | SOUTH2001 | DIMMIT | 0.04185 | -0.038303 | 0.034275 | -0.03137 |  | 69
CARIZOS | CARIZOS | 5872 | CRZSPS9 | 1.489 |  |  |  | SOUTH2001 | DIMMIT | 0.04185 | -0.038303 | 0.062314 | -0.057033 |  | 69
COTULAS | COTULAS | 5876 | COTULA9 | 1.05 |  |  |  | SOUTH2001 | LASALLE | 0.027911 | -0.033906 | 0.029307 | -0.035601 |  | 69
HOLANDS | HOLANDS | 5878 | HOLAND9 | 2.068 |  |  |  | SOUTH2001 | LASALLE | 0.027911 | -0.033906 | 0.05772 | -0.070118 |  | 69
FREERS | FREERS | 5880 | FREER 9 | 1.237 |  |  |  | SOUTH2001 | WEBB | 0.021072 | -0.028894 | 0.026066 | -0.035742 |  | 69
BRUNI | BRUNI | 5887 | BRUNI 8 |  |  |  |  | SOUTH2001 | WEBB | 0.021072 | -0.028894 | 0 | 0 |  | 138
BRUNI | BRUNI | 5888 | BRUNI 9 | 1.771 |  |  |  | SOUTH2001 | WEBB | 0.021072 | -0.028894 | 0.037319 | -0.051172 |  | 69
PEARSALL | PEARSALL | 5890 | PRSGN1 |  |  | 14.195 | 24 | SOUTH2001 | FRIO | 0.025202 | -0.033364 | 0.60485 | -0.80073 |  | 13
PEARSALL | PEARSALL | 5891 | PRSGN2 |  |  | 21.812 | 23 | SOUTH2001 | FRIO | 0.025202 | -0.033364 | 0.57964 | -0.76737 |  | 13
PEARSALL | PEARSALL | 5892 | PRSGN3 |  |  | 21.812 | 23 | SOUTH2001 | FRIO | 0.025202 | -0.033364 | 0.57964 | -0.76737 |  | 13
PEARSALL | PEARSALL | 5893 | PRSL699 |  |  |  |  | SOUTH2001 | FRIO | 0.025202 | -0.033364 | 0 | 0 |  | 69
PEARSALL | PEARSALL | 5895 | PRS1388 | 3.853 |  |  |  | SOUTH2001 | FRIO | 0.028299 | -0.03442 | 0.10904 | -0.13262 |  | 138
|  | 5901 | MIGUEL 5 |  |  |  |  | SOUTH2001 | ATASCOSA | 0.012557 | -0.031221 | 0 | 0 |  | 345
SANMIGL | SANMIGL | 5902 | MIGUEL 8 |  |  |  |  | SOUTH2001 | ATASCOSA | 0.015258 | -0.031007 | 0 | 0 |  | 138
|  | 5903 | MIGUEL |  |  | 391.723 | 395 | SOUTH2001 | ATASCOSA | 0.012557 | -0.031221 | 4.9602 | -12.3324 |  | 22.8
STP | STP | 5911 | STP1 |  |  | 1250 | 1250 | SOUTH2001 | MATAGORDA | 0.0042532 | -0.013699 | 5.3165 | -17.1242 |  | 25
STP | STP | 5912 | STP2 |  |  | 1250 | 1250 | SOUTH2001 | MATAGORDA | 0.0042532 | -0.013699 | 5.3165 | -17.1242 |  | 25
STP | STP | 5915 | SO TEX 5 |  |  |  |  | SOUTH2001 | MATAGORDA | 0.0042532 | -0.013699 | 0 | 0 |  | 345
SILASRAY | SILASRAY | 5930 | PWRPLANT | 20.9 |  |  |  | SOUTH2001 | CAMERON | 0.01112 | -0.02432 | 0.23242 | -0.50829 |  | 69
SILASRAY | SILASRAY | 5932 | SI RAY9 |  |  | 43.703 | 43 | SOUTH2001 | CAMERON | 0.01112 | -0.02432 | 0.47818 | -1.0458 |  | 13.8
SILASRAY | SILASRAY | 5933 | SI RAY6 |  |  | 15 | 22 | SOUTH2001 | CAMERON | 0.01112 | -0.02432 | 0.24465 | -0.53504 |  | 13.8
SILASRAY | SILASRAY | 5934 | SI RAY5 |  | 21 |  |  | SOUTH2001 | CAMERON | 0.01112 | -0.02432 | 0.23353 | -0.51072 |  | 12.5
SILASRAY | SILASRAY | 5935 | SI RAY8 |  | 48 |  |  | SOUTH2001 | CAMERON | 0.01112 | -0.02432 | 0.53378 | -1.1674 |  | 13.8
802_SUB | 802 SUB | 5940 | FM 802 | 23.1 |  |  |  | SOUTH2001 | CAMERON | 0.01112 | -0.02432 | 0.25688 | -0.56179 |  | 69
PRICE_RD | PRICE RD | 5941 | PRICE RD | 22.09 |  |  |  | SOUTH2001 | CAMERON | 0.01112 | -0.02432 | 0.24565 | -0.53722 |  | 69
FILTER_P | FILTER P | 5942 | FILTER P | 21.91 |  |  |  | SOUTH2001 | CAMERON | 0.01112 | -0.02432 | 0.24364 | -0.53285 |  | 69
LOMA ALT | LOMA ALT | 5943 | LOMAALTA |  |  |  |  | SOUTH2001 | CAMERON | 0.01112 | -0.02432 | 0 | 0 |  | 69
UNION_CA | UNION CA | 5944 | CARBIDE | 4.4 |  |  |  | SOUTH2001 | CAMERON | 0.01112 | -0.02432 | 0.048928 | -0.10701 |  | 69
WATERPOR | WATERPOR | 5945 | WATERPRT | 6.6 |  |  |  | SOUTH2001 | CAMERON | 0.01112 | -0.02432 | 0.073392 | -0.16051 |  | 69
AIRPORT | AIRPORT | 5946 | AIRPORT | 25.21 |  |  |  | SOUTH2001 | CAMERON | 0.01112 | -0.02432 | 0.28034 | -0.6131 |  | 69
FORT_BRO | FORT BRO | 5947 | FT BROWN | 25.39 |  |  |  | SOUTH2001 | CAMERON | 0.01112 | -0.02432 | 0.28235 | -0.61748 |  | 69
SIXTH_ST | SIXTH ST | 5948 | 6TH ST | 24.2 |  |  |  | SOUTH2001 | CAMERON | 0.01112 | -0.02432 | 0.26911 | -0.58854 |  | 69
MIDTOWN | MIDTOWN | 5949 | MIDTOWN | 20.9 |  |  |  | SOUTH2001 | CAMERON | 0.01112 | -0.02432 | 0.23242 | -0.50829 |  | 69
MILHWY | MILHWY | 5960 | MIL HWY |  |  |  |  | SOUTH2001 | CAMERON | 0.011121 | -0.02432 | 0 | 0 |  | 69
LAREDO1 | LAREDO1 | 5961 | LAREDO |  |  |  |  | SOUTH2001 | CAMERON | 0.011121 | -0.02432 | 0 | 0 |  | 69
LOMA ALT | LOMA ALT | 5962 | LOMA 138 |  |  |  |  | SOUTH2001 | CAMERON | 0.01112 | -0.024319 | 0 | 0 |  | 138
TITAN_SU | TITAN SU | 5963 | TITAN | 3 |  |  |  | SOUTH2001 | CAMERON | 0.01112 | -0.02432 | 0.03336 | -0.072959 |  | 138
MILHWY | MILHWY | 5964 | MILH DUM | 25.3 |  |  |  | SOUTH2001 | CAMERON | 0.011121 | -0.02432 | 0.28136 | -0.6153 |  | 138
ESTL | ESTL | 6023 | ESTEL2WT |  |  |  |  | SOUTH2001 | HALL | 0 | 0 | 0 | 0 |  | 69
CSSB | CSSB | 6386 | CSANSAB2 | 4.93 |  |  |  | SOUTH2001 | MCCULLOCH | 0.10872 | -0.06563 | 0.53601 | -0.32356 |  | 69
FREDPHIL | FREDPHIL | 6387 | FREDKPH2 | 0.414 |  |  |  | SOUTH2001 | GILLESPIE | 0.055287 | -0.050405 | 0.022889 | -0.020868 |  | 69
FTMA | FTMA | 6388 | MASON 2 | 5.55 |  |  |  | SOUTH2001 | MASON | 0.09111 | -0.060815 | 0.50566 | -0.33752 |  | 69
FRDN | FRDN | 6389 | LCRAFRED | 1.81 |  |  |  | SOUTH2001 | MASON | 0.086084 | -0.05974 | 0.15581 | -0.10813 |  | 69
FTMA | FTMA | 6390 | MASON4 |  |  |  |  | SOUTH2001 | MASON | 0.089741 | -0.059962 | 0 | 0 |  | 138
FRDN | FRDN | 6391 | FRDONIT2 | 3.21 |  |  |  | SOUTH2001 | MASON | 0.086084 | -0.05974 | 0.27633 | -0.19176 |  | 69
PHMT | PHMT | 6392 | FREDPHT2 |  |  |  |  | SOUTH2001 | GILLESPIE | 0.055287 | -0.050405 | 0 | 0 |  | 69
MASN | MASN | 6393 | WTUMASN2 |  |  |  |  | SOUTH2001 | MASON | 0.09137 | -0.060882 | 0 | 0 |  | 69
PHMA | PHMA | 6394 | MASNPHT2 |  |  |  |  | SOUTH2001 | MASON | 0.10664 | -0.064955 | 0 | 0 |  | 69
PHMA | PHMA | 6395 | MASNPH 2 | 0.432 |  |  |  | SOUTH2001 | MASON | 0.10664 | -0.064955 | 0.046068 | -0.02806 |  | 69
MASW | MASW | 6396 | MASONSW2 |  |  |  |  | SOUTH2001 | MASON | 0.10704 | -0.06506 | 0 | 0 |  | 69
STRT | STRT | 6397 | STRETER2 | 1.09 |  |  |  | SOUTH2001 | MASON | 0.109 | -0.065586 | 0.11881 | -0.071488 |  | 69
PAW2 | PAW2 | 6491 | PAVEPAW2 |  |  |  |  | SOUTH2001 | SCHLEICHER | 0 | 0 | 0 | 0 |  | 69
PAVE | PAVE | 6492 | PAVEPAW4 |  |  |  |  | SOUTH2001 | SCHLEICHER | 0 | 0 | 0 | 0 |  | 138
|  | 6568 | RGECBVIL |  |  |  |  | SOUTH2001 | KINNEY | 0.085739 | -0.051769 | 0 | 0 |  | 138
|  | 6570 | RGEC-EPS |  |  |  |  | SOUTH2001 | MAVERICK | 0.078786 | -0.049403 | 0 | 0 |  | 138
OKWDWT4 | OKWDWT4 | 6711 | OKWD WT4 | 1.169 |  |  |  | SOUTH2001 | FREESTONE | -0.0094185 | -0.062932 | -0.01101 | -0.073568 |  | 138
PLSTWT4 | PLSTWT4 | 6736 | PLST WT4 | 8.24 |  |  |  | SOUTH2001 | LEON | -0.0068879 | -0.0088288 | -0.056757 | -0.07275 |  | 138
CTVLWT4 | CTVLWT4 | 6738 | CTVL WT4 | 5.058 |  |  |  | SOUTH2001 | LEON | -0.0067692 | -0.0063041 | -0.034238 | -0.031886 |  | 138
CARY | CARY | 6739 | CARYLK 2 | 5.25 |  |  |  | SOUTH2001 | CHEROKEE | 0 | 0 | 0 | 0 |  | 69
|  | 6935 | LKVEW RC | 4.855 |  |  |  | SOUTH2001 | ANDERSON | -0.0097618 | -0.068742 | -0.047394 | -0.33374 |  | 138
|  | 6937 | TCKER RC |  |  |  |  | SOUTH2001 | ANDERSON | -0.0097618 | -0.068742 | 0 | 0 |  | 138
MSYLK_RC | MSYLK RC | 6940 | MSYLK RC | 2.467 |  |  |  | SOUTH2001 | ANDERSON | -0.0097752 | -0.072572 | -0.024116 | -0.17904 |  | 138
WCTYHRN2 | WCTYHRN2 | 6950 | WCTYHRN2 | 13 |  |  |  | SOUTH2001 | ROBERTSON | -0.0031723 | -0.012669 | -0.04124 | -0.1647 |  | 69
FERGUS | FERGUS | 7000 | FERGUSG1 |  |  | 388.125 | 420 | SOUTH2001 | LLANO | 0.020739 | -0.044384 | 8.7104 | -18.6415 |  | 22.8
GIDEON | GIDEON | 7004 | GIDEONG1 |  |  | 139 | 140 | SOUTH2001 | BASTROP | 0.0072659 | -0.03541 | 1.0172 | -4.9574 |  | 17.2
GIDEON | GIDEON | 7005 | GIDEONG2 |  |  | 139 | 140 | SOUTH2001 | BASTROP | 0.0072659 | -0.03541 | 1.0172 | -4.9574 |  | 17.2
GIDEON | GIDEON | 7006 | GIDEONG3 |  |  | 342 | 342 | SOUTH2001 | BASTROP | 0.0072659 | -0.03541 | 2.485 | -12.1102 |  | 20.9
LOSTPI | LOSTPI | 7007 | LOSTPN 1 |  |  | 167 | 250 | SOUTH2001 | BASTROP | 0.0063115 | -0.035624 | 1.5779 | -8.906 |  | 18
LOSTPI | LOSTPI | 7008 | LOSTPN 2 |  |  | 118 | 250 | SOUTH2001 | BASTROP | 0.0063115 | -0.035624 | 1.5779 | -8.906 |  | 18
LOSTPI | LOSTPI | 7009 | LOSTPN 3 |  | 250 |  |  | SOUTH2001 | BASTROP | 0.0063115 | -0.035624 | 1.5779 | -8.906 |  | 18
FPPYD1 | FPPYD1 | 7010 | FPP G1 |  |  | 584 | 584 | SOUTH2001 | FAYETTE | 0.0064674 | -0.032535 | 3.777 | -19.0002 |  | 22.8
FPPYD1 | FPPYD1 | 7011 | FPP G2 |  |  | 584 | 584 | SOUTH2001 | FAYETTE | 0.0064674 | -0.032535 | 3.777 | -19.0002 |  | 22.8
FPPYD1 | FPPYD1 | 7012 | FPP G3 |  |  | 449.9 | 449.9 | SOUTH2001 | FAYETTE | 0.0064714 | -0.03251 | 2.9115 | -14.626 |  | 26.6
HAYSEN | HAYSEN | 7014 | HAYSN 1 |  | 275 |  |  | SOUTH2001 | HAYS | 0.0094588 | -0.033225 | 2.6012 | -9.137 |  | 21
HAYSEN | HAYSEN | 7015 | HAYSN 2 |  | 275 |  |  | SOUTH2001 | HAYS | 0.0094588 | -0.033225 | 2.6012 | -9.137 |  | 21
HAYSEN | HAYSEN | 7016 | HAYSN 3 |  | 275 |  |  | SOUTH2001 | HAYS | 0.0094588 | -0.033225 | 2.6012 | -9.137 |  | 21
HAYSEN | HAYSEN | 7017 | HAYSN 4 |  | 275 |  |  | SOUTH2001 | HAYS | 0.0094588 | -0.033225 | 2.6012 | -9.137 |  | 21
AUSTPL | AUSTPL | 7020 | AUSTING1 |  |  | 17.3 | 17.3 | SOUTH2001 | TRAVIS | 0.0083607 | -0.037765 | 0.14464 | -0.65333 |  | 11.5
BUCHAN | BUCHAN | 7022 | BUCHANG1 |  |  | 18.2 | 18.5 | SOUTH2001 | LLANO | 0.027844 | -0.048579 | 0.51511 | -0.89872 |  | 6.9
BUCHAN | BUCHAN | 7023 | BUCHANG2 |  |  | 18.2 | 18.5 | SOUTH2001 | LLANO | 0.017291 | -0.046532 | 0.31988 | -0.86085 |  | 6.9
BUCHAN | BUCHAN | 7024 | BUCHANG3 |  |  | 14.9 | 14.9 | SOUTH2001 | LLANO | 0.022474 | -0.047538 | 0.33487 | -0.70831 |  | 6.9
INKSDA | INKSDA | 7026 | INKS G1 |  |  | 14 | 14 | SOUTH2001 | BURNET | 0.027844 | -0.048579 | 0.38981 | -0.68011 |  | 6.9
MARBFA | MARBFA | 7028 | MARBFAG1 |  |  | 18.5 | 18.5 | SOUTH2001 | BURNET | 0.017685 | -0.042761 | 0.32717 | -0.79107 |  | 6.9
MARBFA | MARBFA | 7029 | MARBFAG2 |  |  | 18.5 | 18.5 | SOUTH2001 | BURNET | 0.017685 | -0.042761 | 0.32717 | -0.79107 |  | 6.9
MARSFO | MARSFO | 7031 | MARSFOG1 |  |  | 36 | 36 | SOUTH2001 | TRAVIS | 0.011338 | -0.039386 | 0.40817 | -1.4179 |  | 13.8
MARSFO | MARSFO | 7032 | MARSFOG2 |  |  | 30 | 30 | SOUTH2001 | TRAVIS | 0.011338 | -0.039386 | 0.34014 | -1.1816 |  | 13.8
MARSFO | MARSFO | 7033 | MARSFOG3 |  |  | 36 | 36 | SOUTH2001 | TRAVIS | 0.011338 | -0.039386 | 0.40817 | -1.4179 |  | 13.8
WIRTZ | WIRTZ | 7035 | WIRTZ G1 |  |  | 28 | 28 | SOUTH2001 | BURNET | 0.019723 | -0.044297 | 0.55224 | -1.2403 |  | 13.8
WIRTZ | WIRTZ | 7036 | WIRTZ G2 |  |  | 28 | 28 | SOUTH2001 | BURNET | 0.019723 | -0.044297 | 0.55224 | -1.2403 |  | 13.8
|  | 7038 | TWPP G1 |  |  | 27.5 | 35 | SOUTH2001 | CULBERSON | 0.28609 | -0.1105 | 10.0133 | -3.8675 |  | 34.5
AUSTRO | AUSTRO | 7040 | AUSTRO34 |  |  |  |  | SOUTH2001 | TRAVIS | 0.0062356 | -0.036986 | 0 | 0 |  | 345
LOSTPINE | LOSTPINE | 7041 | LOSTPN34 |  |  |  |  | SOUTH2001 | BASTROP | 0.0063115 | -0.035624 | 0 | 0 |  | 345
ZORN | ZORN | 7042 | ZORN 34 |  |  |  |  | SOUTH2001 | GUADALUPE | 0.0094066 | -0.033203 | 0 | 0 |  | 345
HAYSEN | HAYSEN | 7043 | HAYSN 34 |  |  |  |  | SOUTH2001 | HAYS | 0.0094588 | -0.033225 | 0 | 0 |  | 345
MARION | MARION | 7044 | MARION34 |  |  |  |  | SOUTH2001 | GUADALUPE | 0.010147 | -0.031413 | 0 | 0 |  | 345
ZORN | ZORN | 7045 | ZORN 34 |  |  |  |  | SOUTH2001 | GUADALUPE | 0.0093996 | -0.033205 | 0 | 0 |  | 345
KENDAL | KENDAL | 7046 | KENDAL34 |  |  |  |  | SOUTH2001 | KENDALL | 0.01383 | -0.035129 | 0 | 0 |  | 345
GARFIE | GARFIE | 7048 | GARFIE34 |  |  |  |  | SOUTH2001 | BASTROP | 0.0069122 | -0.035964 | 0 | 0 |  | 345
FPPYD1 | FPPYD1 | 7055 | FPPYD234 |  |  |  |  | SOUTH2001 | FAYETTE | 0.0064714 | -0.03251 | 0 | 0 |  | 345
FPPYD1 | FPPYD1 | 7056 | FPPYD134 |  |  |  |  | SOUTH2001 | FAYETTE | 0.0064674 | -0.032535 | 0 | 0 |  | 345
FAYETT | FAYETT | 7057 | FAYETT34 |  |  |  |  | SOUTH2001 | FAYETTE | 0.0064338 | -0.032156 | 0 | 0 |  | 345
SALEM | SALEM | 7058 | SALEM 34 |  |  |  |  | SOUTH2001 | WASHINGTON | 0.0063937 | -0.031945 | 0 | 0 |  | 345
EBABES | EBABES | 7060 | EBABES13 | 4.085 |  |  |  | SOUTH2001 | BURNET | 0.016526 | -0.052694 | 0.06751 | -0.21525 |  | 138
COPPCV | COPPCV | 7061 | COPPCV13 | 14.441 |  |  |  | SOUTH2001 | LAMPASAS | 0.015594 | -0.054463 | 0.2252 | -0.78649 |  | 138
KEMPNE | KEMPNE | 7062 | KEMPNE13 | 5.528 |  |  |  | SOUTH2001 | LAMPASAS | 0.015594 | -0.054463 | 0.086205 | -0.30107 |  | 138
LAMPAS | LAMPAS | 7064 | LAMPAS13 | 21.992 |  |  |  | SOUTH2001 | LAMPASAS | 0.015594 | -0.054463 | 0.34295 | -1.1977 |  | 138
ADAMSV | ADAMSV | 7066 | ADAMSV13 | 3.342 |  |  |  | SOUTH2001 | LAMPASAS | 0.01354 | -0.060093 | 0.04525 | -0.20083 |  | 138
EVANT | EVANT | 7068 | EVANT 13 | 5.477 |  |  |  | SOUTH2001 | LAMPASAS | 0.010429 | -0.068617 | 0.057122 | -0.37581 |  | 138
GOLDTH | GOLDTH | 7070 | GOLDTH13 | 9.649 |  |  |  | SOUTH2001 | MILLS | 0.006062 | -0.080585 | 0.058492 | -0.77757 |  | 138
GOLDTH | GOLDTH | 7073 | GOLDTH06 |  |  |  |  | SOUTH2001 | MILLS | 0.0083741 | -0.074249 | 0 | 0 |  | 69
SANSAS | SANSAS | 7074 | SANSAS06 |  |  |  |  | SOUTH2001 | SAN SABA | 0.010118 | -0.069471 | 0 | 0 |  | 69
TERRY | TERRY | 7075 | TERRY 06 | 0.719 |  |  |  | SOUTH2001 | SAN SABA | 0.010118 | -0.069471 | 0.0072747 | -0.049949 |  | 69
RICHSP | RICHSP | 7076 | RICHSP06 | 3.293 |  |  |  | SOUTH2001 | SAN SABA | 0.010118 | -0.069471 | 0.033318 | -0.22877 |  | 69
SANSAB | SANSAB | 7078 | SANSAB06 |  |  |  |  | SOUTH2001 | SAN SABA | 0.010494 | -0.068441 | 0 | 0 |  | 69
LOMETA | LOMETA | 7080 | LOMETA06 | 4.6 |  |  |  | SOUTH2001 | LAMPASAS | 0.012529 | -0.062863 | 0.057632 | -0.28917 |  | 69
LAMPAS | LAMPAS | 7082 | LAMPAS06 |  |  |  |  | SOUTH2001 | LAMPASAS | 0.014265 | -0.058106 | 0 | 0 |  | 69
GRAPMI | GRAPMI | 7084 | GRAPMI13 | 6.078 |  |  |  | SOUTH2001 | BURNET | 0.016934 | -0.0482 | 0.10293 | -0.29296 |  | 138
BUCHAN | BUCHAN | 7086 | BUCHAN13 |  |  |  |  | SOUTH2001 | LLANO | 0.017291 | -0.046532 | 0 | 0 |  | 138
BUCHAN | BUCHAN | 7089 | BUCHANN3 |  |  |  |  | SOUTH2001 | LLANO | 0.022474 | -0.047538 | 0 | 0 |  | 0
BUCHAN | BUCHAN | 7092 | BUCHAN06 |  |  |  |  | SOUTH2001 | LLANO | 0.027844 | -0.048579 | 0 | 0 |  | 69
INKSDA | INKSDA | 7094 | INKSDA06 | 2.829 |  |  |  | SOUTH2001 | BURNET | 0.027844 | -0.048579 | 0.07877 | -0.13743 |  | 69
BURNET | BURNET | 7097 | BURNET06 | 9.114 |  |  |  | SOUTH2001 | BURNET | 0.023891 | -0.048535 | 0.21774 | -0.44234 |  | 69
BURNET | BURNET | 7100 | BURNET13 | 13.384 |  |  |  | SOUTH2001 | BURNET | 0.018749 | -0.048477 | 0.25093 | -0.64881 |  | 138
CTECBU | CTECBU | 7101 | CTECBU06 | 5.185 |  |  |  | SOUTH2001 | LLANO | 0.029455 | -0.048726 | 0.15273 | -0.25264 |  | 69
SHERSH | SHERSH | 7102 | SHERSH13 | 12.983 |  |  |  | SOUTH2001 | BURNET | 0.019239 | -0.045319 | 0.24978 | -0.58837 |  | 138
WIRTZ | WIRTZ | 7104 | WIRTZ 13 |  |  |  |  | SOUTH2001 | BURNET | 0.019723 | -0.044297 | 0 | 0 |  | 138
WIRTZ | WIRTZ | 7107 | WIRTZ 06 | 13.229 |  |  |  | SOUTH2001 | BURNET | 0.019723 | -0.044297 | 0.26091 | -0.586 |  | 69
WIRTZ | WIRTZ | 7110 | WIRTZ N1 |  |  |  |  | SOUTH2001 | BURNET | 0.019723 | -0.044297 | 0 | 0 |  | 0
FLATRO | FLATRO | 7111 | FLATRO13 | 6.724 |  |  |  | SOUTH2001 | BURNET | 0.017323 | -0.042891 | 0.11648 | -0.2884 |  | 138
WIRTZ | WIRTZ | 7112 | WIRTZ N2 |  |  |  |  | SOUTH2001 | BURNET | 0.019723 | -0.044297 | 0 | 0 |  | 0
CASTEL | CASTEL | 7114 | CASTEL06 | 1.787 |  |  |  | SOUTH2001 | LLANO | 0.065143 | -0.055258 | 0.11641 | -0.098746 |  | 69
SANDMO | SANDMO | 7116 | SANDMO06 |  |  |  |  | SOUTH2001 | LLANO | 0.035516 | -0.049276 | 0 | 0 |  | 69
PITSBU | PITSBU | 7119 | PITSBU06 |  |  |  |  | SOUTH2001 | LLANO | 0.038424 | -0.04954 | 0 | 0 |  | 69
PITSBU | PITSBU | 7120 | PITSBU13 | 16.606 |  |  |  | SOUTH2001 | LLANO | 0.026667 | -0.046112 | 0.44283 | -0.76574 |  | 138
ECKERT | ECKERT | 7122 | ECKERT06 | 0.068 |  |  |  | SOUTH2001 | GILLESPIE | 0.042564 | -0.046711 | 0.0028944 | -0.0031764 |  | 69
NEBO | NEBO | 7124 | NEBO 06 | 0.732 |  |  |  | SOUTH2001 | GILLESPIE | 0.042564 | -0.046711 | 0.031157 | -0.034193 |  | 69
FERGUS | FERGUS | 7126 | FERGUS13 |  |  |  |  | SOUTH2001 | LLANO | 0.020739 | -0.044384 | 0 | 0 |  | 138
HORSBA | HORSBA | 7128 | HORSBA13 | 13.121 |  |  |  | SOUTH2001 | LLANO | 0.021673 | -0.044385 | 0.28438 | -0.58238 |  | 138
GILLES | GILLES | 7130 | GILLES06 |  |  |  |  | SOUTH2001 | GILLESPIE | 0.042564 | -0.046711 | 0 | 0 |  | 69
GILLES | GILLES | 7132 | GILLES13 |  |  |  |  | SOUTH2001 | GILLESPIE | 0.034136 | -0.044395 | 0 | 0 |  | 138
NIMITZ | NIMITZ | 7133 | NIMITZ13 | 18.565 |  |  |  | SOUTH2001 | GILLESPIE | 0.034136 | -0.044395 | 0.63374 | -0.82418 |  | 138
WOLFCR | WOLFCR | 7134 | WOLFCR13 | 6.758 |  |  |  | SOUTH2001 | KERR | 0.026895 | -0.040999 | 0.18176 | -0.27707 |  | 138
KERRST | KERRST | 7136 | KERRST06 |  |  |  |  | SOUTH2001 | KERR | 0.022891 | -0.039103 | 0 | 0 |  | 69
KERRST | KERRST | 7138 | KERRST13 | 24.129 |  |  |  | SOUTH2001 | KERR | 0.024207 | -0.039739 | 0.5841 | -0.95886 |  | 138
HARPRO | HARPRO | 7140 | HARPRO13 | 18.482 |  |  |  | SOUTH2001 | KERR | 0.024126 | -0.0397 | 0.44589 | -0.73373 |  | 138
INGRAM | INGRAM | 7142 | INGRAM13 | 13.645 |  |  |  | SOUTH2001 | KERR | 0.0238 | -0.039542 | 0.32476 | -0.53956 |  | 138
RIMROC | RIMROC | 7143 | RIMROC13 | 16.4 |  |  |  | SOUTH2001 | KERR | 0.022854 | -0.039085 | 0.3748 | -0.641 |  | 138
HUNT | HUNT | 7144 | HUNT 13 | 6.262 |  |  |  | SOUTH2001 | KERR | 0.023475 | -0.039385 | 0.147 | -0.24663 |  | 138
VERDCR | VERDCR | 7146 | VERDCR13 |  |  |  |  | SOUTH2001 | KERR | 0.022335 | -0.038834 | 0 | 0 |  | 138
KENDCT | KENDCT | 7147 | KENDCT13 | 4.704 |  |  |  | SOUTH2001 | KENDALL | 0.019964 | -0.037807 | 0.093913 | -0.17784 |  | 138
MOUNTO | MOUNTO | 7148 | MOUNTO13 |  |  |  |  | SOUTH2001 | BLANCO | 0.017282 | -0.039847 | 0 | 0 |  | 138
FREDER | FREDER | 7149 | FREDER13 | 16.876 |  |  |  | SOUTH2001 | GILLESPIE | 0.032406 | -0.043539 | 0.54688 | -0.73477 |  | 138
KENDAL | KENDAL | 7150 | KENDAL13 |  |  |  |  | SOUTH2001 | KENDALL | 0.019971 | -0.037802 | 0 | 0 |  | 138
CICO | CICO | 7151 | CICO 13 | 9.904 |  |  |  | SOUTH2001 | KENDALL | 0.015768 | -0.034051 | 0.15617 | -0.33724 |  | 138
KENDAL | KENDAL | 7152 | KENDAL13 |  |  |  |  | SOUTH2001 | KENDALL | 0.019953 | -0.037786 | 0 | 0 |  | 138
WELFAR | WELFAR | 7153 | WELFAR13 | 7.592 |  |  |  | SOUTH2001 | KENDALL | 0.018157 | -0.036985 | 0.13785 | -0.28079 |  | 138
COMFOR | COMFOR | 7154 | COMFOR06 |  |  |  |  | SOUTH2001 | KENDALL | 0.021081 | -0.038229 | 0 | 0 |  | 69
COMFOR | COMFOR | 7155 | COMFOR13 |  |  |  |  | SOUTH2001 | KENDALL | 0.019889 | -0.037653 | 0 | 0 |  | 138
CYPRCR | CYPRCR | 7156 | CYPRCR06 | 9.91 |  |  |  | SOUTH2001 | KENDALL | 0.021248 | -0.038309 | 0.21056 | -0.37964 |  | 69
CENTPO | CENTPO | 7158 | CENTPO06 | 3.767 |  |  |  | SOUTH2001 | KERR | 0.02198 | -0.038663 | 0.082797 | -0.14564 |  | 69
LEGION | LEGION | 7160 | LEGION06 | 11.679 |  |  |  | SOUTH2001 | KERR | 0.022396 | -0.038864 | 0.26156 | -0.45389 |  | 69
TRAVIS | TRAVIS | 7162 | TRAVIS06 | 13.669 |  |  |  | SOUTH2001 | KERR | 0.022752 | -0.039036 | 0.311 | -0.53358 |  | 69
BOERNE | BOERNE | 7168 | BOERNE13 | 32.884 |  |  |  | SOUTH2001 | KENDALL | 0.016386 | -0.036195 | 0.53882 | -1.1902 |  | 138
FAIROA | FAIROA | 7169 | FAIROA13 | 9.651 |  |  |  | SOUTH2001 | KENDALL | 0.014988 | -0.035572 | 0.14465 | -0.34331 |  | 138
BERGHE | BERGHE | 7170 | BERGHE13 | 7.811 |  |  |  | SOUTH2001 | COMAL | 0.014238 | -0.035238 | 0.11121 | -0.27524 |  | 138
ANTLER | ANTLER | 7171 | ANTLER13 | 9.621 |  |  |  | SOUTH2001 | KENDALL | 0.012416 | -0.034338 | 0.11946 | -0.33036 |  | 138
HENNE | HENNE | 7172 | HENNE 13 |  |  |  |  | SOUTH2001 | COMAL | 0.010381 | -0.033332 | 0 | 0 |  | 138
RIVEOA | RIVEOA | 7173 | RIVERO13 | 5.17 |  |  |  | SOUTH2001 | COMAL | 0.010716 | -0.033498 | 0.055403 | -0.17318 |  | 138
HENNE | HENNE | 7174 | HENNE 13 |  |  |  |  | SOUTH2001 | COMAL | 0.010015 | -0.033074 | 0 | 0 |  | 138
HORTON | HORTON | 7175 | HORTON13 | 24.031 |  |  |  | SOUTH2001 | COMAL | 0.010199 | -0.032737 | 0.2451 | -0.78671 |  | 138
COMAL | COMAL | 7176 | COMAL 13 | 43.688 |  |  |  | SOUTH2001 | COMAL | 0.010213 | -0.032792 | 0.44618 | -1.4326 |  | 138
MARION | MARION | 7178 | MARION13 |  |  |  |  | SOUTH2001 | GUADALUPE | 0.010307 | -0.031768 | 0 | 0 |  | 138
ZORN | ZORN | 7180 | ZORN 13 |  |  |  |  | SOUTH2001 | GUADALUPE | 0.0098517 | -0.033306 | 0 | 0 |  | 138
ZORN | ZORN | 7181 | ZORN 13 |  |  |  |  | SOUTH2001 | GUADALUPE | 0.0098528 | -0.033306 | 0 | 0 |  | 138
MCCALA | MCCALA | 7182 | MCCALA13 | 16.935 |  |  |  | SOUTH2001 | HAYS | 0.0099963 | -0.033534 | 0.16929 | -0.56789 |  | 138
MCCALA | MCCALA | 7184 | MCCALA13 |  |  |  |  | SOUTH2001 | HAYS | 0.0099976 | -0.033534 | 0 | 0 |  | 138
RNRD12 | RNRD12 | 7186 | RNRD1213 | 21.851 |  |  |  | SOUTH2001 | HAYS | 0.0098939 | -0.033757 | 0.21619 | -0.73763 |  | 138
REDWOO | REDWOO | 7188 | REDWOO13 | 23.25 |  |  |  | SOUTH2001 | HAYS | 0.0098931 | -0.033761 | 0.23001 | -0.78493 |  | 138
HILLTO | HILLTO | 7190 | HILLTO13 | 12.68 |  |  |  | SOUTH2001 | HAYS | 0.0098344 | -0.033887 | 0.1247 | -0.42969 |  | 138
SANMAR | SANMAR | 7192 | SANMAR13 | 27.583 |  |  |  | SOUTH2001 | HAYS | 0.009804 | -0.033954 | 0.27042 | -0.93654 |  | 138
STRAHAN | STRAHAN | 7193 | STRAHA13 | 13.635 |  |  |  | SOUTH2001 | HAYS | 0.0098221 | -0.033914 | 0.13392 | -0.46242 |  | 138
REEDVI | REEDVI | 7194 | REEDVI06 |  |  |  |  | SOUTH2001 | CALDWELL | 0.009272 | -0.03397 | 0 | 0 |  | 69
CAMPGA | CAMPGA | 7196 | CAMPGA06 | 4.647 |  |  |  | SOUTH2001 | CALDWELL | 0.0093044 | -0.034002 | 0.043238 | -0.15801 |  | 69
CANYON | CANYON | 7199 | CANYON06 |  |  |  |  | SOUTH2001 | HAYS | 0.0094794 | -0.034171 | 0 | 0 |  | 69
CANYON | CANYON | 7200 | CANYON13 |  |  |  |  | SOUTH2001 | HAYS | 0.0096346 | -0.034321 | 0 | 0 |  | 138
HICROS | HICROS | 7202 | HICROS13 |  |  |  |  | SOUTH2001 | TRAVIS | 0.0084905 | -0.036822 | 0 | 0 |  | 138
DUMPHI | DUMPHI | 7204 | DUMPHI06 |  |  |  |  | SOUTH2001 | CALDWELL | 0.0089353 | -0.033645 | 0 | 0 |  | 69
DALE | DALE | 7206 | DALE 06 | 3.825 |  |  |  | SOUTH2001 | CALDWELL | 0.0089353 | -0.033645 | 0.034177 | -0.12869 |  | 69
COLTON | COLTON | 7208 | COLTON13 | 7.64 |  |  |  | SOUTH2001 | TRAVIS | 0.0082636 | -0.035442 | 0.063134 | -0.27077 |  | 138
WOLFLA | WOLFLA | 7212 | WOLFLA13 | 14.784 |  |  |  | SOUTH2001 | BASTROP | 0.0080245 | -0.035434 | 0.11863 | -0.52386 |  | 138
LOCKHA | LOCKHA | 7215 | LOCKHA06 |  |  |  |  | SOUTH2001 | CALDWELL | 0.0089353 | -0.033645 | 0 | 0 |  | 69
LOCKHA | LOCKHA | 7216 | LOCKHA13 | 32.853 |  |  |  | SOUTH2001 | CALDWELL | 0.0085591 | -0.034513 | 0.28119 | -1.1338 |  | 138
MAGNME | MAGNME | 7218 | MAGNME06 | 2.632 |  |  |  | SOUTH2001 | CALDWELL | 0.0089561 | -0.03288 | 0.023572 | -0.086539 |  | 69
LULIMA | LULIMA | 7220 | LULIMA06 | 10.063 |  |  |  | SOUTH2001 | CALDWELL | 0.0089638 | -0.032597 | 0.090203 | -0.32802 |  | 69
LULING1 | LULING1 | 7223 | LULING06 |  |  |  |  | SOUTH2001 | CALDWELL | 0.0089756 | -0.032164 | 0 | 0 |  | 69
LULING1 | LULING1 | 7224 | LULING13 | 21.03 |  |  |  | SOUTH2001 | CALDWELL | 0.008979 | -0.032894 | 0.18883 | -0.69177 |  | 138
CUSHMA | CUSHMA | 7226 | CUSHMA13 | 17.886 |  |  |  | SOUTH2001 | GUADALUPE | 0.010135 | -0.032481 | 0.18128 | -0.58095 |  | 138
SEQUIN | SEQUIN | 7228 | SEGUIN13 | 26.193 |  |  |  | SOUTH2001 | GUADALUPE | 0.010135 | -0.032481 | 0.26548 | -0.85077 |  | 138
SEGUWE | SEGUWE | 7229 | SEGUINW8 | 16.753 |  |  |  | SOUTH2001 | GUADALUPE | 0.010183 | -0.032292 | 0.17059 | -0.54099 |  | 138
HARWOO | HARWOO | 7230 | HARWOO06 | 0.244 |  |  |  | SOUTH2001 | GONZALES | 0.0086911 | -0.031743 | 0.0021206 | -0.0077452 |  | 69
THOMPS | THOMPS | 7231 | THOMPS06 | 2.073 |  |  |  | SOUTH2001 | GONZALES | 0.0084587 | -0.031398 | 0.017535 | -0.065088 |  | 69
WAELDE | WAELDE | 7232 | WAELDE06 | 5.142 |  |  |  | SOUTH2001 | GONZALES | 0.0082808 | -0.031134 | 0.04258 | -0.16009 |  | 69
MOULTO | MOULTO | 7236 | MOULTO06 | 2.439 |  |  |  | SOUTH2001 | LAVACA | 0.0079302 | -0.03026 | 0.019342 | -0.073803 |  | 69
HENKA | HENKA | 7237 | HANKHA06 |  |  |  |  | SOUTH2001 | LAVACA | 0.007958 | -0.030121 | 0 | 0 |  | 69
SHINER | SHINER | 7238 | SHINER06 | 8.583 |  |  |  | SOUTH2001 | LAVACA | 0.008008 | -0.029871 | 0.068732 | -0.25638 |  | 69
WESSER | WESSER | 7239 | WESER 06 | 2.354 |  |  |  | SOUTH2001 | GOLIAD | 0.010925 | -0.02445 | 0.025718 | -0.057556 |  | 69
FRDTRN | FRDTRN | 7240 | FORDTR06 | 5.563 |  |  |  | SOUTH2001 | DEWITT | 0.0087222 | -0.021788 | 0.048522 | -0.12121 |  | 69
YOAKUM | YOAKUM | 7241 | YOAKUM06 |  |  |  |  | SOUTH2001 | DEWITT | 0.0080948 | -0.029437 | 0 | 0 |  | 69
YOAKUM | YOAKUM | 7242 | YOAKUM13 | 22.745 |  |  |  | SOUTH2001 | DEWITT | 0.0082604 | -0.028608 | 0.18788 | -0.65069 |  | 138
CUERO | CUERO | 7244 | CUERO 13 | 29.185 |  |  |  | SOUTH2001 | DEWITT | 0.0086335 | -0.027813 | 0.25197 | -0.81172 |  | 138
GONZAL | GONZAL | 7245 | GONZAL13 | 16.536 |  |  |  | SOUTH2001 | GONZALES | 0.0089076 | -0.030857 | 0.1473 | -0.51025 |  | 138
HALLET | HALLET | 7246 | HALLET13 | 12.865 |  |  |  | SOUTH2001 | LAVACA | 0.0078269 | -0.029451 | 0.10069 | -0.37889 |  | 138
FLATON | FLATON | 7247 | FLATON06 |  |  |  |  | SOUTH2001 | FAYETTE | 0.0078755 | -0.030533 | 0 | 0 |  | 69
FLATON | FLATON | 7248 | FLATON13 | 9.7 |  |  |  | SOUTH2001 | FAYETTE | 0.0071959 | -0.030313 | 0.0698 | -0.29403 |  | 138
ENGLE | ENGLE | 7250 | ENGLE 13 | 0.181 |  |  |  | SOUTH2001 | FAYETTE | 0.0070769 | -0.030116 | 0.0012809 | -0.0054511 |  | 138
SCHULE | SCHULE | 7252 | SCHULE13 | 16.971 |  |  |  | SOUTH2001 | FAYETTE | 0.0069371 | -0.029886 | 0.11773 | -0.50719 |  | 138
WEIMAR | WEIMAR | 7254 | WEIMAR13 | 12.807 |  |  |  | SOUTH2001 | COLORADO | 0.0068092 | -0.029675 | 0.087206 | -0.38004 |  | 138
GLIDDE | GLIDDE | 7257 | GLIDDE06 | 5.126 |  |  |  | SOUTH2001 | COLORADO | 0.0061311 | -0.026314 | 0.031428 | -0.13488 |  | 69
GLIDDE | GLIDDE | 7258 | GLIDDE13 |  |  |  |  | SOUTH2001 | COLORADO | 0.0065385 | -0.029228 | 0 | 0 |  | 138
FRELSB | FRELSB | 7263 | FRELSB13 | 4.399 |  |  |  | SOUTH2001 | COLORADO | 0.0064204 | -0.030047 | 0.028243 | -0.13218 |  | 138
PETERS | PETERS | 7264 | PETERS13 |  |  |  |  | SOUTH2001 | AUSTIN | 0.0028498 | -0.013351 | 0 | 0 |  | 138
PETERS | PETERS | 7266 | PETERS06 |  |  |  |  | SOUTH2001 | AUSTIN | 0.0053799 | -0.024747 | 0 | 0 |  | 69
BELLVI | BELLVI | 7269 | BELLSO06 |  |  |  |  | SOUTH2001 | AUSTIN | 0.0052075 | -0.024388 | 0 | 0 |  | 69
BELLVI | BELLVI | 7270 | BELLSO13 | 12.936 |  |  |  | SOUTH2001 | AUSTIN | 0.0041133 | -0.019678 | 0.05321 | -0.25455 |  | 138
NEWBRE | NEWBRE | 7271 | NEWBRE13 | 2.833 |  |  |  | SOUTH2001 | AUSTIN | 0.0050643 | -0.024485 | 0.014347 | -0.069366 |  | 138
WALLER | WALLER | 7272 | WALLER13 | 20.089 |  |  |  | SOUTH2001 | WALLER | 0.0048535 | -0.023493 | 0.097501 | -0.47194 |  | 138
WILLSP | WILLSP | 7273 | WILLSP13 | 2.789 |  |  |  | SOUTH2001 | FAYETTE | 0.0059916 | -0.029173 | 0.016711 | -0.081363 |  | 138
PLUM | PLUM | 7274 | PLUM 13 | 3.186 |  |  |  | SOUTH2001 | FAYETTE | 0.0068049 | -0.031993 | 0.02168 | -0.10193 |  | 138
RIVERS | RIVERS | 7275 | RIVERS13 | 8.4 |  |  |  | SOUTH2001 | FAYETTE | 0.0066843 | -0.031699 | 0.056148 | -0.26628 |  | 138
LAGRAN | LAGRAN | 7276 | LAGRAN13 | 23.997 |  |  |  | SOUTH2001 | FAYETTE | 0.0066254 | -0.031556 | 0.15899 | -0.75725 |  | 138
FPP138 | FPP138 | 7278 | FPP 13 |  |  |  |  | SOUTH2001 | FAYETTE | 0.0064564 | -0.031145 | 0 | 0 |  | 138
FPPRIP | FPPRIP | 7280 | FPPRIP13 |  |  |  |  | SOUTH2001 | FAYETTE | 0.0064564 | -0.031145 | 0 | 0 |  | 138
FAYSHP | FAYSHP | 7282 | FAYSHP13 | 0.042 |  |  |  | SOUTH2001 | FAYETTE | 0.0063125 | -0.030795 | 0.00026513 | -0.0012934 |  | 138
FAYETT | FAYETT | 7285 | FAYETT06 | 3.299 |  |  |  | SOUTH2001 | FAYETTE | 0.0061549 | -0.02995 | 0.020305 | -0.098804 |  | 69
FAYETT | FAYETT | 7286 | FAYETT13 |  |  |  |  | SOUTH2001 | FAYETTE | 0.0063125 | -0.030795 | 0 | 0 |  | 138
BELLVI | BELLVI | 7287 | BELLVI06 | 7.692 |  |  |  | SOUTH2001 | AUSTIN | 0.0053298 | -0.025123 | 0.040997 | -0.19325 |  | 69
SALEM | SALEM | 7289 | SALEM 13 |  |  |  |  | SOUTH2001 | WASHINGTON | 0.0062367 | -0.030688 | 0 | 0 |  | 138
SALEM | SALEM | 7290 | SALEM 06 |  |  |  |  | SOUTH2001 | WASHINGTON | 0.005944 | -0.028818 | 0 | 0 |  | 69
BRENHA | BRENHA | 7292 | BRENHA13 | 49.248 |  |  |  | SOUTH2001 | WASHINGTON | 0.0061424 | -0.030187 | 0.3025 | -1.4867 |  | 138
BRENNO | BRENNO | 7294 | BRENNO13 | 13.944 |  |  |  | SOUTH2001 | WASHINGTON | 0.005811 | -0.028428 | 0.081028 | -0.3964 |  | 138
PISEK | PISEK | 7296 | PISEK 06 | 2.717 |  |  |  | SOUTH2001 | COLORADO | 0.0060505 | -0.029389 | 0.016439 | -0.079851 |  | 69
ROUNTO | ROUNTO | 7297 | RTOPTA13 |  |  |  |  | SOUTH2001 | FAYETTE | 0.0065593 | -0.031857 | 0 | 0 |  | 138
ROUNTO | ROUNTO | 7299 | ROUNTO13 | 4.167 |  |  |  | SOUTH2001 | FAYETTE | 0.0063125 | -0.030795 | 0.026304 | -0.12832 |  | 138
GIDDIN | GIDDIN | 7302 | GIDDIN13 | 27.412 |  |  |  | SOUTH2001 | LEE | 0.0067188 | -0.032382 | 0.18418 | -0.88767 |  | 138
WINCHE | WINCHE | 7306 | WINCHE13 |  |  |  |  | SOUTH2001 | FAYETTE | 0.0068264 | -0.032825 | 0 | 0 |  | 138
PAIGE | PAIGE | 7308 | PAIGE 13 | 9.351 |  |  |  | SOUTH2001 | BASTROP | 0.0070968 | -0.034415 | 0.066362 | -0.32181 |  | 138
GIDEON | GIDEON | 7310 | GIDEON13 |  |  |  |  | SOUTH2001 | BASTROP | 0.0072659 | -0.03541 | 0 | 0 |  | 138
WARDA | WARDA | 7312 | WARDA 13 | 5.768 |  |  |  | SOUTH2001 | FAYETTE | 0.0067566 | -0.032572 | 0.038972 | -0.18787 |  | 138
SMITHV | SMITHV | 7314 | SMITHV13 | 16.98 |  |  |  | SOUTH2001 | BASTROP | 0.0070616 | -0.034208 | 0.11991 | -0.58085 |  | 138
SMITHV | SMITHV | 7315 | SMITHV06 |  |  |  |  | SOUTH2001 | BASTROP | 0.0070616 | -0.034208 | 0 | 0 |  | 69
ALUMCR | ALUMCR | 7318 | ALUMCR13 | 6.452 |  |  |  | SOUTH2001 | BASTROP | 0.0071494 | -0.034724 | 0.046128 | -0.22404 |  | 138
BASTCI | BASTCI | 7322 | BASTCI13 | 21.381 |  |  |  | SOUTH2001 | BASTROP | 0.0072695 | -0.035764 | 0.15543 | -0.76466 |  | 138
BUTLER | BUTLER | 7324 | BUTLER13 | 9.906 |  |  |  | SOUTH2001 | BASTROP | 0.0061395 | -0.038243 | 0.060818 | -0.37884 |  | 138
MENDOZ | MENDOZ | 7325 | MENDOZ13 | 5.637 |  |  |  | SOUTH2001 | CALDWELL | 0.0085928 | -0.035452 | 0.048438 | -0.19984 |  | 138
SWIFTE | SWIFTE | 7326 | SWIFTE13 | 7.23 |  |  |  | SOUTH2001 | BASTROP | 0.0075349 | -0.036082 | 0.054477 | -0.26087 |  | 138
|  | 7327 | ELGINT13 |  |  |  |  | SOUTH2001 | BASTROP | 0.0077286 | -0.036566 | 0 | 0 |  | 138
AUSTRO | AUSTRO | 7328 | AUSTRO13 |  |  |  |  | SOUTH2001 | TRAVIS | 0.0072819 | -0.036997 | 0 | 0 |  | 138
MANOR | MANOR | 7330 | MANOR 13 | 11.55 |  |  |  | SOUTH2001 | TRAVIS | 0.0080316 | -0.037324 | 0.092765 | -0.43109 |  | 138
CEDAHI | CEDAHI | 7331 | CEDARH13 | 4.527 |  |  |  | SOUTH2001 | BASTROP | 0.0078076 | -0.036764 | 0.035345 | -0.16643 |  | 138
|  | 7332 | ELGIN 13 |  |  |  |  | SOUTH2001 | WILLIAMSON | 0.0060136 | -0.03856 | 0 | 0 |  | 138
HARRBR | HARRBR | 7333 | HARRIS13 | 4.97 |  |  |  | SOUTH2001 | TRAVIS | 0.0081863 | -0.03771 | 0.040686 | -0.18742 |  | 138
MCNEIL_ | MCNEIL- | 7334 | MCNEIL13 |  |  |  |  | SOUTH2001 | TRAVIS | 0.008341 | -0.038097 | 0 | 0 |  | 138
HWRDTP | HWRDTP | 7335 | HOWARD13 |  |  |  |  | SOUTH2001 | TRAVIS | 0.0082928 | -0.038181 | 0 | 0 |  | 138
GILLEL | GILLEL | 7336 | GILLEL13 |  |  |  |  | SOUTH2001 | TRAVIS | 0.0073687 | -0.03843 | 0 | 0 |  | 138
AUSTPL | AUSTPL | 7339 | AUSTIN13 |  |  |  |  | SOUTH2001 | TRAVIS | 0.0083607 | -0.037765 | 0 | 0 |  | 138
BALCRE | BALCRE | 7340 | UTBALC13 | 8.168 |  |  |  | SOUTH2001 | TRAVIS | 0.0084049 | -0.037898 | 0.068651 | -0.30955 |  | 138
GEORGE | GEORGE | 7343 | GEORGE13 | 31.86 |  |  |  | SOUTH2001 | WILLIAMSON | 0.0068655 | -0.039973 | 0.21874 | -1.2735 |  | 138
GABRIE | GABRIE | 7345 | GABRIE06 |  |  |  |  | SOUTH2001 | WILLIAMSON | 0.0050801 | -0.043594 | 0 | 0 |  | 69
GABRIE | GABRIE | 7346 | GABRIE13 | 37.42 |  |  |  | SOUTH2001 | WILLIAMSON | 0.0065387 | -0.040469 | 0.24468 | -1.5143 |  | 138
MARBFA | MARBFA | 7348 | MARBFA13 |  |  |  |  | SOUTH2001 | BURNET | 0.017685 | -0.042761 | 0 | 0 |  | 138
LKWYTP | LKWYTP | 7349 | LKWYTP13 |  |  |  |  | SOUTH2001 | TRAVIS | 0.011888 | -0.039679 | 0 | 0 |  | 138
MORMMI | MORMMI | 7350 | MORMMI13 |  |  |  |  | SOUTH2001 | BURNET | 0.014678 | -0.043529 | 0 | 0 |  | 138
LAGOVI | LAGOVI | 7352 | LAGOVI13 | 20.655 |  |  |  | SOUTH2001 | TRAVIS | 0.011778 | -0.040197 | 0.24327 | -0.83027 |  | 138
MARSFO | MARSFO | 7354 | MARSFO06 |  |  |  |  | SOUTH2001 | TRAVIS | 0.011338 | -0.039386 | 0 | 0 |  | 69
SEGOVI | SEGOVI | 7355 | SEGOVI06 | 3.7 |  |  |  | SOUTH2001 | MASON | 0.12217 | -0.069098 | 0.45203 | -0.25566 |  | 69
MARSFO | MARSFO | 7356 | MARSFO13 |  |  |  |  | SOUTH2001 | TRAVIS | 0.011338 | -0.039386 | 0 | 0 |  | 138
MARSFO | MARSFO | 7359 | MARSFON1 |  |  |  |  | SOUTH2001 | TRAVIS | 0.011338 | -0.039386 | 0 | 0 |  | 0
MARSFO | MARSFO | 7360 | MARSFON2 |  |  |  |  | SOUTH2001 | TRAVIS | 0.011338 | -0.039386 | 0 | 0 |  | 0
MARSFO | MARSFO | 7362 | MARSFON3 |  |  |  |  | SOUTH2001 | TRAVIS | 0.011338 | -0.039386 | 0 | 0 |  | 0
CHIEBR | CHIEBR | 7366 | CHIEBR13 | 13.153 |  |  |  | SOUTH2001 | WILLIAMSON | 0.0071353 | -0.039563 | 0.093851 | -0.52038 |  | 138
CAMPBO | BRADYH | 7386 | CAMPBO13 | 2.7 |  |  |  | SOUTH2001 | MCCULLOCH | -0.00053866 | -0.098372 | -0.0014544 | -0.2656 |  | 138
KUNITZ | KUNITZ | 7387 | KUNITZ13 |  |  |  |  | SOUTH2001 | CULBERSON | 0.28609 | -0.1105 | 0 | 0 |  | 138
SUNRBE | SUNRBE | 7400 | SUNRBE06 | 2.968 |  |  |  | SOUTH2001 | LLANO | 0.029455 | -0.048726 | 0.087424 | -0.14462 |  | 69
KING_2 | KING#2 | 7402 | KING#206 | 6.476 |  |  |  | SOUTH2001 | LLANO | 0.029455 | -0.048726 | 0.19075 | -0.31555 |  | 69
KING_1 | KING#1 | 7404 | KING#106 | 8.119 |  |  |  | SOUTH2001 | LLANO | 0.029455 | -0.048726 | 0.23915 | -0.3956 |  | 69
BLUFFT | BLUFFT | 7406 | BLUFFT06 | 4.654 |  |  |  | SOUTH2001 | LLANO | 0.029455 | -0.048726 | 0.13709 | -0.22677 |  | 69
DOSS | DOSS | 7408 | DOSS 06 | 1.341 |  |  |  | SOUTH2001 | GILLESPIE | 0.041111 | -0.046257 | 0.05513 | -0.062031 |  | 69
HARPER | HARPER | 7410 | HARPER06 | 5.596 |  |  |  | SOUTH2001 | GILLESPIE | 0.041111 | -0.046257 | 0.23006 | -0.25886 |  | 69
LIVEOA | LIVEOA | 7412 | LIVEOA06 | 5.154 |  |  |  | SOUTH2001 | GILLESPIE | 0.041111 | -0.046257 | 0.21188 | -0.23841 |  | 69
LIVEOA | LIVEOA | 7413 | LIVEOT06 |  |  |  |  | SOUTH2001 | GILLESPIE | 0.040457 | -0.046053 | 0 | 0 |  | 69
GOEHLA | GOEHLA | 7414 | GOEHLA06 | 13.536 |  |  |  | SOUTH2001 | GILLESPIE | 0.040457 | -0.046053 | 0.54763 | -0.62338 |  | 69
FREDER | FREDER | 7415 | FREDER06 |  |  |  |  | SOUTH2001 | GILLESPIE | 0.040338 | -0.046016 | 0 | 0 |  | 69
LEAKEY | LEAKEY | 7426 | LEAKEY06 | 9.895 |  |  |  | SOUTH2001 | REAL | 0.022335 | -0.038834 | 0.221 | -0.38427 |  | 69
UTOPIA | UTOPIA | 7428 | UTOPIA06 | 3.694 |  |  |  | SOUTH2001 | BANDERA | 0.022335 | -0.038834 | 0.082505 | -0.14345 |  | 69
MEDINA1 | MEDINA1 | 7430 | MEDINA06 | 4.178 |  |  |  | SOUTH2001 | BANDERA | 0.022335 | -0.038834 | 0.093315 | -0.16225 |  | 69
MEDILA | MEDILA | 7432 | MEDILA06 | 15.365 |  |  |  | SOUTH2001 | BANDERA | 0.015768 | -0.034051 | 0.24228 | -0.5232 |  | 69
BOERNE | BOERNE | 7434 | CICO 06 |  |  |  |  | SOUTH2001 | KENDALL | 0.021081 | -0.038229 | 0 | 0 |  | 69
PIPECR | PIPECR | 7436 | PIPECR06 | 7.497 |  |  |  | SOUTH2001 | BANDERA | 0.015768 | -0.034051 | 0.11822 | -0.25528 |  | 69
PIPECR | PIPECR | 7437 | PIPECR13 |  |  |  |  | SOUTH2001 | BANDERA | 0.015768 | -0.034051 | 0 | 0 |  | 138
BANDER | BANDER | 7438 | BANDER13 | 18.877 |  |  |  | SOUTH2001 | BANDERA | 0.022335 | -0.038834 | 0.42161 | -0.73308 |  | 138
BANDER | BANDER | 7439 | BANDER06 |  |  |  |  | SOUTH2001 | BANDERA | 0.022335 | -0.038834 | 0 | 0 |  | 69
TARPLE | TARPLE | 7440 | TARPLE06 | 1.262 |  |  |  | SOUTH2001 | BANDERA | 0.022335 | -0.038834 | 0.028186 | -0.049009 |  | 69
TURTCR | TURTCR | 7442 | TURTCR13 | 7.088 |  |  |  | SOUTH2001 | KERR | 0.022854 | -0.039085 | 0.16199 | -0.27703 |  | 138
|  | 7454 | TXI 13 | 11.282 |  |  |  | SOUTH2001 | COMAL | 0.010015 | -0.033074 | 0.11299 | -0.37315 |  | 138
LOP337 | LOP337 | 7456 | LOP33713 | 28.212 |  |  |  | SOUTH2001 | COMAL | 0.010229 | -0.032615 | 0.28858 | -0.92013 |  | 138
GPI | GPI | 7458 | GPI-2 13 | 7.521 |  |  |  | SOUTH2001 | COMAL | 0.010274 | -0.032127 | 0.077272 | -0.24163 |  | 138
GPISWI | GPISWI | 7459 | GPI-1 13 |  |  |  |  | SOUTH2001 | COMAL | 0.010274 | -0.032125 | 0 | 0 |  | 138
SHERPO | SHERPO | 7460 | SHERPO13 | 22.064 |  |  |  | SOUTH2001 | COMAL | 0.010294 | -0.031828 | 0.22713 | -0.70224 |  | 138
FREIHE | FREIHE | 7462 | FREIHE13 | 41.45 |  |  |  | SOUTH2001 | COMAL | 0.010194 | -0.032716 | 0.42254 | -1.3561 |  | 138
GRANMO | GRANMO | 7474 | GRANMT13 | 27.102 |  |  |  | SOUTH2001 | BURNET | 0.018609 | -0.043252 | 0.50435 | -1.1722 |  | 138
PALEFA | PALEFA | 7476 | PALEFA13 |  |  |  |  | SOUTH2001 | TRAVIS | 0.015634 | -0.0411 | 0 | 0 |  | 138
|  | 7477 | PALPEC13 | 12.985 |  |  |  | SOUTH2001 | TRAVIS | 0.015252 | -0.041679 | 0.19805 | -0.5412 |  | 138
PHILJC | PHILJC | 7478 | PHILJC13 | 0.77 |  |  |  | SOUTH2001 | BLANCO | 0.016631 | -0.040342 | 0.012806 | -0.031063 |  | 138
MOUNTO | MOUNTO | 7480 | MOUNTO06 |  |  |  |  | SOUTH2001 | BLANCO | 0.017282 | -0.039847 | 0 | 0 |  | 69
BLANCO | BLANCO | 7482 | BLANCO06 | 12.116 |  |  |  | SOUTH2001 | BLANCO | 0.017282 | -0.039847 | 0.20939 | -0.48278 |  | 69
DEVIHI | DEVIHI | 7484 | DEVIHI06 |  |  |  |  | SOUTH2001 | COMAL | 0.013172 | -0.034809 | 0 | 0 |  | 69
CANYHY | CANYHY | 7487 | CANYHY06 |  |  | 6 | 6 | SOUTH2001 | COMAL | 0.011348 | -0.034077 | 0.068087 | -0.20446 |  | 69
SATTLE | SATTLE | 7488 | SATTLE13 | 13.04 |  |  |  | SOUTH2001 | COMAL | 0.011348 | -0.034077 | 0.14798 | -0.44436 |  | 138
SATTLE | SATTLE | 7489 | SATTLE06 |  |  |  |  | SOUTH2001 | COMAL | 0.011348 | -0.034077 | 0 | 0 |  | 69
CRANMI | CRANMI | 7490 | CRANMI13 | 21.48 |  |  |  | SOUTH2001 | COMAL | 0.012261 | -0.034444 | 0.26337 | -0.73985 |  | 138
HUNTER | HUNTER | 7491 | HUNTER13 | 12.539 |  |  |  | SOUTH2001 | HAYS | 0.010229 | -0.033627 | 0.12826 | -0.42165 |  | 138
FISCHE | FISCHE | 7492 | FISCHE06 | 12.694 |  |  |  | SOUTH2001 | COMAL | 0.011348 | -0.034077 | 0.14405 | -0.43257 |  | 69
DEVIHI | DEVIHI | 7493 | DEVIHI13 | 9.943 |  |  |  | SOUTH2001 | COMAL | 0.013172 | -0.034809 | 0.13097 | -0.34611 |  | 138
WIMBER | WIMBER | 7496 | WIMBER06 | 25.285 |  |  |  | SOUTH2001 | HAYS | 0.0094794 | -0.034171 | 0.23969 | -0.86402 |  | 69
BUDA | BUDA | 7498 | BUDA 13 | 35.12 |  |  |  | SOUTH2001 | HAYS | 0.0090503 | -0.036383 | 0.31785 | -1.2778 |  | 138
BUDA | BUDA | 7499 | BUDA 06 |  |  |  |  | SOUTH2001 | HAYS | 0.0090503 | -0.036383 | 0 | 0 |  | 69
TURNER | TURNER | 7500 | TURNER13 |  |  |  |  | SOUTH2001 | HAYS | 0.0088985 | -0.036184 | 0 | 0 |  | 138
GOFORT | GOFORT | 7501 | GOFORT13 | 7.247 |  |  |  | SOUTH2001 | HAYS | 0.0092559 | -0.03528 | 0.067078 | -0.25567 |  | 138
KYLE | KYLE | 7502 | KYLE 06 | 15.25 |  |  |  | SOUTH2001 | HAYS | 0.0094794 | -0.034171 | 0.14456 | -0.52111 |  | 69
MANCHA | MANCHA | 7504 | MANCHA13 | 36.149 |  |  |  | SOUTH2001 | TRAVIS | 0.0090503 | -0.036383 | 0.32716 | -1.3152 |  | 138
CEDAVA | CEDAVA | 7506 | CEDAVA13 | 21.952 |  |  |  | SOUTH2001 | TRAVIS | 0.010306 | -0.038032 | 0.22624 | -0.83487 |  | 138
FRIEND | FRIEND | 7507 | FRIEND13 | 18.369 |  |  |  | SOUTH2001 | HAYS | 0.010002 | -0.037632 | 0.18372 | -0.69126 |  | 138
CENTEX | CENTEX | 7508 | CENTEX06 | 20.328 |  |  |  | SOUTH2001 | HAYS | 0.0090503 | -0.036383 | 0.18397 | -0.7396 |  | 69
RUTHER | RUTHER | 7509 | RUTHER13 |  |  |  |  | SOUTH2001 | HAYS | 0.0096738 | -0.037202 | 0 | 0 |  | 138
RUTHER | RUTHER | 7510 | RUTHER06 |  |  |  |  | SOUTH2001 | HAYS | 0.0096738 | -0.037202 | 0 | 0 |  | 69
DRIPSP | DRIPSP | 7512 | DRIPSP06 | 28.195 |  |  |  | SOUTH2001 | HAYS | 0.0096738 | -0.037202 | 0.27275 | -1.0489 |  | 69
BLANTA | BLANTA | 7514 | BLANTA06 |  |  |  |  | SOUTH2001 | BLANCO | 0.017282 | -0.039847 | 0 | 0 |  | 69
ROHR | ROHR | 7515 | ROHR 13 | 5.952 |  |  |  | SOUTH2001 | HAYS | 0.0095032 | -0.034654 | 0.056563 | -0.20626 |  | 138
JOHNCI | JOHNCI | 7516 | JOHNCI06 | 10.697 |  |  |  | SOUTH2001 | BLANCO | 0.017282 | -0.039847 | 0.18486 | -0.42624 |  | 69
FAIRLA | FAIRLA | 7518 | FAIRLA13 | 12.796 |  |  |  | SOUTH2001 | BURNET | 0.015205 | -0.044135 | 0.19456 | -0.56475 |  | 138
BERTRA | BERTRA | 7520 | BERTRA06 | 9.991 |  |  |  | SOUTH2001 | BURNET | 0.023891 | -0.048535 | 0.23869 | -0.48491 |  | 69
ANDICE | ANDICE | 7522 | ANDICE06 | 18.654 |  |  |  | SOUTH2001 | WILLIAMSON | 0.010513 | -0.039326 | 0.19611 | -0.73358 |  | 69
GLASSC | GLASSC | 7523 | GLASSC13 | 34.651 |  |  |  | SOUTH2001 | WILLIAMSON | 0.0065387 | -0.040469 | 0.22657 | -1.4023 |  | 138
LEANDE | LEANDE | 7524 | LEANDE06 |  |  |  |  | SOUTH2001 | WILLIAMSON | 0.010513 | -0.039326 | 0 | 0 |  | 69
LEANDE | LEANDE | 7525 | LEANDE13 | 35.788 |  |  |  | SOUTH2001 | WILLIAMSON | 0.010513 | -0.039326 | 0.37625 | -1.4074 |  | 138
NAMELE | NAMELE | 7526 | NAMELS13 | 13.354 |  |  |  | SOUTH2001 | TRAVIS | 0.011082 | -0.039718 | 0.14799 | -0.53039 |  | 138
WHITES | WHITES | 7529 | WHITES13 | 44.756 |  |  |  | SOUTH2001 | WILLIAMSON | 0.0099773 | -0.038956 | 0.44654 | -1.7435 |  | 138
BUTTER | BUTTER | 7531 | BUTTER13 | 31.239 |  |  |  | SOUTH2001 | WILLIAMSON | 0.0097424 | -0.038794 | 0.30434 | -1.2119 |  | 138
BALCON | BALCON | 7533 | BALCON13 | 47.811 |  |  |  | SOUTH2001 | WILLIAMSON | 0.010015 | -0.038896 | 0.47883 | -1.8596 |  | 138
|  | 7534 | AVERYR13 | 18.216 |  |  |  | SOUTH2001 | HAYS | 0.0097424 | -0.038794 | 0.17747 | -0.70668 |  | 138
LAKEWAY | LAKEWAY | 7538 | LAKEWY13 | 14.697 |  |  |  | SOUTH2001 | TRAVIS | 0.012688 | -0.040177 | 0.18647 | -0.59047 |  | 138
BEECRE | BEECRE | 7540 | BEECRE13 | 14.04 |  |  |  | SOUTH2001 | TRAVIS | 0.013242 | -0.040146 | 0.18592 | -0.56364 |  | 138
SPICEW | SPICEW | 7542 | SPICEW13 | 25.328 |  |  |  | SOUTH2001 | TRAVIS | 0.0098738 | -0.038756 | 0.25008 | -0.98162 |  | 138
|  | 7545 | HW32BP06 |  |  |  |  | SOUTH2001 | HAYS | 0.0094794 | -0.034171 | 0 | 0 |  | 69
HIGH32 | HIGH32 | 7546 | HIGH3206 | 8.092 |  |  |  | SOUTH2001 | HAYS | 0.011348 | -0.034077 | 0.091827 | -0.27575 |  | 69
MARTIN | MARTIN | 7554 | MARTIN06 | 8.397 |  |  |  | SOUTH2001 | CALDWELL | 0.009272 | -0.03397 | 0.077857 | -0.28525 |  | 69
BASTWE | BASTWE | 7555 | BASWES13 | 9.447 |  |  |  | SOUTH2001 | BASTROP | 0.0074976 | -0.035417 | 0.070829 | -0.33459 |  | 138
BLUEBO | BLUEBO | 7556 | BLUEBO13 | 15.109 |  |  |  | SOUTH2001 | BASTROP | 0.0077292 | -0.035425 | 0.11678 | -0.53523 |  | 138
NEWROS | NEWROS | 7557 | ROSANT06 |  |  |  |  | SOUTH2001 | BASTROP | 0.0070616 | -0.034208 | 0 | 0 |  | 69
NEWROS | NEWROS | 7558 | ROSANK06 | 5.94 |  |  |  | SOUTH2001 | BASTROP | 0.0070616 | -0.034208 | 0.041946 | -0.2032 |  | 69
NEWROS | NEWROS | 7559 | ROSANP06 | 0.235 |  |  |  | SOUTH2001 | BASTROP | 0.0070616 | -0.034208 | 0.0016595 | -0.0080389 |  | 69
REDROC | REDROC | 7560 | REDROC13 | 7.888 |  |  |  | SOUTH2001 | BASTROP | 0.0079198 | -0.034956 | 0.062471 | -0.27574 |  | 138
GUYBUR | GUYBUR | 7564 | GUYBUR13 | 17.112 |  |  |  | SOUTH2001 | WASHINGTON | 0.0062218 | -0.030595 | 0.10647 | -0.52354 |  | 138
MILLCR | MILLCR | 7565 | MILLCR13 |  |  |  |  | SOUTH2001 | WASHINGTON | 0.0061598 | -0.030208 | 0 | 0 |  | 138
MILLCR | MILLCR | 7566 | MILLCR06 |  |  |  |  | SOUTH2001 | WASHINGTON | 0.0061598 | -0.030208 | 0 | 0 |  | 69
DEANVI | DEANVI | 7567 | DEANVI13 | 13.232 |  |  |  | SOUTH2001 | BURLESON | 0.0063889 | -0.031026 | 0.084537 | -0.41054 |  | 138
BURTON | BURTON | 7568 | BURTON06 | 8.091 |  |  |  | SOUTH2001 | WASHINGTON | 0.0061598 | -0.030208 | 0.049839 | -0.24441 |  | 69
SANDHI | SANDHI | 7570 | SANDHI13 | 10.635 |  |  |  | SOUTH2001 | WASHINGTON | 0.0059436 | -0.029075 | 0.06321 | -0.30921 |  | 138
LEXING | LEXING | 7571 | LEXING13 | 7.789 |  |  |  | SOUTH2001 | LEE | 0.0065263 | -0.031591 | 0.050834 | -0.24607 |  | 138
GAYHIL | GAYHIL | 7572 | GAYHIL13 | 5.68 |  |  |  | SOUTH2001 | WASHINGTON | 0.0061018 | -0.029847 | 0.034658 | -0.16953 |  | 138
LYONS | LYONS | 7573 | LYONS 13 | 8.387 |  |  |  | SOUTH2001 | BURLESON | 0.0062312 | -0.030378 | 0.052261 | -0.25478 |  | 138
CHAPHI | CHAPHI | 7574 | CHAPHI13 | 12.375 |  |  |  | SOUTH2001 | WASHINGTON | 0.0055841 | -0.027258 | 0.069103 | -0.33732 |  | 138
HILBIG | HILBIG | 7576 | HILBIG13 |  |  |  |  | SOUTH2001 | BASTROP | 0.0077654 | -0.035063 | 0 | 0 |  | 138
WELCOM | WELCOM | 7577 | WELCOM06 | 5.111 |  |  |  | SOUTH2001 | AUSTIN | 0.0060206 | -0.029229 | 0.030771 | -0.14939 |  | 69
HALLGV | HALLGV | 7586 | HALLGV06 | 4.196 |  |  |  | SOUTH2001 | LAVACA | 0.0082698 | -0.029882 | 0.0347 | -0.12538 |  | 69
MOULGV | MOULGV | 7588 | MOULGV06 | 1.549 |  |  |  | SOUTH2001 | LAVACA | 0.0085808 | -0.030185 | 0.013292 | -0.046756 |  | 69
SHINGV | SHINGV | 7590 | SHINGV06 | 3.622 |  |  |  | SOUTH2001 | LAVACA | 0.0087832 | -0.030381 | 0.031813 | -0.11004 |  | 69
GONZGV | GONZGV | 7592 | GONZGV06 | 10.69 |  |  |  | SOUTH2001 | GONZALES | 0.0092512 | -0.030837 | 0.098896 | -0.32965 |  | 69
OTTINE | OTTINE | 7594 | OTTINE06 | 3.698 |  |  |  | SOUTH2001 | GONZALES | 0.009389 | -0.031032 | 0.034721 | -0.11476 |  | 69
NASHCR | NASHCR | 7596 | NASHCR06 | 2.098 |  |  |  | SOUTH2001 | GUADALUPE | 0.0097364 | -0.031525 | 0.020427 | -0.066139 |  | 69
CAPOTE | CAPOTE | 7598 | CAPOTE06 | 12.885 |  |  |  | SOUTH2001 | GUADALUPE | 0.009887 | -0.031738 | 0.12739 | -0.40895 |  | 69
SEQUIN | SEQUIN | 7600 | SEGUIN06 |  |  |  |  | SOUTH2001 | GUADALUPE | 0.0099972 | -0.031895 | 0 | 0 |  | 69
SMI | SMI | 7602 | SMI 13 | 67.285 |  |  |  | SOUTH2001 | GUADALUPE | 0.010225 | -0.032124 | 0.688 | -2.1615 |  | 138
GERONI | GERONI | 7604 | GERONI13 | 15.891 |  |  |  | SOUTH2001 | GUADALUPE | 0.010147 | -0.032529 | 0.16125 | -0.51692 |  | 138
MCQUEE | MCQUEE | 7605 | MCQUEE06 | 14.147 |  | 8 | 7.6 | SOUTH2001 | GUADALUPE | 0.010094 | -0.031816 | 0.21952 | -0.69191 |  | 69
MCQUEE | MCQUEE | 7606 | MCQUEE13 | 8.364 |  |  |  | SOUTH2001 | GUADALUPE | 0.010255 | -0.032006 | 0.085773 | -0.2677 |  | 138
CIBOLO | CIBOLO | 7608 | CIBOLO13 | 21.783 |  |  |  | SOUTH2001 | GUADALUPE | 0.010439 | -0.031475 | 0.22739 | -0.68563 |  | 138
SCHUMA | SCHUMA | 7609 | SCHUMA13 | 11.002 |  | 3.6 | 3.6 | SOUTH2001 | GUADALUPE | 0.010275 | -0.031916 | 0.15003 | -0.46604 |  | 138
SCHERT | SCHERT | 7610 | SCHERT13 | 18.982 |  |  |  | SOUTH2001 | GUADALUPE | 0.010606 | -0.03106 | 0.20133 | -0.58958 |  | 138
PARKWA | PARKWA | 7611 | PARKWA13 | 13.995 |  |  |  | SOUTH2001 | GUADALUPE | 0.010741 | -0.030726 | 0.15032 | -0.43001 |  | 138
NEWBER | NEWBER | 7612 | NEWBER06 | 16.306 |  |  |  | SOUTH2001 | GUADALUPE | 0.010068 | -0.031607 | 0.16416 | -0.51538 |  | 69
WILSGO | WILSGO | 7613 | WILSGO06 |  |  |  |  | SOUTH2001 | GUADALUPE | 0.010043 | -0.031417 | 0 | 0 |  | 69
LAVERN | LAVERN | 7614 | LAVERN06 | 6.43 |  |  |  | SOUTH2001 | WILSON | 0.010024 | -0.031267 | 0.064455 | -0.20105 |  | 69
WILSON | WILSON | 7615 | WILSON06 | 7.085 |  |  |  | SOUTH2001 | WILSON | 0.010043 | -0.031417 | 0.071157 | -0.22259 |  | 69
NIXOGV | NIXOGV | 7616 | NIXOGV06 | 3.729 |  |  |  | SOUTH2001 | GONZALES | 0.0099648 | -0.030803 | 0.037159 | -0.11487 |  | 69
NIXOGV | NIXOGV | 7617 | NIXON 06 |  |  |  |  | SOUTH2001 | GONZALES | 0.0099578 | -0.030748 | 0 | 0 |  | 69
SMILGO | SMILGO | 7618 | SMILGO06 |  |  |  |  | SOUTH2001 | GONZALES | 0.0097882 | -0.030769 | 0 | 0 |  | 69
SMILEY | SMILEY | 7620 | SMILEY06 | 1.536 |  |  |  | SOUTH2001 | GONZALES | 0.0097882 | -0.030769 | 0.015035 | -0.047262 |  | 69
COST | COST | 7622 | COST 06 | 4.577 |  |  |  | SOUTH2001 | GONZALES | 0.0094773 | -0.030808 | 0.043377 | -0.14101 |  | 69
LAKEWD | LAKEWD | 7624 | LAKEWD06 | 1.645 |  | 4.8 | 4.8 | SOUTH2001 | GONZALES | 0.0093727 | -0.03082 | 0.060407 | -0.19864 |  | 69
GONZAL | GONZAL | 7626 | GONZAL06 |  |  |  |  | SOUTH2001 | GONZALES | 0.0092577 | -0.030835 | 0 | 0 |  | 69
SHELCO | SHELCO | 7636 | COLORA06 | 3.194 |  |  |  | SOUTH2001 | COLORADO | 0.0062433 | -0.02319 | 0.019941 | -0.074068 |  | 69
SHELPL | SHELPL | 7638 | SHELPL06 |  |  |  |  | SOUTH2001 | COLORADO | 0.006241 | -0.023256 | 0 | 0 |  | 69
SHERID | SHERID | 7639 | SHERID06 | 3.694 |  |  |  | SOUTH2001 | COLORADO | 0.0062257 | -0.023682 | 0.022998 | -0.08748 |  | 69
ROCKIS | ROCKIS | 7640 | ROCKIS06 | 1.918 |  |  |  | SOUTH2001 | COLORADO | 0.0061903 | -0.024664 | 0.011873 | -0.047306 |  | 69
SBECTP | SBECTP | 7642 | SBECTP06 |  |  |  |  | SOUTH2001 | COLORADO | 0.0061792 | -0.024976 | 0 | 0 |  | 69
THORSW | THORSW | 7644 | THORSW06 |  |  |  |  | SOUTH2001 | COLORADO | 0.0061738 | -0.025125 | 0 | 0 |  | 69
THOR1 | THOR1 | 7646 | THOR1 06 |  |  |  |  | SOUTH2001 | COLORADO | 0.0061684 | -0.025274 | 0 | 0 |  | 69
PARKBR | PARKBR | 7648 | PARKER06 |  |  |  |  | SOUTH2001 | COLORADO | 0.0061792 | -0.024976 | 0 | 0 |  | 69
THOR2 | THOR2 | 7650 | THOR2 06 | 1.124 |  |  |  | SOUTH2001 | COLORADO | 0.0061738 | -0.025125 | 0.0069393 | -0.028241 |  | 69
BERNAR | BERNAR | 7654 | BERNAR06 | 5.243 |  |  |  | SOUTH2001 | COLORADO | 0.0057963 | -0.025615 | 0.03039 | -0.1343 |  | 69
BELLSO | BELLSO | 7656 | BELSBE06 |  |  |  |  | SOUTH2001 | AUSTIN | 0.0052075 | -0.024388 | 0 | 0 |  | 69
BELLVI | BELLVI | 7658 | BELLTA06 |  |  |  |  | SOUTH2001 | AUSTIN | 0.0052075 | -0.024388 | 0 | 0 |  | 69
QUANSW | QUANSW | 7660 | QUANSW06 |  |  |  |  | SOUTH2001 | AUSTIN | 0.0052075 | -0.024388 | 0 | 0 |  | 69
QUANEX | QUANEX | 7662 | QUANEX06 | 2.865 |  |  |  | SOUTH2001 | AUSTIN | 0.0052075 | -0.024388 | 0.01492 | -0.06987 |  | 69
SUNNYS | SUNNYS | 7664 | SUNNYS06 | 6.51 |  |  |  | SOUTH2001 | WALLER | 0.0052075 | -0.024388 | 0.033901 | -0.15876 |  | 69
PRAIVI | PRAIVI | 7666 | PRAIVI06 |  |  |  |  | SOUTH2001 | WALLER | 0.0052075 | -0.024388 | 0 | 0 |  | 69
PRAIVI | PRAIVI | 7668 | PRAIVI13 | 13.807 |  |  |  | SOUTH2001 | WALLER | 0.0048535 | -0.023493 | 0.067012 | -0.32436 |  | 138
SEAWAY | SEAWAY | 7670 | SEAWAY13 | 13.16 |  |  |  | SOUTH2001 | WALLER | 0.0048535 | -0.023493 | 0.063872 | -0.30916 |  | 138
MACEDO | MACEDO | 7671 | MACEDO13 | 8.362 |  |  |  | SOUTH2001 | WALLER | 0.0048535 | -0.023493 | 0.040585 | -0.19644 |  | 138
MRSES | MRSES | 7704 | MARL SE | 18.59 |  |  |  | SOUTH2001 | FALLS | -0.0032149 | -0.053368 | -0.059764 | -0.9921 |  | 69.6
MRLNS | MRLNS | 7705 | MARLNOSE |  |  |  |  | SOUTH2001 | FALLS | -0.0044583 | -0.035551 | 0 | 0 |  | 69.6
|  | 7706 | LOTT TSE |  |  |  |  | SOUTH2001 | FALLS | -0.0044583 | -0.035551 | 0 | 0 |  | 69.6
|  | 7712 | FAIRF SE | 15.722 |  |  |  | SOUTH2001 | FALLS | -0.0066607 | -0.0039974 | -0.10472 | -0.062848 |  | 138
TEGMN | TEGMN | 7713 | TEAG SE | 13.182 |  |  |  | SOUTH2001 | FALLS | -0.0066607 | -0.0039974 | -0.087801 | -0.052694 |  | 138
|  | 7714 | LOTT SE | 7.022 |  |  |  | SOUTH2001 | FALLS | -0.0044583 | -0.035551 | -0.031307 | -0.24964 |  | 69.6
|  | 7715 | SMARL SE | 8.608 |  |  |  | SOUTH2001 | FREESTONE | -0.0044583 | -0.035551 | -0.038377 | -0.30603 |  | 69.6
|  | 7719 | MEX1 SE | 13.436 |  |  |  | SOUTH2001 | FREESTONE | -0.0066607 | -0.0039974 | -0.089493 | -0.053709 |  | 138
|  | 7720 | MEX2 SE | 14.738 |  |  |  | SOUTH2001 | FALLS | -0.0044583 | -0.035551 | -0.065707 | -0.52396 |  | 138
WTHS_SE | WTHS SE | 7728 | WTHS SE | 13.203 |  |  |  | SOUTH2001 | FALLS | -0.012377 | -0.11488 | -0.16341 | -1.5168 |  | 138
GRSMN | GRSMN | 7731 | GROES SE | 8.019 |  |  |  | SOUTH2001 | FREESTONE | -0.0044583 | -0.035551 | -0.035751 | -0.28509 |  | 138
|  | 7732 | OVERT SE | 6.159 |  |  |  | SOUTH2001 | FREESTONE | -0.012468 | -0.11569 | -0.076787 | -0.71252 |  | 69.6
ARPCM | ARPCM | 7733 | ARP SE | 4.615 |  |  |  | SOUTH2001 | SMITH | -0.012468 | -0.11569 | -0.057538 | -0.5339 |  | 69.6
JKSES | JKSES | 7743 | JAX SE | 15.631 |  |  |  | SOUTH2001 | LIMESTONE | -0.012093 | -0.11243 | -0.18903 | -1.7574 |  | 69.4
MSLMN | MSLMN | 7749 | MTSLM SE | 4.512 |  |  |  | SOUTH2001 | RUSK | -0.01213 | -0.11269 | -0.054729 | -0.50845 |  | 69.6
|  | 7750 | NJAX SE | 14.767 |  |  |  | SOUTH2001 | SMITH | -0.012093 | -0.11243 | -0.17858 | -1.6603 |  | 69.6
|  | 7751 | TXLA TSE |  |  |  |  | SOUTH2001 | CHEROKEE | -0.01213 | -0.11269 | 0 | 0 |  | 69.6
TRPMN | TRPMN | 7752 | TROUP SE | 9.605 |  |  |  | SOUTH2001 | CHEROKEE | -0.01213 | -0.11269 | -0.11651 | -1.0824 |  | 69.6
|  | 7753 | CHIPM SE | 2.947 |  |  |  | SOUTH2001 | CHEROKEE | -0.01213 | -0.11269 | -0.035746 | -0.33209 |  | 69.6
JKSNR | JKSNR | 7754 | JAXNT SE |  |  |  |  | SOUTH2001 | CHEROKEE | -0.012093 | -0.11243 | 0 | 0 |  | 69.4
JKWST | JKWST | 7755 | JAXST SE |  |  |  |  | SOUTH2001 | CHEROKEE | -0.012093 | -0.11243 | 0 | 0 |  | 69.4
|  | 7756 | CLTAP SE |  |  |  |  | SOUTH2001 | SMITH | -0.012093 | -0.11243 | 0 | 0 |  | 69.4
|  | 7757 | W.JAX SE |  |  |  |  | SOUTH2001 | CHEROKEE | -0.012093 | -0.11243 | 0 | 0 |  | 69.4
|  | 7758 | FRANK SE | 4.208 |  |  |  | SOUTH2001 | ANDERSON | -0.012093 | -0.11243 | -0.050887 | -0.47311 |  | 69.6
|  | 7763 | RNLDS SE | 20.074 |  |  |  | SOUTH2001 | CHEROKEE | -0.012093 | -0.11243 | -0.24276 | -2.2569 |  | 69.4
RUSK | RUSK_ | 7765 | RUSK SE | 19.185 |  |  |  | SOUTH2001 | CHEROKEE | -0.011186 | -0.097656 | -0.2146 | -1.8735 |  | 69.4
WORGP | WORGP | 7774 | WTXGF SE | 4.666 |  |  |  | SOUTH2001 | FREESTONE | -0.010708 | -0.10809 | -0.049965 | -0.50433 |  | 69.4
WRTHM | WRTHM | 7781 | WRTHM SE | 2.866 |  |  |  | SOUTH2001 | FREESTONE | -0.010708 | -0.10809 | -0.03069 | -0.30977 |  | 69.4
MXTAP | MXTAP | 7784 | MEX2 TSE |  |  |  |  | SOUTH2001 | FREESTONE | -0.010708 | -0.10809 | 0 | 0 |  | 69.4
MEXIA | MEXIA | 7785 | MEX NOSE |  |  |  |  | SOUTH2001 | FREESTONE | -0.010708 | -0.10809 | 0 | 0 |  | 69.4
|  | 7787 | BMNT TSE |  |  |  |  | SOUTH2001 | CHEROKEE | -0.012093 | -0.11243 | 0 | 0 |  | 69.4
|  | 7788 | BMNT SE | 17.573 |  |  |  | SOUTH2001 | CHEROKEE | -0.012093 | -0.11243 | -0.21251 | -1.9758 |  | 69.4
OTTO_ | OTTO_ | 7789 | OTTO SE | 8.03 |  |  |  | SOUTH2001 | LIMESTONE | -0.0044583 | -0.035551 | -0.035801 | -0.28548 |  | 69.6
MXWST | MXWST | 7791 | MEXW SE |  |  |  |  | SOUTH2001 | FREESTONE | -0.010708 | -0.10809 | 0 | 0 |  | 69.4
COLDG | COLDG | 7794 | COOLG SE | 2.642 |  |  |  | SOUTH2001 | FREESTONE | -0.010708 | -0.10809 | -0.028291 | -0.28556 |  | 69.4
GUADG | GUADG | 7800 | GUALUP 1 |  |  | 150 | 175 | SOUTH2001 | GUADALUPE | 0.010147 | -0.031413 | 1.7757 | -5.4972 |  | 18
GUADG | GUADG | 7801 | GUALUP 2 |  |  | 50 | 175 | SOUTH2001 | GUADALUPE | 0.010147 | -0.031413 | 1.7757 | -5.4972 |  | 18
GUADG | GUADG | 7802 | GUALUP 3 |  |  | 85 | 175 | SOUTH2001 | GUADALUPE | 0.010147 | -0.031413 | 1.7757 | -5.4972 |  | 18
GUADG | GUADG | 7803 | GUALUP 4 |  | 175 |  |  | SOUTH2001 | GUADALUPE | 0.010147 | -0.031413 | 1.7757 | -5.4972 |  | 18
GUADG | GUADG | 7804 | GUALUP 5 |  | 205 |  |  | SOUTH2001 | GUADALUPE | 0.010147 | -0.031413 | 2.0801 | -6.4396 |  | 18
GUADG | GUADG | 7805 | GUALUP 6 |  | 205 |  |  | SOUTH2001 | GUADALUPE | 0.010147 | -0.031413 | 2.0801 | -6.4396 |  | 18
AMISTAD | AMISTAD | 8032 | AMS #1 |  |  | 13 | 33 | SOUTH2001 | VAL VERDE | 0.10942 | -0.05903 | 3.6109 | -1.948 |  | 13.8
AMISTAD | AMISTAD | 8033 | AMS #2 |  | 33 |  |  | SOUTH2001 | VAL VERDE | 0.10942 | -0.05903 | 3.6109 | -1.948 |  | 13.8
FALCON | FALCON | 8048 | FAL #1 |  |  | 6 | 24 | SOUTH2001 | STARR | 0.017623 | -0.027388 | 0.42295 | -0.65731 |  | 13.8
CBL_TWR | CBL-TWR | 8061 | NBCABLE4 |  |  |  |  | SOUTH2001 | NUECES | 0.010106 | -0.023578 | 0 | 0 |  | 138
|  | 8062 | NBRE#1 |  |  |  |  | SOUTH2001 | NUECES | 0.010169 | -0.023653 | 0 | 0 |  | 69
|  | 8063 | NBRE#2 |  |  |  |  | SOUTH2001 | NUECES | 0.010168 | -0.023652 | 0 | 0 |  | 69
|  | 8064 | NBRE#3 |  |  |  |  | SOUTH2001 | NUECES | 0.010168 | -0.023651 | 0 | 0 |  | 69
NUECES_B | NUECES_B | 8065 | NBAYCBL4 |  |  |  |  | SOUTH2001 | NUECES | 0.010103 | -0.023574 | 0 | 0 |  | 138
DUPV1 | DUPV1 | 8066 | DUP1V#1 |  | 82 |  |  | SOUTH2001 | VICTORIA | 0.0087146 | -0.0225 | 0.7146 | -1.845 |  | 13.8
EL_CAMPO | EL_CAMPO | 8100 | EL CAMP2 | 11.403 |  |  |  | SOUTH2001 | WHARTON | 0.0055681 | -0.017932 | 0.063494 | -0.20448 |  | 69
EL_CAMPO | EL_CAMPO | 8102 | EL CAMP4 | 18.594 |  |  |  | SOUTH2001 | WHARTON | 0.0053323 | -0.015868 | 0.099148 | -0.29504 |  | 138
LANCTYPM | LANCTYPM | 8104 | L.C.PMP4 | 0.558 |  |  |  | SOUTH2001 | WHARTON | 0.0041683 | -0.01278 | 0.0023259 | -0.0071311 |  | 138
EAGLE_LK | EAGLE_LK | 8105 | E.LAKE 2 | 10.032 |  |  |  | SOUTH2001 | COLORADO | 0.0059357 | -0.022211 | 0.059547 | -0.22282 |  | 69
ALTAIR | ALTAIR | 8106 | ALTAIR 2 |  |  |  |  | SOUTH2001 | COLORADO | 0.0060142 | -0.023124 | 0 | 0 |  | 69
GLIDDEN | GLIDDEN | 8107 | CPL-GLN2 |  |  |  |  | SOUTH2001 | COLUMBUS | 0.0063429 | -0.026951 | 0 | 0 |  | 69
GLIDDEN | GLIDDEN | 8109 | CPL-GLN4 |  |  |  |  | SOUTH2001 | COLUMBUS | 0.006537 | -0.02921 | 0 | 0 |  | 138
COLUMBUS | COLUMBUS | 8111 | COLUMBS2 | 12.334 |  |  |  | SOUTH2001 | COLORADO | 0.0063001 | -0.026452 | 0.077705 | -0.32626 |  | 69
BAY_CITY | BAY_CITY | 8113 | BAY CTY4 | 44.104 |  |  |  | SOUTH2001 | MATAGORDA | 0.004377 | -0.013295 | 0.19304 | -0.58635 |  | 138
CONOCO | CONOCO | 8114 | CNCO-BC4 | 24.227 |  |  |  | SOUTH2001 | MATAGORDA | 0.0047714 | -0.014291 | 0.1156 | -0.34622 |  | 138
WADSWORT | WADSWORT | 8115 | WADSWRT4 | 4.898 |  |  |  | SOUTH2001 | MATAGORDA | 0.0047725 | -0.014294 | 0.023376 | -0.07001 |  | 138
CELANEBC | CELANEBC | 8116 | CEL-BAY4 | 12.735 |  |  |  | SOUTH2001 | MATAGORDA | 0.0049792 | -0.014816 | 0.063411 | -0.18868 |  | 138
GANADO | GANADO | 8117 | GANADO 4 | 6.848 |  |  |  | SOUTH2001 | JACKSON | 0.0065787 | -0.018334 | 0.045051 | -0.12555 |  | 138
EDNA | EDNA | 8118 | EDNA 4 | 13.97 |  |  |  | SOUTH2001 | JACKSON | 0.0071845 | -0.019533 | 0.10037 | -0.27288 |  | 138
BLESSING | BLESSING | 8119 | BLESSNG2 | 3.919 |  |  |  | SOUTH2001 | MATAGORDA | 0.005655 | -0.016634 | 0.022162 | -0.065189 |  | 69
BLESSING | BLESSING | 8121 | BLESSNG4 |  |  |  |  | SOUTH2001 | MATAGORDA | 0.0052125 | -0.015405 | 0 | 0 |  | 138
BLESSING | BLESSING | 8123 | BLESSNG6 |  |  |  |  | SOUTH2001 | MATAGORDA | 0.0044167 | -0.01399 | 0 | 0 |  | 345
LOLITA | LOLITA | 8125 | LOLITA 4 | 1.391 |  |  |  | SOUTH2001 | JACKSON | 0.0073818 | -0.019762 | 0.010268 | -0.027489 |  | 138
FORMOSA | FORMOSA | 8126 | FORMOSA4 |  |  |  |  | SOUTH2001 | CALHOUN | 0.0079295 | -0.020813 | 0 | 0 |  | 138
LAN_CTY | LAN_CTY | 8127 | L.CITYM4 |  |  |  |  | SOUTH2001 | WHARTON | 0.0040731 | -0.012527 | 0 | 0 |  | 138
PALACIOS | PALACIOS | 8131 | PALACOS2 | 11.501 |  |  |  | SOUTH2001 | MATAGORDA | 0.0062532 | -0.017715 | 0.071918 | -0.20374 |  | 69
PCOMFORT | PCOMFORT | 8132 | P.CMFT 2 | 2.436 |  |  |  | SOUTH2001 | CALHOUN | 0.0076983 | -0.020326 | 0.018753 | -0.049515 |  | 69
BROOKHOL | BROOKHOL | 8133 | B.HOLOW2 | 13.127 |  |  |  | SOUTH2001 | CALHOUN | 0.0080452 | -0.020953 | 0.10561 | -0.27506 |  | 69
GARZA | GARZA | 8134 | FOR #1 |  | 33 |  |  | SOUTH2001 | CALHOUN | 0.0079295 | -0.020813 | 0.26168 | -0.68684 |  | 13.8
P_LAVACA | P_LAVACA | 8135 | PTLAVAC2 | 14.44 |  |  |  | SOUTH2001 | CALHOUN | 0.0081702 | -0.021179 | 0.11798 | -0.30583 |  | 69
PLACEDO | PLACEDO | 8136 | PLACEDO2 | 3.252 |  |  |  | SOUTH2001 | VICTORIA | 0.0085067 | -0.02192 | 0.027664 | -0.071285 |  | 69
ALCOA | ALCOA | 8137 | ALCOA 4 | 13.598 |  |  |  | SOUTH2001 | CALHOUN | 0.008044 | -0.021033 | 0.10938 | -0.28601 |  | 138
FALCON | FALCON | 8138 | FOR #2 |  | 33 |  |  | SOUTH2001 | CALHOUN | 0.0079295 | -0.020813 | 0.26168 | -0.68684 |  | 13.8
JOSLIN | JOSLIN | 8139 | JOS #1 |  |  | 245 | 254 | SOUTH2001 | CALHOUN | 0.008044 | -0.021033 | 2.0432 | -5.3424 |  | 22
JOSLIN | JOSLIN | 8140 | JOSLIN 4 |  |  |  |  | SOUTH2001 | CALHOUN | 0.008044 | -0.021033 | 0 | 0 |  | 138
GOHLKE | GOHLKE | 8141 | GOHLKE 4 | 1.774 |  |  |  | SOUTH2001 | VICTORIA | 0.0084133 | -0.021841 | 0.014925 | -0.038746 |  | 138
V_DUPSW | V_DUPSW | 8143 | DUPSW-V4 |  |  |  |  | SOUTH2001 | VICTORIA | 0.0087146 | -0.0225 | 0 | 0 |  | 138
AIRCO4 | AIRCO4 | 8144 | AIRCO 4 | 2.29 |  |  |  | SOUTH2001 | CALHOUN | 0.0085797 | -0.021927 | 0.019647 | -0.050214 |  | 138
VISTRON | VISTRON | 8145 | VISTRON4 | 5.613 |  |  |  | SOUTH2001 | CALHOUN | 0.008594 | -0.022064 | 0.048238 | -0.12385 |  | 138
BIGTRE | BIGTRE | 8146 | BIG 3 4 | 39.99 |  |  |  | SOUTH2001 | VICTORIA | 0.0086803 | -0.022376 | 0.34712 | -0.89482 |  | 138
|  | 8147 | UCAR #2 |  | 38 |  |  | SOUTH2001 | CALHOUN | 0.008508 | -0.021829 | 0.3233 | -0.82951 |  | 13.8
|  | 8148 | UCAR #1 |  | 38 |  |  | SOUTH2001 | CALHOUN | 0.008508 | -0.021829 | 0.3233 | -0.82951 |  | 13.8
NCARBIDE | NCARBIDE | 8149 | CARB-SD2 | 50.668 |  |  |  | SOUTH2001 | CALHOUN | 0.008508 | -0.021829 | 0.43108 | -1.106 |  | 69
NCARBIDE | NCARBIDE | 8152 | CARB-SD4 |  |  |  |  | SOUTH2001 | CALHOUN | 0.0085466 | -0.021892 | 0 | 0 |  | 138
FORMOSA | FORMOSA | 8153 | FOR #3 |  |  | 75 | 83 | SOUTH2001 | CALHOUN | 0.0079295 | -0.020813 | 0.65815 | -1.7275 |  | 13.8
FORMOSA | FORMOSA | 8154 | FOR #4 |  |  | 75 | 83 | SOUTH2001 | CALHOUN | 0.0079295 | -0.020813 | 0.65815 | -1.7275 |  | 13.8
FORMOSA | FORMOSA | 8155 | FOR #5 |  | 83 |  |  | SOUTH2001 | CALHOUN | 0.0079295 | -0.020813 | 0.65815 | -1.7275 |  | 13.8
FORMOSA | FORMOSA | 8156 | FOR #6 |  | 83 |  |  | SOUTH2001 | CALHOUN | 0.0079295 | -0.020813 | 0.65815 | -1.7275 |  | 13.8
FORMOSA | FORMOSA | 8157 | FOR #7 |  | 83 |  |  | SOUTH2001 | CALHOUN | 0.0079295 | -0.020813 | 0.65815 | -1.7275 |  | 13.8
GREENLK | GREENLK | 8159 | GRNLAKE2 | 5.398 |  |  |  | SOUTH2001 | CALHOUN | 0.0085387 | -0.021905 | 0.046092 | -0.11824 |  | 69
COLETO | COLETO | 8160 | CC1TERT |  |  |  |  | SOUTH2001 | GOLIAD | 0.0095983 | -0.023627 | 0 | 0 |  | 13.8
COLETO | COLETO | 8161 | CLO #1 |  |  | 600 | 632 | SOUTH2001 | GOLIAD | 0.0095386 | -0.0236 | 6.0284 | -14.9152 |  | 24
COLETO | COLETO | 8162 | COLETO 4 |  |  |  |  | SOUTH2001 | GOLIAD | 0.0095386 | -0.0236 | 0 | 0 |  | 138
COLETO | COLETO | 8163 | CC1DUM |  |  |  |  | SOUTH2001 | GOLIAD | 0.0095983 | -0.023627 | 0 | 0 |  | 250
COLETO | COLETO | 8164 | COLETO 6 |  |  |  |  | SOUTH2001 | GOLIAD | 0.0096772 | -0.023662 | 0 | 0 |  | 345
CSABLK | CSABLK | 8166 | CSABLK 9 | 8.445 |  |  |  | SOUTH2001 | JIM WELLS | 0.011779 | -0.025774 | 0.099476 | -0.21766 |  | 69
GEWST | GEWST | 8167 | GWEST2 | 7.698 |  |  |  | SOUTH2001 | VICTORIA | 0.013164 | -0.027674 | 0.10134 | -0.21303 |  | 138
VICTORIA | VICTORIA | 8168 | VIC #4 |  |  | 60 | 69 | SOUTH2001 | VICTORIA | 0.0088656 | -0.022711 | 0.61173 | -1.567 |  | 13.8
VICTORIA | VICTORIA | 8169 | VICTRA 2 | 18.378 |  |  |  | SOUTH2001 | VICTORIA | 0.0088656 | -0.022711 | 0.16293 | -0.41737 |  | 69
VICTORIA | VICTORIA | 8172 | VICTRA 4 |  |  |  |  | SOUTH2001 | VICTORIA | 0.0088171 | -0.022764 | 0 | 0 |  | 138
VICTORIA | VICTORIA | 8173 | VIC #5 |  |  | 168 | 172 | SOUTH2001 | VICTORIA | 0.0088171 | -0.022764 | 1.5165 | -3.9154 |  | 19.5
VICTORIA | VICTORIA | 8174 | VIC #6 |  |  | 250 | 250 | SOUTH2001 | VICTORIA | 0.0088171 | -0.022764 | 2.2043 | -5.691 |  | 22
MAGRUDER | MAGRUDER | 8177 | MAGRUDR2 | 37.727 |  |  |  | SOUTH2001 | VICTORIA | 0.0088656 | -0.022711 | 0.33447 | -0.8568 |  | 69
N_VICT | N_VICT | 8178 | N.VICT 2 | 53.817 |  |  |  | SOUTH2001 | VICTORIA | 0.0088656 | -0.022711 | 0.47712 | -1.2222 |  | 69
FOSTER | FOSTER | 8179 | FOSTR T2 |  |  |  |  | SOUTH2001 | VICTORIA | 0.0088656 | -0.022711 | 0 | 0 |  | 69
FOSTER | FOSTER | 8180 | FOSTER 2 | 5.992 |  |  |  | SOUTH2001 | VICTORIA | 0.0088656 | -0.022711 | 0.053123 | -0.13608 |  | 69
LEARY_LN | LEARY_LN | 8182 | LEARY L2 | 46.524 |  |  |  | SOUTH2001 | VICTORIA | 0.0088656 | -0.022711 | 0.41246 | -1.0566 |  | 69
THOMASTN | THOMASTN | 8183 | THOMSTN4 | 0.647 |  |  |  | SOUTH2001 | DEWITT | 0.008706 | -0.02587 | 0.0056328 | -0.016738 |  | 138
KENEDYSW | KENEDYSW | 8184 | KENDYSW2 | 3.057 |  |  |  | SOUTH2001 | KARNES | 0.011919 | -0.028286 | 0.036436 | -0.086472 |  | 69
KENEDYSW | KENEDYSW | 8186 | KENDYSW4 | 7.504 |  |  |  | SOUTH2001 | KARNES | 0.012809 | -0.028219 | 0.096118 | -0.21176 |  | 138
KENEDY | KENEDY | 8188 | KENEDY 2 | 8.102 |  |  |  | SOUTH2001 | KARNES | 0.011898 | -0.028145 | 0.096394 | -0.22803 |  | 69
CUECPL | CUECPL | 8189 | CUERO 2 |  | 24 |  |  | SOUTH2001 | DEWITT | 0.0093496 | -0.028612 | 0.22439 | -0.68669 |  | 69
CUELCA | CUELCA | 8190 | C.LCRA 2 |  |  |  |  | SOUTH2001 | DEWITT | 0.0092086 | -0.028446 | 0 | 0 |  | 69
CUELCA | CUELCA | 8192 | C.LCRA 4 |  |  |  |  | SOUTH2001 | DEWITT | 0.0086379 | -0.027772 | 0 | 0 |  | 138
DARST_CR | DARST_CR | 8195 | DARST 2 | 5.035 |  |  |  | SOUTH2001 | GUADALUPE | 0.0093537 | -0.031618 | 0.047096 | -0.15919 |  | 69
BEEVILLE | BEEVILLE | 8198 | BEEVLLE2 | 36.355 |  |  |  | SOUTH2001 | BEE | 0.011575 | -0.026002 | 0.42081 | -0.9453 |  | 69
|  | 8199 | LULNG M4 |  |  |  |  | SOUTH2001 | CALDWELL | 0.0089776 | -0.032158 | 0 | 0 |  | 69
PLEASANT | PLEASANT | 8200 | PLESTN 2 |  |  |  |  | SOUTH2001 | ATASCOSA | 0.018617 | -0.0309 | 0 | 0 |  | 69
PLEASANT | PLEASANT | 8203 | PLESTN 4 | 28.773 |  |  |  | SOUTH2001 | ATASCOSA | 0.017973 | -0.030974 | 0.51712 | -0.8912 |  | 138
CHARLOTT | CHARLOTT | 8206 | CHARLOT2 | 3.125 |  |  |  | SOUTH2001 | ATASCOSA | 0.021121 | -0.0317 | 0.066004 | -0.099063 |  | 69
DILLEY2 | DILLEY2 | 8208 | DILLEY 2 | 4.663 |  |  |  | SOUTH2001 | FRIO | 0.026851 | -0.03353 | 0.12521 | -0.15635 |  | 69
DILLEYSW | DILLEYSW | 8210 | DILYSW 2 |  |  |  |  | SOUTH2001 | FRIO | 0.027151 | -0.033611 | 0 | 0 |  | 69
DILLEYSW | DILLEYSW | 8212 | DILYSW 4 |  |  |  |  | SOUTH2001 | FRIO | 0.029146 | -0.034153 | 0 | 0 |  | 138
PEARSAL1 | PEARSAL1 | 8216 | PEARSAL2 | 12.239 |  |  |  | SOUTH2001 | FRIO | 0.02669 | -0.033626 | 0.32666 | -0.41154 |  | 69
BIG_FOOT | BIG_FOOT | 8218 | BIGFOOT2 |  |  |  |  | SOUTH2001 | FRIO | 0.026555 | -0.033706 | 0 | 0 |  | 69
BIG_FOOT | BIG_FOOT | 8221 | BIGFOOT4 |  |  |  |  | SOUTH2001 | FROP | 0.026452 | -0.033768 | 0 | 0 |  | 138
DEVINE | DEVINE | 8223 | DEVINE 2 | 11.144 |  |  |  | SOUTH2001 | MEDINA | 0.026555 | -0.033706 | 0.29593 | -0.37562 |  | 69
MOORE | MOORE | 8225 | MOORE138 |  |  |  |  | SOUTH2001 | FRIO | 0.028162 | -0.034343 | 0 | 0 |  | 138
BATESVL | BATESVL | 8229 | BATSVL 4 |  |  |  |  | SOUTH2001 | ZAVALA | 0.041896 | -0.038316 | 0 | 0 |  | 138
UVALDE | UVALDE | 8231 | UVALDE 2 |  |  |  |  | SOUTH2001 | UVALDE | 0.064065 | -0.045089 | 0 | 0 |  | 69
UVALDE | UVALDE | 8234 | UVALDE 4 | 39.02 |  |  |  | SOUTH2001 | UVALDE | 0.05427 | -0.04212 | 2.1176 | -1.6435 |  | 138
W_BATESV | W_BATESV | 8236 | W.BATSV4 |  |  |  |  | SOUTH2001 | ZAVALA | 0.045334 | -0.039302 | 0 | 0 |  | 138
CRYSTAL | CRYSTAL | 8242 | CRYSTAL2 | 11.981 |  |  |  | SOUTH2001 | ZAVALA | 0.054036 | -0.041783 | 0.64741 | -0.5006 |  | 69
TURTLECK | TURTLECK | 8243 | TURTLCR2 |  |  |  |  | SOUTH2001 | ZAVALA | 0.054481 | -0.041929 | 0 | 0 |  | 69
CARRIZO | CARRIZO | 8244 | CARRIZO2 | 11.168 |  |  |  | SOUTH2001 | DIMMIT | 0.050001 | -0.040452 | 0.55841 | -0.45177 |  | 69
ASPHALT | ASPHALT | 8246 | ASPHALT4 | 0.696 |  |  |  | SOUTH2001 | UVALDE | 0.065686 | -0.045621 | 0.045717 | -0.031752 |  | 138
HAMILTON | HAMILTON | 8251 | HAMILCP4 |  |  |  |  | SOUTH2001 | VAL VERDE | 0.10929 | -0.058988 | 0 | 0 |  | 138
BRACKVL4 | BRACKVL4 | 8252 | BRACKVL4 | 6.417 |  |  |  | SOUTH2001 | KINNEY | 0.085739 | -0.051769 | 0.55019 | -0.3322 |  | 138
HAMILTON | HAMILTON | 8253 | HAMILTN2 |  |  |  |  | SOUTH2001 | VAL VERDE | 0.12094 | -0.062502 | 0 | 0 |  | 69
HAMILTON | HAMILTON | 8255 | HAMILTN4 | 15.89 |  |  |  | SOUTH2001 | VAL VERDE | 0.10942 | -0.05903 | 1.7387 | -0.93798 |  | 138
AMISTAD | AMISTAD | 8258 | AMISTAD4 | 2.851 |  |  |  | SOUTH2001 | VAL VERDE | 0.10942 | -0.05903 | 0.31196 | -0.16829 |  | 138
EAGLE_HY | EAGLE_HY | 8263 | EPASS H4 | 0.686 |  | 6 | 6 | SOUTH2001 | MAVERICK | 0.085039 | -0.051368 | 0.56857 | -0.34345 |  | 138
EP_H_TP | EP_H_TP | 8264 | EP.H TP4 |  |  |  |  | SOUTH2001 | MAVERICK | 0.085039 | -0.051368 | 0 | 0 |  | 138
EAGLE_PS | EAGLE_PS | 8270 | EPASS C4 | 40.078 |  |  |  | SOUTH2001 | MAVERICK | 0.078786 | -0.049403 | 3.1576 | -1.98 |  | 138
PUEBLO | PUEBLO | 8273 | PUEBLO 4 | 19.564 |  |  |  | SOUTH2001 | MAVERICK | 0.072241 | -0.047346 | 1.4133 | -0.92628 |  | 138
W_CONOCO | W_CONOCO | 8274 | CNC.W T4 |  |  |  |  | SOUTH2001 | MAVERICK | 0.063886 | -0.044721 | 0 | 0 |  | 138
ASHERTON | ASHERTON | 8280 | ASHERTN2 | 1.754 |  |  |  | SOUTH2001 | DIMMIT | 0.047399 | -0.039594 | 0.083138 | -0.069449 |  | 69
ASHERTON | ASHERTON | 8283 | ASHERTN4 |  |  |  |  | SOUTH2001 | DIMMIT | 0.043854 | -0.038426 | 0 | 0 |  | 138
LAREDO | LAREDO | 8285 | LAR #1 |  | 35 |  |  | SOUTH2001 | WEBB | 0.026769 | -0.031542 | 0.9369 | -1.104 |  | 13.8
LAREDO | LAREDO | 8287 | LAR #2 |  |  | 34 | 34 | SOUTH2001 | WEBB | 0.027088 | -0.03169 | 0.92099 | -1.0775 |  | 13.8
LAREDO | LAREDO | 8288 | LAR #3 |  |  | 110 | 110 | SOUTH2001 | WEBB | 0.027088 | -0.03169 | 2.9797 | -3.4859 |  | 13.8
LAREDO | LAREDO | 8290 | LAREDO 2 |  |  |  |  | SOUTH2001 | WEBB | 0.026769 | -0.031542 | 0 | 0 |  | 69
LAREDO | LAREDO | 8293 | LAREDO 4 | 36.688 |  |  |  | SOUTH2001 | WEBB | 0.027088 | -0.03169 | 0.9938 | -1.1627 |  | 138
WORMSER | WORMSER | 8295 | WORMSR 4 |  |  |  |  | SOUTH2001 | WEBB | 0.026215 | -0.031444 | 0 | 0 |  | 138
WORMSER | WORMSER | 8296 | WORMCP 4 |  |  |  |  | SOUTH2001 | WEBB | 0.026434 | -0.031521 | 0 | 0 |  | 138
BRUNI4 | BRUNI4 | 8297 | BRUNI 4 | 5.173 |  |  |  | SOUTH2001 | WEBB | 0.021005 | -0.028863 | 0.10866 | -0.14931 |  | 138
ZAPATA | ZAPATA | 8299 | ZAPATA 4 | 16.831 |  |  |  | SOUTH2001 | ZAPATA | 0.021541 | -0.029238 | 0.36256 | -0.4921 |  | 138
RAYMOND2 | RAYMOND2 | 8300 | RAYVILE2 | 0.169 |  |  |  | SOUTH2001 | WILLACY | 0.01111 | -0.024308 | 0.0018776 | -0.0041081 |  | 69
RAYMOND2 | RAYMOND2 | 8302 | RAYVILE4 |  |  |  |  | SOUTH2001 | WILLACY | 0.011076 | -0.02429 | 0 | 0 |  | 138
LA_PALMA | LA_PALMA | 8305 | LAP #4 |  | 25 |  |  | SOUTH2001 | CAMERON | 0.011164 | -0.024341 | 0.27911 | -0.60851 |  | 13.8
LA_PALMA | LA_PALMA | 8306 | LAP #5 |  | 25 |  |  | SOUTH2001 | CAMERON | 0.011164 | -0.024341 | 0.27911 | -0.60851 |  | 13.8
LA_PALMA | LA_PALMA | 8307 | LAP #7 |  |  | 52 | 52 | SOUTH2001 | CAMERON | 0.011164 | -0.024341 | 0.58055 | -1.2657 |  | 13.8
LA_PALMA | LA_PALMA | 8308 | LAP #6 |  |  | 159 | 159 | SOUTH2001 | CAMERON | 0.011123 | -0.024321 | 1.7686 | -3.8671 |  | 18
LA_PALMA | LA_PALMA | 8310 | LAPALM 2 |  |  |  |  | SOUTH2001 | CAMERON | 0.011164 | -0.024341 | 0 | 0 |  | 69
LA_PALMA | LA_PALMA | 8314 | LAPALM 4 |  |  |  |  | SOUTH2001 | CAMERON | 0.011123 | -0.024321 | 0 | 0 |  | 138
LA_PALMA | LA_PALMA | 8315 | LP3DUM |  |  |  |  | SOUTH2001 | CAMERON | 0.011063 | -0.024294 | 0 | 0 |  | 100
LA_PALMA | LA_PALMA | 8317 | LAPALM 6 |  |  |  |  | SOUTH2001 | CAMERON | 0.011045 | -0.024286 | 0 | 0 |  | 345
RIOHONDO | RIOHONDO | 8318 | RIOHND 6 |  |  |  |  | SOUTH2001 | CAMERON | 0.011025 | -0.024277 | 0 | 0 |  | 345
RIOHONDO | RIOHONDO | 8319 | RIOHND 4 |  |  |  |  | SOUTH2001 | CAMERON | 0.011101 | -0.02431 | 0 | 0 |  | 138
W_HARLIN | W_HARLIN | 8320 | W HGN 2 | 29.179 |  |  |  | SOUTH2001 | CAMERON | 0.011171 | -0.024343 | 0.32597 | -0.71032 |  | 69
HARLIN_1 | HARLIN_1 | 8321 | HGN-1 2 | 31.47 |  |  |  | SOUTH2001 | CAMERON | 0.011174 | -0.024344 | 0.35164 | -0.76612 |  | 69
HAINE_DR | HAINE_DR | 8322 | HAINEDR4 | 25.335 |  |  |  | SOUTH2001 | CAMERON | 0.011125 | -0.024322 | 0.28185 | -0.6162 |  | 138
E_HARRIS | E_HARRIS | 8323 | HARRISN2 | 53.16 |  |  |  | SOUTH2001 | CAMERON | 0.011169 | -0.024343 | 0.59377 | -1.2941 |  | 69
RIOHONDO | RIOHONDO | 8324 | RH1DUM |  |  |  |  | SOUTH2001 | CAMERON | 0.011067 | -0.024295 | 0 | 0 |  | 250
HARLINSW | HARLINSW | 8325 | HGN SW 2 | 31.49 |  |  |  | SOUTH2001 | CAMERON | 0.011178 | -0.024346 | 0.352 | -0.76666 |  | 69
HARLINSW | HARLINSW | 8327 | HGN SW 4 |  |  |  |  | SOUTH2001 | CAMERON | 0.011132 | -0.024325 | 0 | 0 |  | 138
L_FRESNO | L_FRESNO | 8328 | LP3TERT |  |  |  |  | SOUTH2001 | CAMERON | 0.011063 | -0.024294 | 0 | 0 |  | 13.8
L_FRESNO | L_FRESNO | 8329 | L.FRES 2 | 25.256 |  |  |  | SOUTH2001 | CAMERON | 0.011164 | -0.024341 | 0.28197 | -0.61474 |  | 69
MV_B_TP | MV_B_TP | 8331 | BRWN CY2 | 10.736 |  |  |  | SOUTH2001 | CAMERON | 0.011164 | -0.024341 | 0.11986 | -0.26132 |  | 69
BROWN_SW | BROWN_SW | 8332 | BRWN SW2 |  |  |  |  | SOUTH2001 | CAMERON | 0.011164 | -0.024341 | 0 | 0 |  | 69
CAVAZOS | CAVAZOS | 8334 | CAVAZOS2 | 7.27 |  |  |  | SOUTH2001 | CAMERON | 0.011164 | -0.024341 | 0.081166 | -0.17696 |  | 69
S_PADRE | S_PADRE | 8335 | S.PADRE4 | 27.377 |  |  |  | SOUTH2001 | CAMERON | 0.011121 | -0.02432 | 0.30445 | -0.66581 |  | 138
RIOHONDO | RIOHONDO | 8336 | RH1TERT |  |  |  |  | SOUTH2001 | CAMERON | 0.011067 | -0.024295 | 0 | 0 |  | 13.8
SCARBIDE | SCARBIDE | 8337 | CARB-VL4 |  |  |  |  | SOUTH2001 | CAMERON | 0.011119 | -0.024319 | 0 | 0 |  | 138
P_ISABEL | P_ISABEL | 8338 | P.ISABL4 | 7.569 |  |  |  | SOUTH2001 | CAMERON | 0.011121 | -0.02432 | 0.084173 | -0.18408 |  | 138
MILITARY | MILITARY | 8339 | MIL.HWY4 |  |  |  |  | SOUTH2001 | CAMERON | 0.011121 | -0.02432 | 0 | 0 |  | 138
|  | 8341 | ED1TERT |  |  |  |  | SOUTH2001 | HIDALGO | 0.011283 | -0.024398 | 0 | 0 |  | 13.8
WESMER | WESMER | 8347 | WESMER 4 | 30.593 |  |  |  | SOUTH2001 | HIDALGO | 0.011396 | -0.024449 | 0.34863 | -0.74798 |  | 138
WESLACOU | WESLACOU | 8348 | WES UNT4 | 49.057 |  |  |  | SOUTH2001 | HIDALGO | 0.011463 | -0.024481 | 0.56236 | -1.201 |  | 138
SAN_ROSA | SAN_ROSA | 8349 | S.ROSA 2 | 13.185 |  |  |  | SOUTH2001 | CAMERON | 0.011288 | -0.024398 | 0.14883 | -0.32168 |  | 69
N_MERCED | N_MERCED | 8351 | MERCDES2 | 10.696 |  |  |  | SOUTH2001 | HIDALGO | 0.011355 | -0.024429 | 0.12145 | -0.2613 |  | 69
NWESLACO | NWESLACO | 8352 | NWESLCO2 | 7.131 |  |  |  | SOUTH2001 | HIDALGO | 0.011417 | -0.024459 | 0.081416 | -0.17441 |  | 69
WESLACO | WESLACO | 8353 | WES.SW 2 |  |  |  |  | SOUTH2001 | HIDALGO | 0.01143 | -0.024465 | 0 | 0 |  | 69
WESLACO | WESLACO | 8354 | WESLCSW4 |  |  |  |  | SOUTH2001 | HIDAGLO | 0.011459 | -0.024478 | 0 | 0 |  | 138
|  | 8356 | HIDGOB 4 |  |  |  |  | SOUTH2001 | HIDALGO | 0.011532 | -0.024512 | 0 | 0 |  | 138
ELSA | ELSA | 8360 | ELSA 4 | 19.489 |  |  |  | SOUTH2001 | HIDALGO | 0.011476 | -0.024486 | 0.22366 | -0.47721 |  | 138
N_ALAMO | N_ALAMO | 8362 | ALAMO 2 | 24.997 |  |  |  | SOUTH2001 | HIDALGO | 0.011488 | -0.024492 | 0.28717 | -0.61223 |  | 69
N_PHARR | N_PHARR | 8363 | PHARR 2 |  |  |  |  | SOUTH2001 | HIDALGO | 0.011523 | -0.024509 | 0 | 0 |  | 69
W_MCALLN | W_MCALLN | 8367 | WMCALN 4 | 67.092 |  |  |  | SOUTH2001 | HIDALGO | 0.011785 | -0.024632 | 0.79068 | -1.6526 |  | 138
N_MCALLN | N_MCALLN | 8368 | NMCALN 4 | 64.603 |  |  |  | SOUTH2001 | HIDALGO | 0.011787 | -0.024633 | 0.7615 | -1.5914 |  | 138
S_MCALLN | S_MCALLN | 8369 | SMCALN 2 | 33.282 |  |  |  | SOUTH2001 | HIDALGO | 0.011915 | -0.024693 | 0.39654 | -0.82185 |  | 69
S_MCALLN | S_MCALLN | 8371 | SMCALN 4 |  |  |  |  | SOUTH2001 | HIDALGO | 0.011783 | -0.024631 | 0 | 0 |  | 138
N_PHARR | N_PHARR | 8372 | NPHARR 4 | 37.509 |  |  |  | SOUTH2001 | HIDALGO | 0.011625 | -0.024557 | 0.43604 | -0.92109 |  | 138
POLK_AVE | POLK_AVE | 8373 | POLK 4 | 67.6 |  |  |  | SOUTH2001 | HIDALGO | 0.01168 | -0.024583 | 0.7896 | -1.6618 |  | 138
SE_EDINB | SE_EDINB | 8374 | SE EDNB4 | 35.991 |  |  |  | SOUTH2001 | HIDALGO | 0.011562 | -0.024527 | 0.41613 | -0.88275 |  | 138
NEDIN | NEDIN | 8377 | EDNBRG 2 | 11.413 |  |  |  | SOUTH2001 | HIDALGO | 0.011606 | -0.024548 | 0.13246 | -0.28016 |  | 69
NEDIN | NEDIN | 8380 | EDNBRG 4 |  |  |  |  | SOUTH2001 | HIDALGO | 0.011532 | -0.024512 | 0 | 0 |  | 138
NEDIN | NEDIN | 8381 | ED3DUM |  |  |  |  | SOUTH2001 | HIDALGO | 0.011283 | -0.024398 | 0 | 0 |  | 100
NEDIN | NEDIN | 8383 | EDNBRG 6 |  |  |  |  | SOUTH2001 | HIDALGO | 0.011218 | -0.024367 | 0 | 0 |  | 345
MOORE_FL | MOORE_FL | 8385 | MOORE F2 | 8.266 |  |  |  | SOUTH2001 | HIDALGO | 0.011819 | -0.024648 | 0.097694 | -0.20374 |  | 69
S_MISSIN | S_MISSIN | 8386 | MISSION2 | 36.701 |  |  |  | SOUTH2001 | HIDALGO | 0.012154 | -0.024806 | 0.44607 | -0.91042 |  | 69
PALMVIEW | PALMVIEW | 8387 | PALMVW 4 | 17.069 |  |  |  | SOUTH2001 | HIDALGO | 0.012057 | -0.024761 | 0.20581 | -0.42264 |  | 138
BATES | BATES | 8388 | BAT #1 |  |  | 72 | 72 | SOUTH2001 | HIDALGO | 0.012277 | -0.024864 | 0.88392 | -1.7902 |  | 13.8
BATES | BATES | 8390 | BATES 2 |  |  |  |  | SOUTH2001 | HIDALGO | 0.012277 | -0.024864 | 0 | 0 |  | 69
|  | 8391 | SHLND 4 | 25.103 |  |  |  | SOUTH2001 | HIDALGO | 0.011889 | -0.024682 | 0.29846 | -0.61958 |  | 138
BATES | BATES | 8392 | BATES 4 |  |  |  |  | SOUTH2001 | HIDALGO | 0.012133 | -0.024796 | 0 | 0 |  | 138
BATES | BATES | 8393 | BAT #2 |  |  | 110 | 110 | SOUTH2001 | HIDALGO | 0.012133 | -0.024796 | 1.3346 | -2.7276 |  | 13.8
FALCON | FALCON | 8395 | FALCON 4 |  |  |  |  | SOUTH2001 | STARR | 0.017623 | -0.027388 | 0 | 0 |  | 138
GARZA | GARZA | 8397 | GARZA 2 | 4.48 |  |  |  | SOUTH2001 | STARR | 0.014719 | -0.026017 | 0.065943 | -0.11656 |  | 69
GARZA | GARZA | 8399 | GARZA 4 |  |  |  |  | SOUTH2001 | STARR | 0.014806 | -0.026058 | 0 | 0 |  | 138
THREE_RI | THREE_RI | 8400 | T.RIVR 2 | 8.317 |  |  |  | SOUTH2001 | LIVE OAK | 0.014166 | -0.028471 | 0.11782 | -0.23679 |  | 69
THREE_RI | THREE_RI | 8403 | T.RIVR 4 |  |  |  |  | SOUTH2001 | LIVE OAK | 0.014052 | -0.02887 | 0 | 0 |  | 138
SIGMOR | SIGMOR | 8404 | SIGMOR 4 | 42.007 |  |  |  | SOUTH2001 | LIVE OAK | 0.014044 | -0.028898 | 0.58997 | -1.2139 |  | 138
SKIDMORE | SKIDMORE | 8405 | SKIDMOR2 | 2.319 |  |  |  | SOUTH2001 | BEE | 0.011166 | -0.025319 | 0.025893 | -0.058716 |  | 69
MATHI_ST | MATHI ST | 8407 | MATHIS 2 | 12.834 |  |  |  | SOUTH2001 | SAN PATRICIO | 0.011054 | -0.025046 | 0.14186 | -0.32144 |  | 69
EDROY | EDROY | 8408 | EDROY 2 | 3.439 |  |  |  | SOUTH2001 | SAN PATRICIO | 0.010749 | -0.024487 | 0.036964 | -0.084211 |  | 69
GRETA | GRETA | 8409 | GRETA 2 | 2.89 |  |  |  | SOUTH2001 | REGUGIO | 0.0093789 | -0.02303 | 0.027105 | -0.066558 |  | 69
REFUGIO | REFUGIO | 8410 | REFUGIO2 | 9.998 |  |  |  | SOUTH2001 | REFUGIO | 0.0094943 | -0.023102 | 0.094924 | -0.23098 |  | 69
SINTON | SINTON | 8413 | SINTON 2 | 13.696 |  |  |  | SOUTH2001 | SAN PATRICIO | 0.010429 | -0.024091 | 0.14284 | -0.32995 |  | 69
PORTLAND | PORTLAND | 8414 | PORTLND4 | 27.656 |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0098459 | -0.023259 | 0.2723 | -0.64326 |  | 138
RINCON | RINCON | 8416 | RINCON 2 |  |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0098575 | -0.023329 | 0 | 0 |  | 69
RINCON | RINCON | 8418 | RINCON 4 |  |  |  |  | SOUTH2001 | SAN PATRICIO | 0.00977 | -0.023186 | 0 | 0 |  | 138
GREGORY | GREGORY | 8421 | GREGORY2 | 6.211 |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0098532 | -0.023306 | 0.061198 | -0.14476 |  | 69
I_DUPSW | I_DUPSW | 8422 | DUPSW-I4 |  |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0098296 | -0.023245 | 0 | 0 |  | 138
CITGO_NB | CITGO_NB | 8423 | CITGONB | 13.486 |  |  |  | SOUTH2001 | NUECES | 0.010108 | -0.023581 | 0.13632 | -0.31801 |  | 138
INGLESID | INGLESID | 8425 | INGLSDE4 | 19.221 |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0098324 | -0.02325 | 0.18899 | -0.44688 |  | 138
CITGO_NO | CITGO_NO | 8426 | CITNOP4 | 3.664 |  |  |  | SOUTH2001 | SAN PATRICIO | 0.010108 | -0.023581 | 0.037037 | -0.0864 |  | 138
ARANSAS | ARANSAS | 8427 | A PASS 2 | 9.934 |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0098475 | -0.023277 | 0.097825 | -0.23123 |  | 69
ARANSAS | ARANSAS | 8430 | A PASS 4 |  |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0098368 | -0.023258 | 0 | 0 |  | 138
|  | 8431 | LVEOAK2 | 9.924 |  |  |  | SOUTH2001 | ARANAS | 0.009828 | -0.023254 | 0.097533 | -0.23077 |  | 69
ROCKPORT | ROCKPORT | 8432 | ROCKPRT2 | 7.387 |  |  |  | SOUTH2001 | ARANSAS | 0.009828 | -0.023254 | 0.072599 | -0.17178 |  | 69
ROCKPORT | ROCKPORT | 8434 | ROCKPRT4 |  |  |  |  | SOUTH2001 | ARANSAS | 0.0097902 | -0.02321 | 0 | 0 |  | 138
SEAWALL | SEAWALL | 8435 | SEAWALL2 | 11.648 |  |  |  | SOUTH2001 | NUECES | 0.0098724 | -0.023304 | 0.11499 | -0.27145 |  | 69
PORT_A | PORT_A | 8436 | P ARANS2 | 16.899 |  |  |  | SOUTH2001 | NUECES | 0.0099359 | -0.023375 | 0.16791 | -0.39501 |  | 69
NUECES_B | NUECES_B | 8437 | NBY #5 |  |  | 25 | 30 | SOUTH2001 | NUECES | 0.010137 | -0.023615 | 0.30412 | -0.70846 |  | 13.8
NUECES_B | NUECES_B | 8438 | NBY #6 |  |  | 165 | 169 | SOUTH2001 | NUECES | 0.010137 | -0.023615 | 1.7132 | -3.991 |  | 20
NUECES_B | NUECES_B | 8439 | N BAY 2 | 10.218 |  |  |  | SOUTH2001 | NUECES | 0.010137 | -0.023615 | 0.10358 | -0.2413 |  | 69
NUECES_B | NUECES_B | 8441 | N BAY 4 |  |  |  |  | SOUTH2001 | NUECES | 0.010101 | -0.023573 | 0 | 0 |  | 138
NUECES_B | NUECES_B | 8442 | NBY #7 |  |  | 368 | 368 | SOUTH2001 | NUECES | 0.010101 | -0.023573 | 3.7173 | -8.6748 |  | 22
LON_HILL | LON_HILL | 8444 | LCH #1 |  |  | 71 | 73 | SOUTH2001 | NUECES | 0.010491 | -0.024015 | 0.76586 | -1.7531 |  | 13.8
LON_HILL | LON_HILL | 8445 | LCH #2 |  |  | 71 | 73 | SOUTH2001 | NUECES | 0.010491 | -0.024015 | 0.76586 | -1.7531 |  | 13.8
LON_HILL | LON_HILL | 8446 | LCH #3 |  |  | 164 | 164 | SOUTH2001 | NUECES | 0.010269 | -0.023827 | 1.6841 | -3.9076 |  | 18
LON_HILL | LON_HILL | 8447 | LCH #4 |  |  | 247 | 247 | SOUTH2001 | NUECES | 0.010269 | -0.023827 | 2.5365 | -5.8853 |  | 22
LON_HILL | LON_HILL | 8448 | LNHILL 2 |  |  |  |  | SOUTH2001 | NUECES | 0.010491 | -0.024015 | 0 | 0 |  | 69
LON_HILL | LON_HILL | 8452 | LNHILL 4 |  |  |  |  | SOUTH2001 | NUECES | 0.010269 | -0.023827 | 0 | 0 |  | 138
LON_HILL | LON_HILL | 8453 | LH3DUM |  |  |  |  | SOUTH2001 | NUECES | 0.010292 | -0.02383 | 0 | 0 |  | 100
LON_HILL | LON_HILL | 8454 | LH4DUM |  |  |  |  | SOUTH2001 | NUECES | 0.010289 | -0.02383 | 0 | 0 |  | 100
LON_HILL | LON_HILL | 8455 | LNHILL 6 |  |  |  |  | SOUTH2001 | NUECES | 0.0099392 | -0.02378 | 0 | 0 |  | 345
B_DAVIS | B_DAVIS | 8456 | COSW#1 |  | 20 |  |  | SOUTH2001 | NUECES | 0.010171 | -0.023655 | 0.20343 | -0.4731 |  | 13.8
B_DAVIS | B_DAVIS | 8457 | COSW#2 |  | 20 |  |  | SOUTH2001 | NUECES | 0.010171 | -0.023655 | 0.20343 | -0.4731 |  | 13.8
B_DAVIS | B_DAVIS | 8458 | DAVIS 4 |  |  |  |  | SOUTH2001 | NUECES | 0.010253 | -0.023711 | 0 | 0 |  | 138
B_DAVIS | B_DAVIS | 8459 | DAV #1 |  |  | 328.436 | 344 | SOUTH2001 | NUECES | 0.010253 | -0.023711 | 3.5271 | -8.1565 |  | 24
B_DAVIS | B_DAVIS | 8460 | DAV #2 |  |  | 300.01 | 353 | SOUTH2001 | NUECES | 0.010253 | -0.023711 | 3.6194 | -8.3699 |  | 22
KOCH_UP | KOCH_UP | 8461 | KOCHREF2 |  | 38 |  |  | SOUTH2001 | NUECES | 0.010309 | -0.023819 | 0.39173 | -0.90514 |  | 12.5
ASR_REF | ASR_REF | 8462 | ASARCO2 |  |  |  |  | SOUTH2001 | NUECES | 0.010244 | -0.023742 | 0 | 0 |  | 69
COASTSTE | COASTSTE | 8463 | COSTL E2 | 4.115 |  |  |  | SOUTH2001 | NUECES | 0.01017 | -0.023654 | 0.04185 | -0.097335 |  | 69
COASTAL | COASTAL | 8464 | COSTL W2 | 4.653 |  |  |  | SOUTH2001 | NUECES | 0.010171 | -0.023655 | 0.047327 | -0.11007 |  | 69
INDUSTRI | INDUSTRI | 8465 | INDSTRL2 | 27.674 |  |  |  | SOUTH2001 | NUECES | 0.010171 | -0.023655 | 0.28149 | -0.65464 |  | 69
KOCH_UP | KOCH_UP | 8467 | UPRIVER4 | 17.683 |  |  |  | SOUTH2001 | NUECES | 0.010204 | -0.023722 | 0.18044 | -0.41947 |  | 138
HIWAY_9 | HIWAY_9 | 8468 | HIWAY9 2 | 40.029 |  |  |  | SOUTH2001 | NUECES | 0.010174 | -0.023659 | 0.40727 | -0.94703 |  | 69
KOCH_UP | KOCH_UP | 8469 | UPRIVER2 | 17.588 |  |  |  | SOUTH2001 | NUECES | 0.010309 | -0.023819 | 0.18131 | -0.41894 |  | 69
HIWAY_9 | HIWAY_9 | 8470 | HIWAY9 4 |  |  |  |  | SOUTH2001 | NUECES | 0.010139 | -0.023616 | 0 | 0 |  | 138
CITGO_OP | CITGO_OP | 8471 | CITGOE 4 | 31.183 |  |  |  | SOUTH2001 | NUECES | 0.010111 | -0.023584 | 0.31528 | -0.73541 |  | 138
SOUTHWES | SOUTHWES | 8473 | KOCHEST4 | 22.483 |  |  |  | SOUTH2001 | NUECES | 0.01011 | -0.023583 | 0.2273 | -0.53021 |  | 138
MORRIS | MORRIS | 8474 | MORRIS 4 | 70.616 |  |  |  | SOUTH2001 | NUECES | 0.010125 | -0.0236 | 0.71497 | -1.6665 |  | 138
JAVELINA | JAVELINA | 8475 | JAVELIN4 | 44.8 |  |  |  | SOUTH2001 | NUECES | 0.010152 | -0.023631 | 0.4548 | -1.0587 |  | 138
CITGO_W | CITGO_W | 8476 | CHMPLNP4 | 20.833 |  |  |  | SOUTH2001 | NUECES | 0.010219 | -0.023734 | 0.2129 | -0.49446 |  | 138
VALERO | VALERO | 8477 | VALEROW2 | 28.093 |  |  |  | SOUTH2001 | NUECES | 0.010268 | -0.023771 | 0.28846 | -0.66779 |  | 69
OXY_CC | OXY_CC | 8478 | CCPETRO4 | 0.078 |  |  |  | SOUTH2001 | NUECES | 0.01025 | -0.023792 | 0.00079952 | -0.0018558 |  | 138
CLARK_WD | CLARK_WD | 8479 | CLARKWD4 | 20.357 |  |  |  | SOUTH2001 | NUECES | 0.010235 | -0.023764 | 0.20835 | -0.48376 |  | 138
WEIL_TRC | WEIL_TRC | 8480 | WEIL 2 |  |  |  |  | SOUTH2001 | NUECES | 0.010209 | -0.0237 | 0 | 0 |  | 69
KOCH_HF | KOCH_HF | 8481 | HEARNSF4 | 11.069 |  |  |  | SOUTH2001 | NUECES | 0.010212 | -0.023734 | 0.11304 | -0.26271 |  | 138
WEIL_TRC | WEIL_TRC | 8482 | WEIL 4 | 14.861 |  |  |  | SOUTH2001 | NUECES | 0.010212 | -0.023721 | 0.15176 | -0.35251 |  | 138
SOUTH_SI | SOUTH_SI | 8483 | S.SIDE 4 | 69.654 |  |  |  | SOUTH2001 | NUECES | 0.010192 | -0.023669 | 0.70989 | -1.6487 |  | 138
WEST_OSO | WEST_OSO | 8484 | WESTOSO4 | 18.663 |  |  |  | SOUTH2001 | NUECES | 0.01017 | -0.023652 | 0.1898 | -0.44142 |  | 138
WESTSIDE | WESTSIDE | 8485 | WSTSIDE4 |  |  |  |  | SOUTH2001 | NUECES | 0.010185 | -0.023671 | 0 | 0 |  | 138
HOLLY4 | HOLLY4 | 8486 | HOLLY 4 | 59.23 |  |  |  | SOUTH2001 | NUECES | 0.0102 | -0.023676 | 0.60414 | -1.4023 |  | 138
AIRLINE | AIRLINE | 8487 | AIRLINE2 | 64.903 |  |  |  | SOUTH2001 | NUECES | 0.010204 | -0.023672 | 0.66224 | -1.5364 |  | 69
AIRLINE | AIRLINE | 8490 | AIRLINE4 |  |  |  |  | SOUTH2001 | NUECES | 0.010214 | -0.023684 | 0 | 0 |  | 138
WOOLRIDG | WOOLRIDG | 8492 | WOOLDRI4 | 17.987 |  |  |  | SOUTH2001 | NUECES | 0.010216 | -0.023686 | 0.18376 | -0.42604 |  | 138
PHARAOH | PHARAOH | 8493 | PHARAOH4 | 31.526 |  |  |  | SOUTH2001 | NUECES | 0.010222 | -0.02369 | 0.32226 | -0.74684 |  | 138
LAGUNA | LAGUNA | 8494 | LAGUNA 2 | 16.185 |  |  |  | SOUTH2001 | NUECES | 0.010181 | -0.023648 | 0.16478 | -0.38274 |  | 69
NAVAL_BS | NAVAL_BS | 8495 | N BASE 2 | 40.088 |  |  |  | SOUTH2001 | NUECES | 0.010171 | -0.023636 | 0.40772 | -0.94751 |  | 69
ARCADIA | ARCADIA | 8496 | ARCADIA4 | 67.861 |  |  |  | SOUTH2001 | NUECES | 0.010178 | -0.023659 | 0.69071 | -1.6055 |  | 138
CALALLEN | CALALLEN | 8497 | CALAN M2 |  |  |  |  | SOUTH2001 | NUECES | 0.010615 | -0.024075 | 0 | 0 |  | 69
BISHOP | BISHOP | 8498 | BISHOP 2 | 6.221 |  |  |  | SOUTH2001 | NUECES | 0.01236 | -0.024819 | 0.076889 | -0.1544 |  | 69
LON_HILL | LON_HILL | 8499 | LH3TERT |  |  |  |  | SOUTH2001 | NUECES | 0.010292 | -0.02383 | 0 | 0 |  | 13.8
ALICE | ALICE | 8500 | ALICE 2 | 0.196 |  |  |  | SOUTH2001 | JIM WELLS | 0.012579 | -0.024934 | 0.0024655 | -0.0048871 |  | 69
LON_HILL | LON_HILL | 8502 | LH4TERT |  |  |  |  | SOUTH2001 | NUECES | 0.010289 | -0.02383 | 0 | 0 |  | 13.8
ALICE | ALICE | 8503 | ALICE 4 |  |  |  |  | SOUTH2001 | JIM WELLS | 0.011599 | -0.024462 | 0 | 0 |  | 138
FREER | FREER | 8505 | FREER 2 | 0.323 |  |  |  | SOUTH2001 | DUVAL | 0.017476 | -0.027214 | 0.0056448 | -0.0087902 |  | 69
|  | 8506 | VAL #1 |  | 25 |  |  | SOUTH2001 | DUVAL | 0.010268 | -0.023771 | 0.2567 | -0.59427 |  | 13.8
|  | 8507 | VAL #2 |  | 25 |  |  | SOUTH2001 | DUVAL | 0.010268 | -0.023771 | 0.2567 | -0.59427 |  | 13.8
FALFUR | FALFUR | 8508 | FALF 2 | 7.063 |  |  |  | SOUTH2001 | BROOKS | 0.014447 | -0.025812 | 0.10204 | -0.18231 |  | 69
FALFUR | FALFUR | 8510 | FALF 4 | 7.386 |  |  |  | SOUTH2001 | BROOKS | 0.015051 | -0.026096 | 0.11117 | -0.19275 |  | 138
|  | 8511 | STARCO#1 |  | 38 |  |  | SOUTH2001 | NUECES | 0.01025 | -0.023792 | 0.38951 | -0.9041 |  | 13.8
STRATTON | STRATTON | 8512 | STRATN 2 |  |  |  |  | SOUTH2001 | NUECES | 0.01236 | -0.024819 | 0 | 0 |  | 69
STRATTON | STRATTON | 8514 | STRATN 4 |  |  |  |  | SOUTH2001 | NUECES | 0.01236 | -0.024819 | 0 | 0 |  | 138
ALAZAN | ALAZAN | 8515 | ALAZAN 4 | 1.851 |  |  |  | SOUTH2001 | KLEBERG | 0.010441 | -0.023834 | 0.019327 | -0.044116 |  | 138
CELANEBI | CELANEBI | 8516 | CEL-BIS4 | 2.684 |  |  |  | SOUTH2001 | NUECES | 0.010757 | -0.02404 | 0.028871 | -0.064523 |  | 138
CELANEBI | CELANEBI | 8517 | CEL-B #1 |  | 38 |  |  | SOUTH2001 | NUECES | 0.010757 | -0.02404 | 0.40876 | -0.91352 |  | 13.8
KINGSVIL | KINGSVIL | 8518 | KINGSVL4 | 27.822 |  |  |  | SOUTH2001 | KLEBERG | 0.010911 | -0.024131 | 0.30357 | -0.67136 |  | 138
KLEBERG | KLEBERG | 8519 | KLEBERG4 | 30.83 |  |  |  | SOUTH2001 | KLEBERG | 0.010846 | -0.024098 | 0.33439 | -0.74296 |  | 138
STAFFORD | STAFFORD | 8520 | STAFORD2 | 0.745 |  |  |  | SOUTH2001 | COLORADO | 0.0061978 | -0.025261 | 0.0046173 | -0.01882 |  | 69
PRAIRPMP | PRAIRPMP | 8523 | PRARPMP2 | 1.891 |  |  |  | SOUTH2001 | COLORADO | 0.0059678 | -0.022584 | 0.011285 | -0.042706 |  | 69
PRAIRPMP | PRAIRPMP | 8524 | P.PMP T2 |  |  |  |  | SOUTH2001 | COLORADO | 0.0059678 | -0.022584 | 0 | 0 |  | 69
RIVER_SD | RIVER_SD | 8526 | R.SIDET2 |  |  |  |  | SOUTH2001 | COLORADO | 0.0059708 | -0.022619 | 0 | 0 |  | 69
RIVER_SD | RIVER_SD | 8527 | RVRSPMP2 | 0.108 |  |  |  | SOUTH2001 | COLORADO | 0.0059708 | -0.022619 | 0.00064484 | -0.0024429 |  | 69
PARKER | PARKER | 8528 | PKR TP 2 |  |  |  |  | SOUTH2001 | COLORADO | 0.0059647 | -0.022548 | 0 | 0 |  | 69
PARKER | PARKER | 8529 | PARKER 2 | 0.994 |  |  |  | SOUTH2001 | COLORADO | 0.0059647 | -0.022548 | 0.0059289 | -0.022412 |  | 69
B_GRAVEL | B_GRAVEL | 8530 | GARRLTP2 |  |  |  |  | SOUTH2001 | COLORADO | 0.0060142 | -0.023124 | 0 | 0 |  | 69
GARWDPMP | GARWDPMP | 8531 | GAR PMP2 | 0.167 |  |  |  | SOUTH2001 | COLORADO | 0.0060142 | -0.023124 | 0.0010044 | -0.0038617 |  | 69
IDEAL_TP | IDEAL-TP | 8532 | IDL TP 2 |  |  |  |  | SOUTH2001 | COLORADO | 0.0060142 | -0.023124 | 0 | 0 |  | 69
GARWDRLF | GARWDRLF | 8533 | GARWD R2 | 0.186 |  |  |  | SOUTH2001 | COLORADO | 0.0060142 | -0.023124 | 0.0011186 | -0.0043011 |  | 69
TXI_TP | TXI-TP | 8534 | TXI TP 2 |  |  |  |  | SOUTH2001 | COLORADO | 0.0060142 | -0.023124 | 0 | 0 |  | 69
TXI | TXI | 8535 | TXI 2 | 0.647 |  |  |  | SOUTH2001 | COLORADO | 0.0060142 | -0.023124 | 0.0038912 | -0.014961 |  | 69
PV_TAP | PV_TAP | 8536 | PTLAVTP2 |  |  |  |  | SOUTH2001 | CALHOUN | 0.00824 | -0.021284 | 0 | 0 |  | 69
IDEAL_ | IDEAL_ | 8537 | IDEAL C2 | 0.216 |  |  |  | SOUTH2001 | COLORADO | 0.0060142 | -0.023124 | 0.0012991 | -0.0049948 |  | 69
GARWOOD | GARWOOD | 8538 | GARWOD 2 | 1.647 |  |  |  | SOUTH2001 | COLORADO | 0.0058184 | -0.020845 | 0.0095829 | -0.034332 |  | 69
LONE_STR | LONE_STR | 8539 | L.STR T2 |  |  |  |  | SOUTH2001 | COLORADO | 0.0058275 | -0.020951 | 0 | 0 |  | 69
LONE_STR | LONE_STR | 8541 | L.STAR 2 | 0.784 |  |  |  | SOUTH2001 | COLORADO | 0.0058275 | -0.020951 | 0.0045687 | -0.016426 |  | 69
MATTHEWS | MATTHEWS | 8542 | MATHEWS2 | 0.49 |  |  |  | SOUTH2001 | COLORADO | 0.0058804 | -0.021566 | 0.0028814 | -0.010568 |  | 69
LAKESIDP | LAKESIDP | 8543 | LAKSIDE2 | 0.098 |  |  |  | SOUTH2001 | COLORADO | 0.0059199 | -0.022026 | 0.00058015 | -0.0021586 |  | 69
|  | 8545 | BC-TP 2 |  |  |  |  | SOUTH2001 | MATAGORDA | 0.005655 | -0.016634 | 0 | 0 |  | 69
BYCTYPM1 | BYCTYPM1 | 8546 | BCPMPTP2 |  |  |  |  | SOUTH2001 | MATAGORDA | 0.005655 | -0.016634 | 0 | 0 |  | 69
BYCTYPM1 | BYCTYPM1 | 8547 | BC PMP12 | 0.294 |  |  |  | SOUTH2001 | MATAGORDA | 0.005655 | -0.016634 | 0.0016626 | -0.0048904 |  | 69
BYCTYPM3 | BYCTYPM3 | 8549 | BC PMP32 | 0.549 |  |  |  | SOUTH2001 | MATAGORDA | 0.005655 | -0.016634 | 0.0031046 | -0.0091321 |  | 69
MARKHAM | MARKHAM | 8550 | MARKHAM2 | 2.821 |  |  |  | SOUTH2001 | MATAGORDA | 0.005655 | -0.016634 | 0.015953 | -0.046925 |  | 69
MIDFLD_T | MIDFLD_T | 8552 | CST TP 2 |  |  |  |  | SOUTH2001 | MATAGORDA | 0.0056208 | -0.017145 | 0 | 0 |  | 69
CARANCUA | CARANCUA | 8555 | CARANCA2 | 0.598 |  |  |  | SOUTH2001 | JACKSON | 0.0070738 | -0.019198 | 0.0042302 | -0.01148 |  | 69
CLEMVILL | CLEMVILL | 8556 | CLMVL T2 |  |  |  |  | SOUTH2001 | MATAGORDA | 0.0056161 | -0.017215 | 0 | 0 |  | 69
CLEMVILL | CLEMVILL | 8557 | CLMVLE 2 | 0.774 |  |  |  | SOUTH2001 | MATAGORDA | 0.0056161 | -0.017215 | 0.0043469 | -0.013324 |  | 69
STPSW | STPSW | 8558 | STP PTP4 |  |  |  |  | SOUTH2001 | MATAGORDA | 0.0050953 | -0.015109 | 0 | 0 |  | 138
STPCONST | STPCONST | 8559 | STP-CON4 |  |  |  |  | SOUTH2001 | MATAGORDA | 0.0050953 | -0.015109 | 0 | 0 |  | 138
STPCONST | STPCONST | 8563 | STP PMP4 |  |  |  |  | SOUTH2001 | MATAGORDA | 0.0050953 | -0.015109 | 0 | 0 |  | 138
DUP1_V | DUP1-V | 8564 | DUP1-V 4 | 43.801 |  |  |  | SOUTH2001 | VICTORIA | 0.0087146 | -0.0225 | 0.38171 | -0.98554 |  | 138
DUP2_V | DUP2-V | 8565 | DUP2-V 4 |  |  |  |  | SOUTH2001 | VICTORIA | 0.0087146 | -0.0225 | 0 | 0 |  | 138
WEAVERRD | WEAVERRD | 8572 | WEVR RD2 | 4.026 |  |  |  | SOUTH2001 | VICTORIA | 0.0087715 | -0.022478 | 0.035314 | -0.090498 |  | 69
RUNGE | RUNGE | 8573 | RUNGE 2 | 1.063 |  |  |  | SOUTH2001 | KARNES | 0.011259 | -0.02837 | 0.011968 | -0.030157 |  | 69
NORDHEIM | NORDHEIM | 8574 | NRDHEIM2 | 2.394 |  |  |  | SOUTH2001 | DEWITT | 0.010724 | -0.028438 | 0.025673 | -0.06808 |  | 69
YORKTOWN | YORKTOWN | 8575 | YRKTOWN2 | 9.358 |  |  |  | SOUTH2001 | DEWITT | 0.010229 | -0.028501 | 0.095725 | -0.26671 |  | 69
HOCHHEIM | HOCHHEIM | 8577 | HOCH.TP2 |  |  |  |  | SOUTH2001 | DEWITT | 0.0092723 | -0.029348 | 0 | 0 |  | 69
HOCHHEIM | HOCHHEIM | 8578 | HOCHEIM2 | 0.01 |  |  |  | SOUTH2001 | DEWITT | 0.0092723 | -0.029348 | 9.2723e-05 | -0.00029348 |  | 69
MALONE | MALONE | 8579 | MALONE 2 | 0.725 |  |  |  | SOUTH2001 | GUADALUPE | 0.0093261 | -0.031657 | 0.0067614 | -0.022951 |  | 69
NIXON | NIXON | 8580 | NIXON 2 | 7.073 |  |  |  | SOUTH2001 | GONZALES | 0.010078 | -0.030597 | 0.071284 | -0.21642 |  | 69
MAGNOLIA | MAGNOLIA | 8581 | MAG.TP 2 |  |  |  |  | SOUTH2001 | KARNES | 0.011109 | -0.029303 | 0 | 0 |  | 69
NIXONLCR | NIXONLCR | 8582 | NIXTAP 2 |  |  |  |  | SOUTH2001 | GONZALES | 0.0099595 | -0.030747 | 0 | 0 |  | 69
MAGNOLIA | MAGNOLIA | 8583 | MAGNOLA2 | 0.313 |  |  |  | SOUTH2001 | KARNES | 0.011109 | -0.029303 | 0.0034772 | -0.0091718 |  | 69
CHASEFLD | CHASEFLD | 8584 | C.FLD T2 |  |  |  |  | SOUTH2001 | BEE | 0.01139 | -0.025777 | 0 | 0 |  | 69
CHASEFLD | CHASEFLD | 8585 | C.FLD 2 | 3.292 |  |  |  | SOUTH2001 | BEE | 0.011457 | -0.025805 | 0.037716 | -0.08495 |  | 69
BERCLAIR | BERCLAIR | 8586 | BERCLAR2 | 0.47 |  |  |  | SOUTH2001 | BEE | 0.011016 | -0.025322 | 0.0051773 | -0.011901 |  | 69
GOLIAD | GOLIAD | 8587 | GOLIAD 2 | 7.573 |  |  |  | SOUTH2001 | GOLIAD | 0.010115 | -0.024228 | 0.076598 | -0.18348 |  | 69
FANNIN | FANNIN | 8589 | FAN.CPL2 | 0.049 |  |  |  | SOUTH2001 | GOLIAD | 0.0096256 | -0.023634 | 0.00047165 | -0.0011581 |  | 69
OCONNER | OCONNER | 8591 | OCONNER2 | 0.5 |  |  |  | SOUTH2001 | REGUGIO | 0.0091706 | -0.022901 | 0.0045853 | -0.01145 |  | 69
NORMANNA | NORMANNA | 8592 | NORMANA2 | 0.46 |  |  |  | SOUTH2001 | BEE | 0.011683 | -0.026722 | 0.0053744 | -0.012292 |  | 69
PETTUS | PETTUS | 8593 | PETTUS 2 | 3.174 |  |  |  | SOUTH2001 | BEE | 0.011749 | -0.027158 | 0.037291 | -0.086199 |  | 69
FASHING | FASHING | 8598 | COY CTY2 |  |  |  |  | SOUTH2001 | ATASCOSA | 0.016747 | -0.02988 | 0 | 0 |  | 69
FASHING | FASHING | 8599 | FASHNG 2 | 0.01 |  |  |  | SOUTH2001 | ATASCOSA | 0.016747 | -0.02988 | 0.00016747 | -0.0002988 |  | 69
COY_CITY | COY_CITY | 8600 | COY C.T2 |  |  |  |  | SOUTH2001 | ATASCOSA | 0.016747 | -0.02988 | 0 | 0 |  | 69
IMOGENE | IMOGENE | 8603 | IMOG.TP2 |  |  |  |  | SOUTH2001 | ATASCOSA | 0.018379 | -0.03077 | 0 | 0 |  | 69
IMOGENE | IMOGENE | 8604 | IMOGNE 2 | 0.01 |  |  |  | SOUTH2001 | ATASCOSA | 0.018379 | -0.03077 | 0.00018379 | -0.0003077 |  | 69
JOURDNTN | JOURDNTN | 8607 | JOURDTN2 | 10.825 |  |  |  | SOUTH2001 | ATASCOSA | 0.019389 | -0.031147 | 0.20988 | -0.33716 |  | 69
COTULLA | COTULLA | 8610 | COTULLA4 | 7.632 |  |  |  | SOUTH2001 | LA SALLE | 0.028609 | -0.033642 | 0.21834 | -0.25675 |  | 138
BIG_WELL | BIG_WELL | 8613 | B WELLS4 | 1.656 |  |  |  | SOUTH2001 | DIMMIT | 0.037632 | -0.036618 | 0.062319 | -0.06064 |  | 138
ENCINAL | ENCINAL | 8619 | ENCINL 4 | 1.567 |  |  |  | SOUTH2001 | LA SALLE | 0.027717 | -0.032793 | 0.043432 | -0.051387 |  | 138
LYTLE2 | LYTLE2 | 8622 | LYTLE 2 | 1.228 |  |  |  | SOUTH2001 | MEDINA | 0.026555 | -0.033706 | 0.03261 | -0.041391 |  | 69
KNIPPA | KNIPPA | 8628 | KNIPPA 2 | 1.43 |  |  |  | SOUTH2001 | UVALDE | 0.064065 | -0.045089 | 0.091613 | -0.064477 |  | 69
SABINAL | SABINAL | 8630 | SABINAL2 | 2.332 |  |  |  | SOUTH2001 | UVALDE | 0.064065 | -0.045089 | 0.1494 | -0.10515 |  | 69
CAMPWOOD | CAMPWOOD | 8633 | CMPWOOD2 | 3.595 |  |  |  | SOUTH2001 | EDWARDS | 0.10957 | -0.059203 | 0.3939 | -0.21284 |  | 69
HEIGHTS | HEIGHTS | 8636 | HEIGHTS2 | 60.347 |  |  |  | SOUTH2001 | WEBB | 0.026769 | -0.031542 | 1.6154 | -1.9034 |  | 69
ANNA_ST | ANNA_ST | 8639 | ANNA ST2 | 36.581 |  |  |  | SOUTH2001 | WEBB | 0.026769 | -0.031542 | 0.97923 | -1.1538 |  | 69
WASH_ST | WASH_ST | 8642 | WASH ST2 | 46.475 |  |  |  | SOUTH2001 | WEBB | 0.026769 | -0.031542 | 1.2441 | -1.4659 |  | 69
MINES_RD | MINES_RD | 8643 | MINESRD4 | 13.48 |  |  |  | SOUTH2001 | WEBB | 0.028599 | -0.032297 | 0.38552 | -0.43537 |  | 138
DEL_MAR | DEL_MAR | 8645 | DEL MAR4 | 37.403 |  |  |  | SOUTH2001 | WEBB | 0.026916 | -0.03165 | 1.0068 | -1.1838 |  | 138
RIO_BRAV | RIO_BRAV | 8646 | RIOBRAV4 | 8.278 |  |  |  | SOUTH2001 | WEBB | 0.025103 | -0.030919 | 0.2078 | -0.25595 |  | 138
UNIV4 | UNIV4 | 8647 | UNIVERS4 | 6.975 |  |  |  | SOUTH2001 | WEBB | 0.026762 | -0.031613 | 0.18666 | -0.2205 |  | 138
GATEWAY4 | GATEWAY4 | 8648 | GATEWAY4 | 18.986 |  |  |  | SOUTH2001 | WEBB | 0.026483 | -0.031557 | 0.5028 | -0.59915 |  | 138
GATEWAY4 | GATEWAY4 | 8649 | GATETPE4 |  |  |  |  | SOUTH2001 | WEBB | 0.026553 | -0.031564 | 0 | 0 |  | 138
GATEWAY4 | GATEWAY4 | 8650 | GATETPW4 |  |  |  |  | SOUTH2001 | WEBB | 0.026412 | -0.031551 | 0 | 0 |  | 138
|  | 8651 | UNIVMEC |  |  |  |  | SOUTH2001 | WEBB | 0.026762 | -0.031613 | 0 | 0 |  | 138
ST_NINO | ST_NINO | 8653 | S.NINO 4 | 43.105 |  |  |  | SOUTH2001 | WEBB | 0.026324 | -0.031483 | 1.1347 | -1.3571 |  | 138
LA_PRYOR | LA_PRYOR | 8672 | LA PRYR2 | 3.674 |  |  |  | SOUTH2001 | ZAVALA | 0.059337 | -0.04353 | 0.21801 | -0.15993 |  | 69
AMSTDTAP | AMSTDTAP | 8684 | AMSTD T4 |  |  |  |  | SOUTH2001 | VAL VERDE | 0.10942 | -0.05903 | 0 | 0 |  | 138
AMSTDTAP | AMSTDTAP | 8686 | AMSIBWC4 |  |  |  |  | SOUTH2001 | VAL VERDE | 0.10942 | -0.05903 | 0 | 0 |  | 138
BUENA_VI | BUENA_VI | 8688 | B VISTA4 | 19.642 |  |  |  | SOUTH2001 | VAL VERDE | 0.10942 | -0.05903 | 2.1492 | -1.1595 |  | 138
DEL_RIO | DEL_RIO | 8690 | DRIOCTY4 | 38.716 |  |  |  | SOUTH2001 | VAL VERDE | 0.10942 | -0.05903 | 4.2363 | -2.2854 |  | 138
MAVERICK | MAVERICK | 8692 | MAVRICK4 | 1.832 |  |  |  | SOUTH2001 | MAVERICK | 0.086365 | -0.051785 | 0.15822 | -0.094869 |  | 138
W_CONOCO | W_CONOCO | 8694 | CNCO.W 4 | 0.833 |  |  |  | SOUTH2001 | MAVERICK | 0.063886 | -0.044721 | 0.053217 | -0.037252 |  | 138
CRESTONI | CRESTONI | 8695 | CRSTNIO4 | 11.1 |  |  |  | SOUTH2001 | DUVAL | 0.019024 | -0.027943 | 0.21117 | -0.31016 |  | 138
RANDADO | RANDADO | 8699 | RANDADO4 | 5.819 |  |  |  | SOUTH2001 | JIM HOGG | 0.021541 | -0.029238 | 0.12535 | -0.17013 |  | 138
RAYMOND1 | RAYMOND1 | 8700 | RAYVL1-2 | 11.761 |  |  |  | SOUTH2001 | WILLACY | 0.011124 | -0.024316 | 0.13083 | -0.28598 |  | 69
MV_YUTT | MV_YUTT | 8702 | MVYTRA4 | 1.978 |  |  |  | SOUTH2001 | KENNEDY | 0.011038 | -0.024262 | 0.021833 | -0.047989 |  | 138
MV_LASAR | MV.LASAR | 8704 | MV.LASR4 | 4.4 |  |  |  | SOUTH2001 | WILLACY | 0.011076 | -0.02429 | 0.048735 | -0.10687 |  | 138
MV_ERAY2 | MV.ERAY2 | 8705 | MV.ERAY4 | 2.146 |  |  |  | SOUTH2001 | WILLACY | 0.011076 | -0.02429 | 0.023769 | -0.052126 |  | 138
S_BENITO | S_BENITO | 8710 | SBENITO2 | 37.365 |  |  |  | SOUTH2001 | CAMERON | 0.011165 | -0.024341 | 0.41717 | -0.90949 |  | 69
CAUSEWAY | CAUSEWAY | 8744 | CAUSWAY4 | 11.074 |  |  |  | SOUTH2001 | CAMERON | 0.011121 | -0.02432 | 0.12315 | -0.26932 |  | 138
MVRANGER | MVRANGER | 8747 | MV.RNGR | 6.501 |  |  |  | SOUTH2001 | CAMERON | 0.01138 | -0.024442 | 0.073982 | -0.1589 |  | 138
RANGERVL | RANGERVL | 8748 | RNGRVLE2 | 3.774 |  |  |  | SOUTH2001 | CAMERON | 0.01133 | -0.024418 | 0.042759 | -0.092155 |  | 69
RIO_RICO | RIO_RICO | 8751 | RIORICO2 | 7.907 |  |  |  | SOUTH2001 | HIDALGO | 0.011448 | -0.024474 | 0.090521 | -0.19352 |  | 69
MV_DOEDN | MV_DOEDN | 8753 | MVDOEYN4 | 16.81 |  |  |  | SOUTH2001 | HIDALGO | 0.011548 | -0.02452 | 0.19411 | -0.41218 |  | 138
MV_ADRHD | MV_ADRHD | 8754 | MVADRHD4 | 10.877 |  |  |  | SOUTH2001 | HIDALGO | 0.011504 | -0.0245 | 0.12513 | -0.26648 |  | 138
|  | 8755 | MVGANDY4 | 12.855 |  |  |  | SOUTH2001 | HIDALGO | 0.011459 | -0.024478 | 0.14731 | -0.31467 |  | 138
HIDALGO | HIDALGO | 8757 | HIDALGO2 | 10.258 |  |  |  | SOUTH2001 | HIDALGO | 0.011856 | -0.024666 | 0.12162 | -0.25302 |  | 69
L_MILPAS | L_MILPAS | 8758 | MVLASMI4 | 15.277 |  |  |  | SOUTH2001 | HIDALGO | 0.011707 | -0.024595 | 0.17884 | -0.37574 |  | 138
MV_ALRDTP | MV_ALRDTP | 8759 | MVABRTP4 |  |  |  |  | SOUTH2001 | HIDALGO | 0.011548 | -0.02452 | 0 | 0 |  | 138
HALL_ACR | HALL_ACR | 8760 | H.ACRES4 | 61.525 |  |  |  | SOUTH2001 | HIDALGO | 0.011727 | -0.024605 | 0.72151 | -1.5138 |  | 138
PHARMVEC | PHARMVEC | 8762 | MV.PHAR4 | 18.343 |  |  |  | SOUTH2001 | HIDALGO | 0.011569 | -0.02453 | 0.2122 | -0.44995 |  | 138
MV_BURNS | MV_BURNS | 8763 | MVBURNS4 | 6.546 |  |  |  | SOUTH2001 | CAMERON | 0.011194 | -0.024353 | 0.073273 | -0.15942 |  | 138
MV_RIOHO | MV_RIOHO | 8764 | MVERIOH4 | 10.007 |  |  |  | SOUTH2001 | CAMERON | 0.011107 | -0.024312 | 0.11114 | -0.24329 |  | 138
MV_HBRG4 | MV_HBRG4 | 8765 | MV.HBRG4 | 6.734 |  |  |  | SOUTH2001 | HIDALGO | 0.011334 | -0.024419 | 0.076321 | -0.16444 |  | 138
MV_CNTRA | MV_CNTRA | 8766 | MVCENTR4 | 13.102 |  |  |  | SOUTH2001 | CAMERON | 0.011116 | -0.024318 | 0.14565 | -0.31861 |  | 138
MV_HW511 | MV_HW511 | 8767 | MVHW5114 | 13.666 |  |  |  | SOUTH2001 | CAMERON | 0.011118 | -0.024318 | 0.15194 | -0.33234 |  | 138
MV_WESL4 | MV_WESL4 | 8768 | MV.WESL4 | 15.95 |  |  |  | SOUTH2001 | HIDALGO | 0.011413 | -0.024457 | 0.18204 | -0.39008 |  | 138
MV_VALV4 | MV_VALV4 | 8769 | MV.VALV4 | 10.304 |  |  |  | SOUTH2001 | HIDALGO | 0.011504 | -0.024499 | 0.11854 | -0.25244 |  | 138
MV_WEDN4 | MV_WEDN4 | 8771 | MV.WEDN4 | 15.01 |  |  |  | SOUTH2001 | HIDALGO | 0.011543 | -0.024518 | 0.17326 | -0.36801 |  | 138
MV_WEDN4 | MV_WEDN4 | 8772 | MV.ALTON | 14.971 |  |  |  | SOUTH2001 | HIDALGO | 0.011543 | -0.024518 | 0.17281 | -0.36706 |  | 138
MV_PALM4 | MV_PALM4 | 8774 | MV.PALM4 | 26.582 |  |  |  | SOUTH2001 | HIDALGO | 0.011552 | -0.024522 | 0.30707 | -0.65185 |  | 138
MV_FAYSW | MV.FAYSW | 8782 | MV.FAYSW |  |  |  |  | SOUTH2001 | HIDALGO | 0.011606 | -0.024548 | 0 | 0 |  | 69
MV_COOK1 | MV.COOK1 | 8783 | MV.COOK1 | 2.522 |  |  |  | SOUTH2001 | HIDALGO | 0.011606 | -0.024548 | 0.02927 | -0.061909 |  | 69
PALMHURS | PALMHURS | 8784 | PALMHST2 | 34.926 |  |  |  | SOUTH2001 | HIDALGO | 0.012031 | -0.024748 | 0.4202 | -0.86436 |  | 69
MV_COOK2 | MV.COOK2 | 8785 | MV.COOK2 | 1.592 |  |  |  | SOUTH2001 | HIDALGO | 0.011606 | -0.024548 | 0.018477 | -0.03908 |  | 69
MV_FAYVL | MV.FAYVL | 8786 | MV.FAYVL | 10.294 |  |  |  | SOUTH2001 | HIDALGO | 0.011606 | -0.024548 | 0.11947 | -0.25269 |  | 69
GOODWIN | GOODWIN | 8788 | GOODWIN2 | 18.195 |  |  |  | SOUTH2001 | HIDALGO | 0.01257 | -0.025003 | 0.22871 | -0.45492 |  | 69
|  | 8790 | MV.RAYTP |  |  |  |  | SOUTH2001 | WILLACY | 0.011076 | -0.02429 | 0 | 0 |  | 138
L_GRULLA | L_GRULLA | 8791 | LAGRULA2 | 13.444 |  |  |  | SOUTH2001 | STARR | 0.013566 | -0.025473 | 0.18238 | -0.34246 |  | 69
ROMA | ROMA | 8794 | ROMA 2 | 13.723 |  |  |  | SOUTH2001 | STARR | 0.015628 | -0.026446 | 0.21446 | -0.36292 |  | 69
ROMA_TAP | ROMA_TAP | 8795 | ROMA TP4 |  |  |  |  | SOUTH2001 | STARR | 0.01654 | -0.026877 | 0 | 0 |  | 138
ROMA | ROMA | 8796 | ROMA 4 |  |  |  |  | SOUTH2001 | STARR | 0.016424 | -0.026822 | 0 | 0 |  | 138
RIO_GRAN | RIO_GRAN | 8797 | RG CTY 2 | 31.191 |  |  |  | SOUTH2001 | STARR | 0.014658 | -0.025988 | 0.4572 | -0.8106 |  | 69
CONTINEN | CONTINEN | 8799 | CONTINL2 | 0.767 |  |  |  | SOUTH2001 | STARR | 0.014719 | -0.026017 | 0.01129 | -0.019955 |  | 69
TATTON | TATTON | 8800 | TATTON 2 | 3.625 |  |  |  | SOUTH2001 | ARANSAS | 0.0094943 | -0.023102 | 0.034417 | -0.083746 |  | 69
HEARD | HEARD | 8802 | HEARD T2 |  |  |  |  | SOUTH2001 | REFUGIO | 0.0095357 | -0.023128 | 0 | 0 |  | 69
HEARD | HEARD | 8803 | HEARD 2 | 0.206 |  |  |  | SOUTH2001 | REFUGIO | 0.0095357 | -0.023128 | 0.0019644 | -0.0047644 |  | 69
WOODSBOR | WOODSBOR | 8804 | WDSBRO 2 | 3.772 |  |  |  | SOUTH2001 | REFUGIO | 0.0095823 | -0.023157 | 0.036144 | -0.087349 |  | 69
BONIVIEW | BONIVIEW | 8805 | BONEVEW2 | 1.058 |  |  |  | SOUTH2001 | REFUGIO | 0.0096724 | -0.023213 | 0.010233 | -0.02456 |  | 69
HOMEPORT | HOMEPORT | 8808 | HOMPRT 4 | 7.698 |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0098324 | -0.02325 | 0.07569 | -0.17898 |  | 138
ODEM | ODEM | 8810 | ODEM 2 | 6.733 |  |  |  | SOUTH2001 | SAN PATRICIO | 0.010458 | -0.024055 | 0.070416 | -0.16197 |  | 69
TAFT | TAFT | 8812 | TAFT 2 | 9.914 |  |  |  | SOUTH2001 | SAN PATRICIO | 0.010091 | -0.023629 | 0.10005 | -0.23426 |  | 69
MID_WAYT | MID-WAYT | 8814 | MIDWY T2 |  |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0099648 | -0.023456 | 0 | 0 |  | 69
MIDWPUMP | MIDWPUMP | 8815 | MIDWAY 2 | 0.549 |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0099648 | -0.023456 | 0.0054707 | -0.012877 |  | 69
I_DUPP1 | I_DUPP1 | 8817 | DUP1-I2 | 6.187 |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0098296 | -0.023245 | 0.060816 | -0.14381 |  | 138
OXY_INGL | OXY_INGL | 8818 | OXYCHEM4 | 114.562 |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0098296 | -0.023245 | 1.1261 | -2.6629 |  | 138
I_DUPP1 | I_DUPP1 | 8819 | DPTP1-I4 | 6.139 |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0098296 | -0.023245 | 0.060344 | -0.1427 |  | 138
OXY_INGL | OXY_INGL | 8820 | OXY1 4 | 114.426 |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0098296 | -0.023245 | 1.1248 | -2.6598 |  | 138
|  | 8821 | TAYLOR | 7.8 |  |  |  | SOUTH2001 | HILDAGO | 0.011844 | -0.02466 | 0.09238 | -0.19235 |  | 138
REYSHERW | REYSHERW | 8832 | REYSHR 4 | 11.45 |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0098296 | -0.023245 | 0.11255 | -0.26615 |  | 138
FULTONCP | FULTONCP | 8839 | FULTN2 2 | 17.046 |  |  |  | SOUTH2001 | ARANSAS | 0.009828 | -0.023254 | 0.16753 | -0.39639 |  | 69
FULTONCP | FULTONCP | 8841 | FULTN1 2 | 14.479 |  |  |  | SOUTH2001 | ARANSAS | 0.009828 | -0.023254 | 0.1423 | -0.33669 |  | 69
MUSTANG | MUSTANG | 8847 | M.ISLND2 | 3.187 |  |  |  | SOUTH2001 | NUECES | 0.010011 | -0.023459 | 0.031906 | -0.074763 |  | 69
N_PADRE | N_PADRE | 8856 | N PADRE2 | 15.488 |  |  |  | SOUTH2001 | NUECES | 0.010102 | -0.023559 | 0.15646 | -0.36488 |  | 69
MCKENZIE | MCKENZIE | 8858 | MCKENZE4 | 14.117 |  |  |  | SOUTH2001 | NUECES | 0.010244 | -0.02378 | 0.14461 | -0.33571 |  | 138
VALERO_E | VALERO_E | 8859 | VALRO E2 | 28.244 |  |  |  | SOUTH2001 | NUECES | 0.010266 | -0.023768 | 0.28995 | -0.67131 |  | 69
HEARN_RD | HEARN_RD | 8860 | HERN RD2 | 32.28 |  |  |  | SOUTH2001 | NUECES | 0.01049 | -0.024017 | 0.3386 | -0.77528 |  | 69
STEVENS | STEVENS | 8862 | STEVEN22 | 2.748 |  |  |  | SOUTH2001 | NUECES | 0.010486 | -0.024022 | 0.028815 | -0.066012 |  | 69
STEVENS | STEVENS | 8864 | STEVEN12 | 2.748 |  |  |  | SOUTH2001 | NUECES | 0.010558 | -0.024138 | 0.029014 | -0.066332 |  | 69
CAL_WWKS | CAL_WWKS | 8865 | WWORKTP2 |  |  |  |  | SOUTH2001 | NUECES | 0.010486 | -0.024022 | 0 | 0 |  | 69
SMITH | SMITH | 8866 | SMITH 2 | 2.562 |  |  |  | SOUTH2001 | NUECES | 0.010558 | -0.024138 | 0.02705 | -0.061842 |  | 69
CUNINGWW | CUNINGWW | 8867 | W WORKS2 | 0.647 |  |  |  | SOUTH2001 | NUECES | 0.010481 | -0.024028 | 0.0067812 | -0.015546 |  | 69
KARON | KARON | 8868 | KARON T2 |  |  |  |  | SOUTH2001 | LIVE OAK | 0.013169 | -0.027521 | 0 | 0 |  | 69
KARON | KARON | 8869 | KARON 2 | 0.069 |  |  |  | SOUTH2001 | LIVE OAK | 0.013169 | -0.027521 | 0.00090868 | -0.001899 |  | 69
AVERY_P1 | AVERY-P1 | 8870 | AVRYP2-2 |  |  |  |  | SOUTH2001 | NUECES | 0.010169 | -0.023653 | 0 | 0 |  | 69
AVERY_P2 | AVERY-P2 | 8871 | AVRYP1-2 |  |  |  |  | SOUTH2001 | NUECES | 0.01017 | -0.023654 | 0 | 0 |  | 69
N_ELLA | N_ELLA | 8878 | N ELLA | 0.647 |  |  |  | SOUTH2001 | JIM WELLS | 0.0132 | -0.025226 | 0.0085407 | -0.016321 |  | 69
CABANISS | CABANISS | 8882 | CABINES4 | 19.388 |  |  |  | SOUTH2001 | NUECES | 0.010194 | -0.023676 | 0.19764 | -0.45903 |  | 138
RODD_FLD | RODD_FLD | 8883 | R.FIELD4 | 34.095 |  |  |  | SOUTH2001 | NUECES | 0.010224 | -0.023693 | 0.34858 | -0.80783 |  | 138
ROBSTWN | ROBSTWN | 8884 | RBSTN T2 |  |  |  |  | SOUTH2001 | NUECES | 0.010491 | -0.024015 | 0 | 0 |  | 69
RBTWNCTY | RBTWNCTY | 8885 | ROBSTWN2 | 10.26 |  |  |  | SOUTH2001 | NUECES | 0.010491 | -0.024015 | 0.10764 | -0.2464 |  | 69
ROB_CPL | ROB_CPL | 8886 | ROB.CPL2 | 3.674 |  |  |  | SOUTH2001 | NUECES | 0.010491 | -0.024015 | 0.038545 | -0.088232 |  | 69
LOYOLA4 | LOYOLA4 | 8887 | LOYOLA 4 | 5.016 |  |  |  | SOUTH2001 | KLEBERG | 0.010891 | -0.024154 | 0.05463 | -0.12115 |  | 138
BANQUETE | BANQUETE | 8888 | BANQUTE2 | 4.595 |  |  |  | SOUTH2001 | NUECES | 0.011369 | -0.024404 | 0.052239 | -0.11214 |  | 69
STADIUM | STADIUM | 8889 | STADIUM2 | 34.464 |  |  |  | SOUTH2001 | JIM WELLS | 0.012371 | -0.024843 | 0.42637 | -0.85619 |  | 69
SAN_DIEG | SAN_DIEG | 8890 | S.DIEGOX | 11.586 |  |  |  | SOUTH2001 | DUVAL | 0.013937 | -0.025566 | 0.16147 | -0.29621 |  | 69
GOVTWELL | GOVTWELL | 8891 | G.WELLS | 4.604 |  |  |  | SOUTH2001 | DUVAL | 0.017476 | -0.027214 | 0.08046 | -0.12529 |  | 69
PREMONT | PREMONT | 8894 | PREMONT2 | 8.846 |  |  |  | SOUTH2001 | JIM WELLS | 0.013816 | -0.025515 | 0.12222 | -0.22571 |  | 69
RACHAL | RACHAL | 8896 | RACHAL 4 | 1.656 |  |  |  | SOUTH2001 | BROOKS | 0.013647 | -0.025464 | 0.022599 | -0.042169 |  | 138
ARMSTRON | ARMSTRON | 8899 | ARMSTNG4 | 0.372 |  |  |  | SOUTH2001 | KENEDY | 0.010974 | -0.024215 | 0.0040824 | -0.0090079 |  | 138
QUALTCH4 | QUALTCH4 | 8900 | QUALTCH4 | 0.029 |  |  |  | SOUTH2001 | NUECES | 0.01018 | -0.023687 | 0.00029523 | -0.00068693 |  | 138
|  | 8904 | CFLD2TP2 |  |  |  |  | SOUTH2001 | BEE | 0.011457 | -0.025805 | 0 | 0 |  | 69
MCOLL_RD | MCOLL_RD | 8908 | MCCOLL 4 | 35.264 |  |  |  | SOUTH2001 | HIDALGO | 0.011603 | -0.024546 | 0.40916 | -0.86559 |  | 138
BLKBYU | BLKBYU | 8911 | BLCBAYU4 |  |  |  |  | SOUTH2001 | VICTORIA | 0.008601 | -0.022089 | 0 | 0 |  | 138
MEDIOCR | MEDIOCR | 8912 | MEDIOCK4 | 0.049 |  |  |  | SOUTH2001 | REFUGIO | 0.0094578 | -0.023233 | 0.00046343 | -0.0011384 |  | 138
COFFPORT | COFFPORT | 8914 | COFEPRT4 | 7.05 |  |  |  | SOUTH2001 | CAMERON | 0.011117 | -0.024318 | 0.078374 | -0.17144 |  | 138
MILO | MILO | 8918 | MILO 4 | 23.11 |  |  |  | SOUTH2001 | WEBB | 0.027601 | -0.031896 | 0.63786 | -0.73713 |  | 138
|  | 8924 | BBGRVEL | 0.48 |  |  |  | SOUTH2001 | COLORADO | 0.0060142 | -0.023124 | 0.0028868 | -0.0111 |  | 69
LGE | LGE | 8925 | LGE |  |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0098296 | -0.023245 | 0 | 0 |  | 138
LGE | LGE | 8926 | LGEGN#1 |  |  | 76 | 160 | SOUTH2001 | SAN PATRICIO | 0.0098296 | -0.023245 | 1.5727 | -3.7191 |  | 13.8
LGE | LGE | 8927 | LGEGN#2 |  | 160 |  |  | SOUTH2001 | SAN PATRICIO | 0.0098296 | -0.023245 | 1.5727 | -3.7191 |  | 13.8
LGE | LGE | 8928 | LGEGN#3 |  | 130 |  |  | SOUTH2001 | SAN PATRICIO | 0.0098296 | -0.023245 | 1.2778 | -3.0218 |  | 13.8
|  | 8930 | ICPGN#1 |  |  | 88.8 | 175 | SOUTH2001 | NUECES | 0.0098296 | -0.023245 | 1.7202 | -4.0678 |  | 18
|  | 8931 | ICPGN#2 |  |  | 88.8 | 175 | SOUTH2001 | NUECES | 0.0098296 | -0.023245 | 1.7202 | -4.0678 |  | 18
|  | 8932 | ICPGN#3 |  |  | 88.8 | 150 | SOUTH2001 | NUECES | 0.0098296 | -0.023245 | 1.4744 | -3.4867 |  | 18
|  | 8933 | FGNTS001 |  |  | 100 | 180 | SOUTH2001 | HIDALGO | 0.012123 | -0.024792 | 2.1822 | -4.4625 |  | 18
|  | 8934 | FGNTS101 |  | 180 |  |  | SOUTH2001 | HIDALGO | 0.012123 | -0.024792 | 2.1822 | -4.4625 |  | 18
|  | 8935 | FGNTS201 |  | 180 |  |  | SOUTH2001 | HIDALGO | 0.012123 | -0.024792 | 2.1822 | -4.4625 |  | 18
|  | 8936 | CALGN#1 |  |  | 116.9 | 250 | SOUTH2001 | HIDALGO | 0.011532 | -0.024512 | 2.8829 | -6.1281 |  | 16
|  | 8937 | CALGN#2 |  |  | 116.9 | 250 | SOUTH2001 | HIDALGO | 0.011532 | -0.024512 | 2.8829 | -6.1281 |  | 16
|  | 8938 | CALGN#3 |  | 250 |  |  | SOUTH2001 | HIDALGO | 0.011532 | -0.024512 | 2.8829 | -6.1281 |  | 16
WHITEPT | WHITEPT | 8956 | WHITEPT |  |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0090532 | -0.022125 | 0 | 0 |  | 345
|  | 8957 | MECLOPN4 | 4.61 |  |  |  | SOUTH2001 | STARR | 0.01919 | -0.028128 | 0.088467 | -0.12967 |  | 138
|  | 8958 | MECBRUTP |  |  |  |  | SOUTH2001 | WEBB | 0.021072 | -0.028894 | 0 | 0 |  | 138
|  | 8959 | AIRLIQ2 | 1.189 |  |  |  | SOUTH2001 | NUECES | 0.010263 | -0.023765 | 0.012203 | -0.028257 |  | 69
WHITEPT | WHITEPT | 8960 | WHITEPT2 |  |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0099558 | -0.023443 | 0 | 0 |  | 69
WHITEPT | WHITEPT | 8961 | WHITEPT2 |  |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0098635 | -0.023275 | 0 | 0 |  | 138
|  | 8963 | HIDGO 4 |  |  |  |  | SOUTH2001 | HIDALGO | 0.011532 | -0.024512 | 0 | 0 |  | 138
|  | 8968 | ICP |  |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0098296 | -0.023245 | 0 | 0 |  | 138
|  | 8969 | CALGN#1 |  |  |  |  | SOUTH2001 | HIDALGO | 0.011532 | -0.024512 | 0 | 0 |  | 138
|  | 8970 | CALGN#2 |  |  |  |  | SOUTH2001 | HIDALGO | 0.011532 | -0.024512 | 0 | 0 |  | 138
|  | 8971 | CALGN#3 |  |  |  |  | SOUTH2001 | HIDALGO | 0.011532 | -0.024512 | 0 | 0 |  | 138
|  | 8978 | AIRLQT 2 |  |  |  |  | SOUTH2001 | NUECES | 0.0098296 | -0.023245 | 0 | 0 |  | 138
|  | 8979 | AIRLQ 2 | 27.478 |  |  |  | SOUTH2001 | NUECES | 0.0098296 | -0.023245 | 0.2701 | -0.63872 |  | 138
FRONTERA | FRONTERA | 8980 | FRONT |  |  |  |  | SOUTH2001 | HIDALGO | 0.012123 | -0.024792 | 0 | 0 |  | 138
HIDALGO | HIDALGO | 8981 | HIDGN1 |  |  | 95 | 175 | SOUTH2001 | HIDALGO | 0.011532 | -0.024512 | 2.0181 | -4.2897 |  | 18
HIDALGO | HIDALGO | 8982 | HIDGN2 |  |  | 95 | 175 | SOUTH2001 | HIDALGO | 0.011532 | -0.024512 | 2.0181 | -4.2897 |  | 18
HIDALGO | HIDALGO | 8983 | HIDGN3 |  | 160 |  |  | SOUTH2001 | HIDALGO | 0.011532 | -0.024512 | 1.8451 | -3.922 |  | 18
|  | 8984 | MARKHMTP |  |  |  |  | SOUTH2001 | MATAGORDA | 0.005655 | -0.016634 | 0 | 0 |  | 69
|  | 8985 | YGNACIO | 1.714 |  |  |  | SOUTH2001 | ZAPATA | 0.023244 | -0.030041 | 0.03984 | -0.051491 |  | 138
|  | 8988 | WPT2DUM |  |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0094478 | -0.022685 | 0 | 0 |  | 100
|  | 8989 | WPT2TERT |  |  |  |  | SOUTH2001 | SAN PATRICIO | 0.0094478 | -0.022685 | 0 | 0 |  | 13.8
|  | 8997 | FRTTS001 |  |  |  |  | SOUTH2001 | HIDALGO | 0.012123 | -0.024792 | 0 | 0 |  | 138
|  | 8998 | FRTTS101 |  |  |  |  | SOUTH2001 | HIDALGO | 0.012123 | -0.024792 | 0 | 0 |  | 138
|  | 8999 | FRTTS201 |  |  |  |  | SOUTH2001 | HIDALGO | 0.012123 | -0.024792 | 0 | 0 |  | 138
DECKER | DECKER | 9000 | DECKR G1 |  |  | 330 | 347 | SOUTH2001 | TRAVIS | 0.0079011 | -0.037283 | 2.7417 | -12.9373 |  | 24
DECKER | DECKER | 9001 | DECKR G2 |  |  | 415.043 | 432 | SOUTH2001 | TRAVIS | 0.0079103 | -0.037457 | 3.4172 | -16.1815 |  | 24
DECKER | DECKER | 9002 | DECKR G3 |  |  | 55 | 55 | SOUTH2001 | TRAVIS | 0.0079011 | -0.037283 | 0.43456 | -2.0506 |  | 13.8
DECKER | DECKER | 9003 | DECKR G4 |  | 55 |  |  | SOUTH2001 | TRAVIS | 0.0079011 | -0.037283 | 0.43456 | -2.0506 |  | 13.8
DECKER | DECKER | 9004 | DECKR G5 |  | 55 |  |  | SOUTH2001 | TRAVIS | 0.0079011 | -0.037283 | 0.43456 | -2.0506 |  | 13.8
DECKER | DECKER | 9005 | DECKR G6 |  |  | 55 | 55 | SOUTH2001 | TRAVIS | 0.0079011 | -0.037283 | 0.43456 | -2.0506 |  | 13.8
HOLLY | HOLLY | 9012 | HOLLY G1 |  |  | 75 | 97 | SOUTH2001 | TRAVIS | 0.0082725 | -0.037484 | 0.80243 | -3.6359 |  | 13.8
HOLLY | HOLLY | 9013 | HOLLY G2 |  |  | 75 | 98 | SOUTH2001 | TRAVIS | 0.0082725 | -0.037484 | 0.8107 | -3.6735 |  | 13.8
HOLLY | HOLLY | 9014 | HOLLY G3 |  |  | 170 | 191 | SOUTH2001 | TRAVIS | 0.0082724 | -0.037484 | 1.58 | -7.1595 |  | 18
HOLLY | HOLLY | 9015 | HOLLY G4 |  |  | 170 | 193 | SOUTH2001 | TRAVIS | 0.0082725 | -0.037485 | 1.5966 | -7.2346 |  | 20
SANDHSYD | SANDHSYD | 9016 | SANDH G1 |  |  | 20 | 45 | SOUTH2001 | TRAVIS | 0.0080091 | -0.036857 | 0.36041 | -1.6586 |  | 13.8
SANDHSYD | SANDHSYD | 9017 | SANDH G2 |  |  | 20 | 45 | SOUTH2001 | TRAVIS | 0.0080091 | -0.036857 | 0.36041 | -1.6586 |  | 13.8
SANDHSYD | SANDHSYD | 9018 | SANDH G3 |  |  | 20 | 45 | SOUTH2001 | TRAVIS | 0.0080091 | -0.036857 | 0.36041 | -1.6586 |  | 13.8
SANDHSYD | SANDHSYD | 9019 | SANDH G4 |  |  | 20 | 45 | SOUTH2001 | TRAVIS | 0.0080091 | -0.036857 | 0.36041 | -1.6586 |  | 13.8
|  | 9040 | AUSTROP |  |  |  |  | SOUTH2001 | TRAVIS | 0.0062444 | -0.036953 | 0 | 0 |  | 345
GARFIELD | GARFIELD | 9071 | GARFIELD |  |  |  |  | SOUTH2001 | BASTROP | 0.0075521 | -0.036392 | 0 | 0 |  | 138
HOLMAN | HOLMAN | 9073 | HOLMAN |  |  |  |  | SOUTH2001 | FAYETTE | 0.0064419 | -0.031108 | 0 | 0 |  | 345
LYTTON_S | LYTTON_S | 9074 | LYTTON |  |  |  |  | SOUTH2001 | CALDWELL | 0.007546 | -0.034468 | 0 | 0 |  | 345
LYTTON_S | LYTTON_S | 9075 | LYTTON |  |  |  |  | SOUTH2001 | CALDWELL | 0.0078093 | -0.035363 | 0 | 0 |  | 138
MCNEIL | MCNEIL | 9076 | MCNEILW |  |  |  |  | SOUTH2001 | TRAVIS | 0.0083358 | -0.038081 | 0 | 0 |  | 138
MCNEIL | MCNEIL | 9077 | MCNEILS |  |  |  |  | SOUTH2001 | TRAVIS | 0.0083358 | -0.038077 | 0 | 0 |  | 138
MCNEIL | MCNEIL | 9079 | MCNEILN | 68.365 |  |  |  | SOUTH2001 | TRAVIS | 0.0083373 | -0.038087 | 0.56998 | -2.6038 |  | 138
MCNEIL | MCNEIL | 9080 | MCNEIL |  |  |  |  | SOUTH2001 | TRAVIS | 0.008335 | -0.037924 | 0 | 0 |  | 69
BURLESON | BURLESON | 9120 | BURLESON | 64.344 |  |  |  | SOUTH2001 | TRAVIS | 0.0082706 | -0.036939 | 0.53216 | -2.3768 |  | 138
BURLESON | BURLESON | 9121 | BURLESON |  |  |  |  | SOUTH2001 | TRAVIS | 0.0082769 | -0.037337 | 0 | 0 |  | 69
KINGSBER | KINGSBER | 9122 | KINGSMB1 |  |  |  |  | SOUTH2001 | TRAVIS | 0.008048 | -0.03735 | 0 | 0 |  | 138
KINGSBER | KINGSBER | 9123 | KINGS DB | 38.908 |  |  |  | SOUTH2001 | TRAVIS | 0.0080489 | -0.037352 | 0.31317 | -1.4533 |  | 138
KINGSBER | KINGSBER | 9125 | KINGSBRY |  |  |  |  | SOUTH2001 | TRAVIS | 0.0081967 | -0.037439 | 0 | 0 |  | 69
NORTHLAN | NORTHLAN | 9128 | NORTHLND | 72.387 |  |  |  | SOUTH2001 | TRAVIS | 0.0083755 | -0.037817 | 0.60627 | -2.7375 |  | 138
NORTHLAN | NORTHLAN | 9129 | NORTHLND |  |  |  |  | SOUTH2001 | TRAVIS | 0.0083443 | -0.037792 | 0 | 0 |  | 69
NORTHLAN | NORTHLAN | 9130 | NL NEUT |  |  |  |  | SOUTH2001 | TRAVIS | 0.0083391 | -0.037787 | 0 | 0 |  | 0
SEAHOLM | SEAHOLM | 9132 | SEAHM8 | 92.796 |  |  |  | SOUTH2001 | TRAVIS | 0.008354 | -0.037741 | 0.77522 | -3.5022 |  | 138
SEAHOLM | SEAHOLM | 9133 | SEAHM DB | 17.092 |  |  |  | SOUTH2001 | TRAVIS | 0.0083032 | -0.037561 | 0.14192 | -0.64199 |  | 69
SEAHOLM | SEAHOLM | 9134 | SEAHMMB3 |  |  |  |  | SOUTH2001 | TRAVIS | 0.0083032 | -0.037561 | 0 | 0 |  | 69
AUSTIN | AUSTIN | 9139 | AUSTNDAM | 24.129 |  |  |  | SOUTH2001 | TRAVIS | 0.0083607 | -0.037765 | 0.20174 | -0.91122 |  | 138
HICROSS | HICROSS | 9147 | HICRSMB2 | 69.27 |  |  |  | SOUTH2001 | TRAVIS | 0.0084828 | -0.036821 | 0.58761 | -2.5506 |  | 138
HICROSS | HICROSS | 9148 | HICRSMB1 |  |  |  |  | SOUTH2001 | TRAVIS | 0.0084785 | -0.036821 | 0 | 0 |  | 138
ADVANCE | ADVANCE | 9151 | AMD | 16.287 |  |  |  | SOUTH2001 | TRAVIS | 0.0081279 | -0.036939 | 0.13238 | -0.60163 |  | 138
ANGUS | ANGUS | 9155 | ANGUSVAL | 32.574 |  |  |  | SOUTH2001 | TRAVIS | 0.0084149 | -0.037872 | 0.27411 | -1.2336 |  | 138
BARTON | BARTON | 9158 | BARTON | 65.651 |  |  |  | SOUTH2001 | TRAVIS | 0.0083881 | -0.036888 | 0.55069 | -2.4217 |  | 138
BEECREEK | BEECREEK | 9160 | BEECREEK | 44.739 |  |  |  | SOUTH2001 | TRAVIS | 0.0083615 | -0.037767 | 0.37408 | -1.6897 |  | 138
BERGSTRO | BERGSTRO | 9163 | BERGSTRM | 25.135 |  |  |  | SOUTH2001 | TRAVIS | 0.0080986 | -0.036907 | 0.20356 | -0.92766 |  | 138
|  | 9164 | METCENTR | 15.081 |  |  |  | SOUTH2001 | TRAVIS | 0.0081542 | -0.036939 | 0.12297 | -0.55707 |  | 138
BRACKENR | BRACKENR | 9166 | BRACK | 60.322 |  |  |  | SOUTH2001 | TRAVIS | 0.0082725 | -0.037485 | 0.49901 | -2.2612 |  | 69
BRODIE | BRODIE | 9169 | BRODIE | 53.988 |  |  |  | SOUTH2001 | TRAVIS | 0.0081692 | -0.036311 | 0.44104 | -1.9604 |  | 138
CAMERON | CAMERON | 9171 | CAMERON | 46.649 |  |  |  | SOUTH2001 | TRAVIS | 0.0082102 | -0.03776 | 0.383 | -1.7614 |  | 138
CARSON | CARSON | 9175 | CARSON | 26.14 |  |  |  | SOUTH2001 | TRAVIS | 0.0081343 | -0.036792 | 0.21263 | -0.96174 |  | 138
CARDINAL | CARDINAL | 9179 | CARDINAL | 59.92 |  |  |  | SOUTH2001 | TRAVIS | 0.0082909 | -0.037456 | 0.49679 | -2.2444 |  | 69
COMMON | COMMON | 9183 | COMMONFD | 50.268 |  |  |  | SOUTH2001 | TRAVIS | 0.0083952 | -0.037148 | 0.42201 | -1.8673 |  | 138
DAFFIN | DAFFIN | 9184 | DAFFIN G | 25.536 |  |  |  | SOUTH2001 | TRAVIS | 0.0077779 | -0.03749 | 0.19862 | -0.95733 |  | 138
DECKER | DECKER | 9187 | DECKER |  |  |  |  | SOUTH2001 | TRAVIS | 0.0079103 | -0.037457 | 0 | 0 |  | 138
DECKER | DECKER | 9188 | DECK_MB2 |  |  |  |  | SOUTH2001 | TRAVIS | 0.0079011 | -0.037283 | 0 | 0 |  | 138
TRIDGE | TRIDGE | 9190 | TECHRIDG | 19.907 |  |  |  | SOUTH2001 | TRAVIS | 0.0082517 | -0.038089 | 0.16427 | -0.75824 |  | 138
DESSAU | DESSAU | 9193 | DESSAU | 39.209 |  |  |  | SOUTH2001 | TRAVIS | 0.008128 | -0.037838 | 0.31869 | -1.4836 |  | 138
ED_BLUES | ED_BLUES | 9196 | ED BLUE | 62.334 |  |  |  | SOUTH2001 | TRAVIS | 0.0079984 | -0.037388 | 0.49858 | -2.3306 |  | 138
FISKVILL | FISKVILL | 9199 | FISKVILL | 48.761 |  |  |  | SOUTH2001 | TRAVIS | 0.008264 | -0.037895 | 0.40296 | -1.8478 |  | 138
GROVE | GROVE | 9200 | GROVE | 25.135 |  |  |  | SOUTH2001 | TRAVIS | 0.008126 | -0.036983 | 0.20425 | -0.92956 |  | 138
HAMILTN | HAMILTN | 9202 | HAMILMB2 | 35.289 |  |  |  | SOUTH2001 | TRAVIS | 0.0084167 | -0.037932 | 0.29702 | -1.3386 |  | 138
HAMILTN | HAMILTN | 9203 | HAMILMB1 | 42.427 |  |  |  | SOUTH2001 | TRAVIS | 0.0084164 | -0.03793 | 0.35708 | -1.6093 |  | 138
HARRIS | HARRIS | 9204 | HARRIS |  |  |  |  | SOUTH2001 | TRAVIS | 0.0082725 | -0.037485 | 0 | 0 |  | 69
HIDDENVL | HIDDENVL | 9207 | HIDDENVL | 23.325 |  |  |  | SOUTH2001 | TRAVIS | 0.0084025 | -0.037414 | 0.19599 | -0.87269 |  | 138
HOLLY | HOLLY | 9212 | HOLLYMB1 |  |  |  |  | SOUTH2001 | TRAVIS | 0.0082725 | -0.037484 | 0 | 0 |  | 69
HOLLY | HOLLY | 9213 | HOLLYMB2 |  |  |  |  | SOUTH2001 | TRAVIS | 0.0082725 | -0.037484 | 0 | 0 |  | 69
HOLLY | HOLLY | 9214 | HOLLYMB3 |  |  |  |  | SOUTH2001 | TRAVIS | 0.0082724 | -0.037484 | 0 | 0 |  | 69
HOLLY | HOLLY | 9215 | HOLLYMB4 |  |  |  |  | SOUTH2001 | TRAVIS | 0.0082725 | -0.037485 | 0 | 0 |  | 69
SANDHSYD | SANDHSYD | 9216 | SANDHSYD |  |  |  |  | SOUTH2001 | TRAVIS | 0.0080091 | -0.036857 | 0 | 0 |  | 138
HWRDLN | HWRDLN | 9217 | HOWARD | 39.009 |  |  |  | SOUTH2001 | TRAVIS | 0.0082957 | -0.038179 | 0.32361 | -1.4893 |  | 138
JETT | JETT | 9220 | JETT | 46.247 |  |  |  | SOUTH2001 | TRAVIS | 0.0084126 | -0.037789 | 0.38906 | -1.7476 |  | 138
JOLLYVIL | JOLLYVIL | 9223 | JOLLYVIL | 53.185 |  |  |  | SOUTH2001 | WILLIAMSON | 0.0090385 | -0.038448 | 0.48071 | -2.0448 |  | 138
KOENIG | KOENIG | 9227 | KOENIG | 78.419 |  |  |  | SOUTH2001 | TRAVIS | 0.0083254 | -0.037745 | 0.65287 | -2.9599 |  | 69
LAKESHOR | LAKESHOR | 9228 | LAKESHOR | 24.129 |  |  |  | SOUTH2001 | TRAVIS | 0.0083654 | -0.037781 | 0.20185 | -0.91163 |  | 138
LAKEWY | LAKEWY | 9235 | LAKEWAY | 12.567 |  |  |  | SOUTH2001 | TRAVIS | 0.011888 | -0.039679 | 0.1494 | -0.49864 |  | 138
MAGPLANT | MAGPLANT | 9239 | MAGPLANT | 71.382 |  |  |  | SOUTH2001 | TRAVIS | 0.0083396 | -0.037858 | 0.59529 | -2.7024 |  | 69
NORTH | NORTH | 9243 | NORTH | 47.453 |  |  |  | SOUTH2001 | TRAVIS | 0.0083063 | -0.037651 | 0.39416 | -1.7866 |  | 69
|  | 9244 | FIESTA | 18.298 |  |  |  | SOUTH2001 | TRAVIS | 0.0082985 | -0.037613 | 0.15185 | -0.68824 |  | 69
OAKHILL | OAKHILL | 9247 | OAKHILL | 56.301 |  |  |  | SOUTH2001 | TRAVIS | 0.008261 | -0.036553 | 0.4651 | -2.058 |  | 138
ONION | ONION | 9251 | ONION CK | 12.064 |  |  |  | SOUTH2001 | TRAVIS | 0.0080091 | -0.036857 | 0.096622 | -0.44464 |  | 138
PATTON | PATTON | 9253 | PATTON | 53.285 |  |  |  | SOUTH2001 | TRAVIS | 0.0082783 | -0.036598 | 0.44111 | -1.9501 |  | 138
PEDERNAL | PEDERNAL | 9257 | PEDERNAL | 45.604 |  |  |  | SOUTH2001 | TRAVIS | 0.0082725 | -0.037485 | 0.37726 | -1.7094 |  | 69
PILOT | PILOT | 9259 | PILOT KB | 8.144 |  |  |  | SOUTH2001 | TRAVIS | 0.0081406 | -0.036649 | 0.066297 | -0.29847 |  | 138
RIVER | RIVER | 9260 | RIVERPLS | 7.842 |  |  |  | SOUTH2001 | TRAVIS | 0.0084085 | -0.037635 | 0.06594 | -0.29513 |  | 138
SALEM1 | SALEM1 | 9263 | SALEMWLK | 74.8 |  |  |  | SOUTH2001 | TRAVIS | 0.0084572 | -0.036837 | 0.6326 | -2.7554 |  | 138
SLAUGHTE | SLAUGHTE | 9267 | SLAUGHTR | 38.707 |  |  |  | SOUTH2001 | TRAVIS | 0.0081164 | -0.036172 | 0.31416 | -1.4001 |  | 138
SPRINKLE | SPRINKLE | 9271 | SPRINKLE | 30.161 |  |  |  | SOUTH2001 | TRAVIS | 0.0080681 | -0.037691 | 0.24334 | -1.1368 |  | 138
STECK | STECK | 9275 | STECK | 53.586 |  |  |  | SOUTH2001 | TRAVIS | 0.008392 | -0.037863 | 0.4497 | -2.0289 |  | 138
SUMMIT | SUMMIT | 9279 | SUMMITN | 44.739 |  |  |  | SOUTH2001 | TRAVIS | 0.0084171 | -0.038108 | 0.37657 | -1.7049 |  | 138
SUMMIT | SUMMIT | 9280 | SUMMITS | 37.601 |  |  |  | SOUTH2001 | TRAVIS | 0.0083867 | -0.037986 | 0.31535 | -1.4283 |  | 138
TRADPOST | TRADPOST | 9282 | TRADPOST | 24.33 |  |  |  | SOUTH2001 | TRAVIS | 0.010748 | -0.038612 | 0.26151 | -0.93944 |  | 138
WALNUT | WALNUT | 9284 | WALNUTCK | 32.373 |  |  |  | SOUTH2001 | TRAVIS | 0.0079863 | -0.037322 | 0.25854 | -1.2082 |  | 138
WARREN | WARREN | 9286 | WARREN | 49.967 |  |  |  | SOUTH2001 | TRAVIS | 0.0083684 | -0.037792 | 0.41814 | -1.8884 |  | 138
WHELESS | WHELESS | 9291 | WHELESS | 40.718 |  |  |  | SOUTH2001 | TRAVIS | 0.0081474 | -0.037601 | 0.33174 | -1.531 |  | 138
WILLIAMS | WILLIAMS | 9295 | WILIAMSN | 79.424 |  |  |  | SOUTH2001 | TRAVIS | 0.0086139 | -0.038159 | 0.68415 | -3.0308 |  | 138
ZILKER | ZILKER | 9299 | ZILKER | 18.901 |  |  |  | SOUTH2001 | TRAVIS | 0.0083006 | -0.037539 | 0.15689 | -0.70953 |  | 69
|  | 13131 | CALFRE1G |  | 189 |  |  | SOUTH2001 | FREESTONE | -0.0093613 | -0.069903 | -1.7693 | -13.2116 |  | 18
|  | 13132 | CALFRE2G |  | 189 |  |  | SOUTH2001 | FREESTONE | -0.0093613 | -0.069903 | -1.7693 | -13.2116 |  | 18
|  | 13133 | CALFRE3G |  | 189 |  |  | SOUTH2001 | FREESTONE | -0.0093613 | -0.069903 | -1.7693 | -13.2116 |  | 18
|  | 13134 | CALFRE4G |  | 189 |  |  | SOUTH2001 | FREESTONE | -0.0094979 | -0.069716 | -1.7951 | -13.1764 |  | 18
|  | 13135 | CALFRE5G |  | 189 |  |  | SOUTH2001 | FREESTONE | -0.0094979 | -0.069716 | -1.7951 | -13.1764 |  | 18
|  | 13136 | CALFRE6G |  | 189 |  |  | SOUTH2001 | FREESTONE | -0.0094979 | -0.069716 | -1.7951 | -13.1764 |  | 18
GAF | GAF | 38500 | GAF | 6.9 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 2.622e-13 | 3.312e-13 |  | 138
TEJAS | TEJAS | 38530 | TEJAS | 17.7 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 6.726e-13 | 8.496e-13 |  | 138
COMAN_TN | COMAN TN | 38560 | COMANCHE |  |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 0 | 0 |  | 138
AMOCOOIL | AMOCOOIL | 38570 | AMOCOOIL | 180 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 6.84e-12 | 8.64e-12 |  | 138
AMOCOOIL | AMOCOOIL | 38580 | AMOLCGN1 |  |  | 60 | 92.4 | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 3.5112e-12 | 4.4352e-12 |  | 13.8
AMOCOOIL | AMOCOOIL | 38590 | AMOLCGN2 |  |  | 60 | 92.4 | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 3.5112e-12 | 4.4352e-12 |  | 13.8
AMOCOOIL | AMOCOOIL | 38600 | AMOLCGN3 |  |  | 30 | 59.63 | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 2.2659e-12 | 2.8622e-12 |  | 13.8
AMOCOOIL | AMOCOOIL | 38610 | AMOLCGN4 |  |  | 30 | 89.5 | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 3.401e-12 | 4.296e-12 |  | 13.8
AMOCOTN | AMOCOTN | 38620 | AMOCO |  |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 0 | 0 |  | 138
AMOCOTN | AMOCOTN | 38650 | AMOCO |  |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 0 | 0 |  | 69
CARBDOCK | CARBDOCK | 38670 | CARBDOCK | 3.2 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 1.216e-13 | 1.536e-13 |  | 69
AMCOCHEM | AMCOCHEM | 38680 | AMCOCHEM | 62.1 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 2.3598e-12 | 2.9808e-12 |  | 138
AMCOCHEM | AMCOCHEM | 38690 | AMCHMCGN | 30 |  | 30 | 40 | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 2.66e-12 | 3.36e-12 |  | 13.8
CADDOTN | CADDOTN | 38710 | CADDO |  |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 0 | 0 |  | 138
APACHE | APACHE | 38720 | APACHE |  |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 0 | 0 |  | 138
UCC_COGN | UCC COGN | 38730 | UCC COGN | 60 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 2.28e-12 | 2.88e-12 |  | 138
HEIGHTTN | HEIGHTTN | 38740 | HEIGHTS | 20.4 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 7.752e-13 | 9.792e-13 |  | 138
HEIGHTTN | HEIGHTTN | 38770 | HEIGHTS |  |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 0 | 0 |  | 69
AMOCOPL | AMOCOPL | 38790 | AMOCOPL |  |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 0 | 0 |  | 69
FRWYPARK | FRWYPARK | 38820 | FRWYPARK | 36.7 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 1.3946e-12 | 1.7616e-12 |  | 138
DICKNSON | DICKNSON | 38850 | DICKNSON | 43.7 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 1.6606e-12 | 2.0976e-12 |  | 138
SOUSHORE | SOUSHORE | 38890 | SOUSHORE | 32.1 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 1.2198e-12 | 1.5408e-12 |  | 138
LEAGCITY | LEAGCITY | 38920 | LEAGCITY | 29.3 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 1.1134e-12 | 1.4064e-12 |  | 138
MAGNO_TN | MAGNO TN | 38950 | MAGNOLIA | 31.5 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 1.197e-12 | 1.512e-12 |  | 138
FRDSWOOD | FRDSWOOD | 38980 | FRDSWOOD | 62.3 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 2.3674e-12 | 2.9904e-12 |  | 138
|  | 38990 | SEMINOLE | 15.6 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 5.928e-13 | 7.488e-13 |  | 138
HASTINGS | HASTINGS | 39010 | HASTINGS | 8.1 |  |  |  | SOUTH2001 | BRAZORIA | 3.8e-14 | 4.8e-14 | 3.078e-13 | 3.888e-13 |  | 138
ALVIN | ALVIN | 39030 | ALVIN | 64.6 |  |  |  | SOUTH2001 | BRAZORIA | 3.8e-14 | 4.8e-14 | 2.4548e-12 | 3.1008e-12 |  | 138
TERMINAL | TERMINAL | 39070 | TERMINAL |  |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 0 | 0 |  | 69
MARTHNOL | MARTHNOL | 39090 | MARTHNOL | 13.4 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 5.092e-13 | 6.432e-13 |  | 69
PHIBRO | PHIBRO | 39110 | PHIBRO | 33.8 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 1.2844e-12 | 1.6224e-12 |  | 69
PHIBRO | PHIBRO | 39120 | PHIBCGN1 | 10 |  | 10 | 19 | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 1.102e-12 | 1.392e-12 |  | 13.8
PHIBRO | PHIBRO | 39130 | PHIBCGN2 | 10 |  | 10 | 19 | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 1.102e-12 | 1.392e-12 |  | 13.8
TXCITYMN | TXCITYMN | 39140 | TXCITYMN |  |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 0 | 0 |  | 69
S_LCOGEN | S_LCOGEN | 39180 | S&LCOGEN | 30 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 1.14e-12 | 1.44e-12 |  | 69
S_LCOGEN | S_LCOGEN | 39190 | S&LCGN1 |  |  | 30 | 48.4 | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 1.8392e-12 | 2.3232e-12 |  | 13.8
STRLNG_3 | STRLNG#3 | 39200 | STRLNG#3 | 62 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 2.356e-12 | 2.976e-12 |  | 69
NTHSDTAP | NTHSDTAP | 39220 | NTHSDTAP |  |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 0 | 0 |  | 69
NORTHSDE | NORTHSDE | 39250 | NORTHSDE | 28.2 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 1.0716e-12 | 1.3536e-12 |  | 69
TXCITYWT | TXCITYWT | 39280 | TXCITYWT | 0.9 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 3.42e-14 | 4.32e-14 |  | 69
INTRCITY | INTRCITY | 39310 | INTRCITY | 2 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 7.6e-14 | 9.6e-14 |  | 69
LAMARQUE | LAMARQUE | 39340 | LAMARQUE | 23.1 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 8.778e-13 | 1.1088e-12 |  | 69
CARBIDE | CARBIDE | 39360 | CARBIDE |  |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 0 | 0 |  | 69
LINDE | LINDE | 39380 | LINDE | 0.9 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 3.42e-14 | 4.32e-14 |  | 69
GRANTAVE | GRANTAVE | 39400 | GRANTAVE |  |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 0 | 0 |  | 69
ARCOPL | ARCOPL | 39410 | ARCOPL | 4.3 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 1.634e-13 | 2.064e-13 |  | 69
LIQDCARB | LIQDCARB | 39430 | LIQDCARB | 1.4 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 5.32e-14 | 6.72e-14 |  | 69
MARTHNPL | MARTHNPL | 39440 | MARTHNPL | 2.5 |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 9.5e-14 | 1.2e-13 |  | 69
UCC_COGN | UCC COGN | 39470 | UCCCGNSG |  |  | 30 | 36 | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 1.368e-12 | 1.728e-12 |  | 13.8
UCC_COGN | UCC COGN | 39480 | UCCCGNGG |  |  | 30 | 34 | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 1.292e-12 | 1.632e-12 |  | 13.8
WCOLMAIN | WCOLMAIN | 39500 | WCOLMAIN |  |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0 | 0 |  | 138
WCOLLOCL | WCOLLOCL | 39530 | WCOLLOCL | 13.4 |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0.01995 | -0.06385 |  | 138
ANGLETON | ANGLETON | 39560 | ANGLETON | 57.9 |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0.086203 | -0.27589 |  | 138
BRAZORIA | BRAZORIA | 39600 | BRAZORIA | 16.8 |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0.025012 | -0.08005 |  | 138
BRAZORIA | BRAZORIA | 39630 | BRAZORIA |  |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0 | 0 |  | 69
DOW_PUMP | DOW PUMP | 39650 | DOW PUMP | 2 |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0.0029776 | -0.0095298 |  | 69
CLMNSTAP | CLMNSTAP | 39670 | CLMNSTAP |  |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0 | 0 |  | 69
CLEMENS | CLEMENS | 39680 | CLEMENS | 2.8 |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0.0041687 | -0.013342 |  | 69
SWEENY | SWEENY | 39700 | SWEENY | 14.4 |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0.021439 | -0.068615 |  | 69
P66_2 | P66#2 | 39720 | P66#2 |  |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0 | 0 |  | 69
P66_3 | P66#3 | 39730 | P66#3 |  |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0 | 0 |  | 69
AMCOASHW | AMCOASHW | 39740 | AMCOASHW |  |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0 | 0 |  | 69
OLDOCEAN | OLDOCEAN | 39750 | OLDOCEAN | 3.4 |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0.005062 | -0.016201 |  | 69
SCLPCOGN | SCLPCOGN | 39760 | SCLP#1 |  |  | 60 | 118 | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0.17568 | -0.56226 |  | 13.8
SCLPCOGN | SCLPCOGN | 39770 | SCLP#2 |  |  | 60 | 118 | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0.17568 | -0.56226 |  | 13.8
SCLPCOGN | SCLPCOGN | 39775 | SCLP#4 |  |  | 55 | 118 | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0.17568 | -0.56226 |  | 13.8
AMCOEAST | AMCOEAST | 39780 | AMCOEAST |  |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0 | 0 |  | 69
SCLPCOGN | SCLPCOGN | 39790 | SCLP#3 |  |  | 55 | 118 | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0.17568 | -0.56226 |  | 13.8
AMCOMAIN | AMCOMAIN | 39810 | AMCOMAIN | 1.4 |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0.0020844 | -0.0066709 |  | 69
AMBRLTAP | AMBRLTAP | 39830 | AMBRLTAP |  |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0 | 0 |  | 69
SCLPCOGN | SCLPCOGN | 39860 | SCLPCOGN |  |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0 | 0 |  | 138
PHILLPS5 | PHILLPS5 | 39870 | PHILLPS5 |  |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0 | 0 |  | 69
SCLPCOGN | SCLPCOGN | 39880 | SCLPCOGN | 120 |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0.17866 | -0.57179 |  | 69
PHILLPS2 | PHILLPS2 | 39890 | PHILLPS2 |  |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0 | 0 |  | 69
PHILLPS3 | PHILLPS3 | 39910 | PHILLPS3 |  |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0 | 0 |  | 69
PHLLPSOP | PHLLPSOP | 39930 | PHLLPSOP |  |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0 | 0 |  | 69
PHLLPSTF | PHLLPSTF | 39940 | PHLLPSTF |  |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0 | 0 |  | 69
TNP_ONE | TNP ONE | 39950 | TNP ONE |  |  |  |  | SOUTH2001 | ROBERTSON | -0.0062568 | 0.032427 | 0 | 0 |  | 345
TNP_ONE | TNP ONE | 39960 | TNPONE#1 |  |  | 149.593 | 153 | SOUTH2001 | ROBERTSON | -0.0062568 | 0.032427 | -0.95729 | 4.9613 |  | 18
TNP_ONE | TNP ONE | 39970 | TNPONE#2 |  |  | 151 | 155 | SOUTH2001 | ROBERTSON | -0.0062568 | 0.032427 | -0.96981 | 5.0262 |  | 18
CBY | CBY | 40000 | CEDARP 5 |  |  |  |  | SOUTH2001 | CHAMBERS | -0.00075646 | 0.0024569 | 0 | 0 |  | 345
CBY | CBY | 40010 | CEDARE 8 |  |  |  |  | SOUTH2001 | CHAMBERS | -0.00072936 | 0.0023557 | 0 | 0 |  | 138
_CD | _CD | 40011 | CEDARD 8 | 63.3 |  |  |  | SOUTH2001 | HARRIS | -0.00076089 | 0.0024574 | -0.048165 | 0.15555 |  | 138
_CD | _CD | 40012 | CEDARD 8 | 43.2 |  |  |  | SOUTH2001 | HARRIS | -0.00076124 | 0.0024582 | -0.032886 | 0.1062 |  | 138
CBY | CBY | 40015 | CEDARW |  |  |  |  | SOUTH2001 | CHAMBERS | -0.00075703 | 0.0024465 | 0 | 0 |  | 138
AGR | AGR | 40051 | AGRI__ | 0.4 |  |  |  | SOUTH2001 | HARRIS | -0.00064647 | 0.0020782 | -0.00025859 | 0.00083126 |  | 69
_AZ | _AZ | 40070 | AIRPRO | 100.4 |  |  |  | SOUTH2001 | HARRIS | -0.00070176 | 0.0022629 | -0.070456 | 0.2272 |  | 138
_AI | _AI | 40081 | ALEX_I 9 | 5.8 |  |  |  | SOUTH2001 | HARRIS | -0.00066395 | 0.002135 | -0.0038509 | 0.012383 |  | 69
_AI | _AI | 40082 | ALEX_I 9 | 7.2 |  |  |  | SOUTH2001 | HARRIS | -0.00066399 | 0.0021353 | -0.0047807 | 0.015374 |  | 69
_AU | _AU | 40100 | ANBUSH | 20 |  |  |  | SOUTH2001 | HARRIS | -0.00075252 | 0.0024297 | -0.01505 | 0.048595 |  | 138
APD | APD | 40110 | APLIED | 0.1 |  |  |  | SOUTH2001 | HARRIS | -0.00078073 | 0.0025248 | -7.8073e-05 | 0.00025248 |  | 138
|  | 40111 | OPNAPD 8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00078073 | 0.0025248 | 0 | 0 |  | 138
ATK | ATK | 40120 | ARITEK | 12.8 |  |  |  | SOUTH2001 | HARRIS | -0.0006789 | 0.0021847 | -0.00869 | 0.027964 |  | 138
_AT | _AT | 40130 | ATASCO 8 | 26.8 |  |  |  | SOUTH2001 | HARRIS | -0.00094149 | 0.0029667 | -0.025232 | 0.079509 |  | 138
BBC | BBC | 40140 | BARBUR | 8.9 |  |  |  | SOUTH2001 | HARRIS | -0.00064747 | 0.0020803 | -0.0057625 | 0.018515 |  | 138
BIL | BIL | 40150 | BARHIL | 7.6 |  |  |  | SOUTH2001 | HARRIS | -0.00079944 | 0.0025649 | -0.0060758 | 0.019493 |  | 138
BAY | BAY | 40160 | BTNENY 8 | 99.4 |  |  |  | SOUTH2001 | CHAMBERS | -0.00083142 | 0.002719 | -0.082643 | 0.27027 |  | 138
_BT | _BT | 40170 | BAYTWN 8 | 43.9 |  |  |  | SOUTH2001 | HARRIS | -0.00073301 | 0.0023667 | -0.032179 | 0.1039 |  | 138
_BE | _BE | 40180 | BERTWD 8 | 26.5 |  |  |  | SOUTH2001 | HARRIS | -0.00085089 | 0.0026588 | -0.022548 | 0.070458 |  | 138
BCV | BCV | 40190 | BIGVUE | 35.1 |  |  |  | SOUTH2001 | HARRIS | -0.00086326 | 0.0027731 | -0.0303 | 0.097335 |  | 138
BFM | BFM | 40200 | BIMONT | 13.5 |  |  |  | SOUTH2001 | HARRIS | -0.0006239 | 0.0020035 | -0.0084227 | 0.027047 |  | 138
BOR | BOR | 40210 | BORDEN | 0.4 |  |  |  | SOUTH2001 | HARRIS | -0.00075161 | 0.0024171 | -0.00030064 | 0.00096683 |  | 138
BRN | BRN | 40220 | BRINE_ | 4.7 |  |  |  | SOUTH2001 | CHAMBERS | -0.00078504 | 0.0025247 | -0.0036897 | 0.011866 |  | 138
_BU | _BU | 40231 | BUSCH 9 | 13.4 |  |  |  | SOUTH2001 | HARRIS | -0.00068125 | 0.002183 | -0.0091287 | 0.029252 |  | 69
_BU | _BU | 40232 | BUSCH 9 | 11.7 |  |  |  | SOUTH2001 | HARRIS | -0.00070526 | 0.0022643 | -0.0082516 | 0.026492 |  | 69
CAS | CAS | 40250 | CASTEN | 1.6 |  |  |  | SOUTH2001 | HARRIS | -0.00068749 | 0.0022043 | -0.0011 | 0.0035269 |  | 69
|  | 40255 | CHAMBR 5 |  |  |  |  | SOUTH2001 | CHAMBERS | -0.00083142 | 0.002719 | 0 | 0 |  | 345
CHS | CHS | 40260 | CHAMON | 37.2 |  |  |  | SOUTH2001 | HARRIS | -0.00092084 | 0.0029326 | -0.034255 | 0.10909 | 3 | 138
CHL | CHL | 40270 | CHANEL | 3.4 |  |  |  | SOUTH2001 | HARRIS | -0.00063272 | 0.0020298 | -0.0021512 | 0.0069013 | 4 | 69
_CV | _CV | 40280 | CHANLV |  |  |  |  | SOUTH2001 | HARRIS | -0.00078543 | 0.0025264 | 0 | 0 |  | 138
_CV | _CV | 40290 | CHANLV | 67.6 |  |  |  | SOUTH2001 | HARRIS | -0.00078316 | 0.0025232 | -0.052942 | 0.17057 |  | 69
CVN | CVN | 40300 | CHEVON | 100.3 |  |  |  | SOUTH2001 | HARRIS | -0.00077113 | 0.0024858 | -0.077344 | 0.24933 |  | 138
CHO | CHO | 40310 | CHOATE | 25.9 |  |  |  | SOUTH2001 | HARRIS | -0.00061344 | 0.0019694 | -0.015888 | 0.051007 |  | 138
RIN | RIN | 40320 | CHORIN | 32.7 |  |  |  | SOUTH2001 | HARRIS | -0.00069072 | 0.0022247 | -0.022586 | 0.072749 |  | 138
_CF | _CF | 40330 | CITFIL | 9 |  |  |  | SOUTH2001 | HARRIS | -0.00079346 | 0.0025691 | -0.0071412 | 0.023122 |  | 138
CTY | CTY | 40340 | CITIES | 9.9 |  |  |  | SOUTH2001 | HARRIS | -0.00078803 | 0.002533 | -0.0078015 | 0.025077 |  | 138
_CL | _CL | 40351 | CLINTN98 | 12.4 |  |  |  | SOUTH2001 | HARRIS | -0.00069267 | 0.002228 | -0.0085891 | 0.027628 |  | 138
_CL | _CL | 40352 | CLINTN98 | 24.7 |  |  |  | SOUTH2001 | HARRIS | -0.00067287 | 0.0021543 | -0.01662 | 0.053212 |  | 69
_CO | _CO | 40370 | CONIAL | 3.8 |  |  |  | SOUTH2001 | HARRIS | -0.00067806 | 0.0021831 | -0.0025766 | 0.0082957 |  | 138
_CS | _CS | 40380 | CROSBY 9 | 20.3 |  |  |  | SOUTH2001 | HARRIS | -0.00081444 | 0.0026067 | -0.016533 | 0.052917 |  | 69
_CS | _CS | 40390 | CROSBY 8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00083002 | 0.0026502 | 0 | 0 |  | 138
CRN | CRN | 40400 | CROWN_ | 18.6 |  |  |  | SOUTH2001 | HARRIS | -0.0007091 | 0.0022873 | -0.013189 | 0.042544 |  | 138
DAV | DAV | 40420 | DAVSON | 13.1 |  |  |  | SOUTH2001 | HARRIS | -0.00077937 | 0.0025079 | -0.01021 | 0.032853 |  | 138
|  | 40425 | OPNDAY 8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00083002 | 0.0026502 | 0 | 0 |  | 138
DKR | DKR | 40430 | DECKER | 70 |  |  |  | SOUTH2001 | HARRIS | -0.0007325 | 0.0023562 | -0.051275 | 0.16494 |  | 138
_DE | _DE | 40441 | DEERPK 8 | 24.7 |  |  |  | SOUTH2001 | HARRIS | -0.00073107 | 0.0023519 | -0.018058 | 0.058093 |  | 138
_DE | _DE | 40442 | DEERPK 8 | 27.4 |  |  |  | SOUTH2001 | HARRIS | -0.00066707 | 0.0021457 | -0.018278 | 0.058792 |  | 138
DPW | DPW | 40460 | DEPWTR 8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00078073 | 0.0025248 | 0 | 0 |  | 138
DPW | DPW | 40470 | DEPWTR 9 |  |  |  |  | SOUTH2001 | HARRIS | -0.00062015 | 0.0019908 | 0 | 0 |  | 69
DIB | DIB | 40480 | DIABOX | 41 |  |  |  | SOUTH2001 | HARRIS | -0.00068749 | 0.002211 | -0.028187 | 0.090651 | 5 | 138
DOL | DOL | 40490 | DOWLAP | 15.7 |  |  |  | SOUTH2001 | HARRIS | -0.000692 | 0.0022244 | -0.010864 | 0.034924 |  | 138
EAG | EAG | 40500 | EAGLE_ | 42 |  |  |  | SOUTH2001 | CHAMBERS | -0.00077548 | 0.002498 | -0.03257 | 0.10492 |  | 138
_EP | _EP | 40510 | ENPROD | 23.3 |  |  |  | SOUTH2001 | CHAMBERS | -0.00079208 | 0.0025443 | -0.018455 | 0.059282 | 6 | 138
ETH | ETH | 40520 | EPOTH_ | 18.7 |  |  |  | SOUTH2001 | HARRIS | -0.00075621 | 0.002432 | -0.014141 | 0.045478 |  | 138
EAB | EAB | 40530 | ESBELT | 7.7 |  |  |  | SOUTH2001 | HARRIS | -0.00068754 | 0.002215 | -0.0052941 | 0.017056 |  | 138
EAF | EAF | 40540 | ESFORK | 2.3 |  |  |  | SOUTH2001 | HARRIS | -0.00069739 | 0.0022434 | -0.001604 | 0.0051599 |  | 138
_ET | _ET | 40550 | ETHYL_ | 32.8 |  |  |  | SOUTH2001 | HARRIS | -0.00065826 | 0.0021173 | -0.021591 | 0.069448 |  | 69
_ET | _ET | 40551 | ETH_CLR1 |  |  |  |  | SOUTH2001 | HARRIS | -0.00065826 | 0.0021173 | 0 | 0 |  | 69
_ET | _ET | 40552 | ETH_CLR2 |  |  |  |  | SOUTH2001 | HARRIS | -0.00065826 | 0.0021173 | 0 | 0 |  | 69
_EX | _EX | 40560 | EXPLOR | 5.7 |  |  |  | SOUTH2001 | HARRIS | -0.00088465 | 0.0028595 | -0.0050425 | 0.016299 |  | 138
EXN | EXN | 40570 | EXXON_ | 34.6 |  |  |  | SOUTH2001 | HARRIS | -0.00073298 | 0.0023563 | -0.025361 | 0.081528 | 7 | 138
FED | FED | 40580 | FEDRAL | 0.1 |  |  |  | SOUTH2001 | HARRIS | -0.00076071 | 0.0024461 | -7.6071e-05 | 0.00024461 |  | 138
FDL | FDL | 40590 | FDLITY | 7.6 |  |  |  | SOUTH2001 | HARRIS | -0.00088817 | 0.0028593 | -0.0067501 | 0.02173 |  | 138
FTR | FTR | 40600 | FRONTR |  |  |  |  | SOUTH2001 | GRIMES | -0.0037855 | 0.017654 | 0 | 0 |  | 345
_GP | _GP | 40610 | GALENA 8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00076808 | 0.0024839 | 0 | 0 |  | 138
_GP | _GP | 40611 | GALENA98 | 19.5 |  |  |  | SOUTH2001 | HARRIS | -0.00076801 | 0.0024795 | -0.014976 | 0.04835 |  | 69
_GP | _GP | 40612 | GALENA98 | 32.8 |  |  |  | SOUTH2001 | HARRIS | -0.00076753 | 0.002482 | -0.025175 | 0.081411 |  | 138
_GW | _GW | 40620 | GLENWD 8 | 30.7 |  |  |  | SOUTH2001 | HARRIS | -0.00088881 | 0.0028108 | -0.027287 | 0.086292 |  | 138
GBY | GBY | 40700 | GRNBYU 5 |  |  |  |  | SOUTH2001 | HARRIS | -0.0013358 | 0.0044753 | 0 | 0 |  | 345
GBY | GBY | 40710 | GRNBYUE8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00095356 | 0.0030704 | 0 | 0 |  | 138
GBY | GBY | 40715 | GRNBYUW8 |  |  |  |  | SOUTH2001 | HARRIS | -0.000894 | 0.0029066 | 0 | 0 |  | 138
GBY | GBY | 40720 | GRNBYUA9 |  |  |  |  | SOUTH2001 | HARRIS | -0.0007944 | 0.0025668 | 0 | 0 |  | 69
GBY | GBY | 40725 | GRNBYUB9 |  |  |  |  | SOUTH2001 | HARRIS | -0.00072925 | 0.002347 | 0 | 0 |  | 69
GY | GY | 40751 | GYPSUM | 6.9 |  |  |  | SOUTH2001 | HARRIS | -0.00076765 | 0.0024782 | -0.0052968 | 0.0171 |  | 69
GY | GY | 40752 | GYPSUM |  |  |  |  | SOUTH2001 | HARRIS | -0.00076801 | 0.0024795 | 0 | 0 |  | 69
HAT | HAT | 40770 | HACHER | 34.6 |  |  |  | SOUTH2001 | CHAMBERS | -0.00079614 | 0.0025557 | -0.027546 | 0.088426 |  | 138
HAD | HAD | 40780 | HADEN_ | 9.4 |  |  |  | SOUTH2001 | HARRIS | -0.00077311 | 0.0024864 | -0.0072673 | 0.023372 |  | 138
HNY | HNY | 40790 | HANEY 8 | 23.4 |  |  |  | SOUTH2001 | HARRIS | -0.00080045 | 0.0025607 | -0.018731 | 0.05992 |  | 138
_HG | _HG | 40800 | HARRIS 9 | 45.8 |  |  |  | SOUTH2001 | HARRIS | -0.00063514 | 0.0020373 | -0.02909 | 0.09331 |  | 69
_HL | _HL | 40811 | HILAND98 | 20.5 |  |  |  | SOUTH2001 | HARRIS | -0.00085162 | 0.0027271 | -0.017458 | 0.055906 |  | 138
_HL | _HL | 40812 | HILAND98 | 25.1 |  |  |  | SOUTH2001 | HARRIS | -0.00080685 | 0.0025855 | -0.020252 | 0.064897 |  | 69
|  | 40815 | CUST_3 | 13.5 |  |  |  | SOUTH2001 | HARRIS | -0.00074323 | 0.00239 | -0.010034 | 0.032265 |  | 138
_HB | _HB | 40830 | HUMBLE 8 | 182 |  |  |  | SOUTH2001 | HARRIS | -0.0010662 | 0.0033209 | -0.19405 | 0.6044 |  | 138
IND | IND | 40841 | INDUST98 | 10.2 |  |  |  | SOUTH2001 | HARRIS | -0.0007696 | 0.002475 | -0.0078499 | 0.025245 |  | 138
IND | IND | 40842 | INDUST98 | 9.6 |  |  |  | SOUTH2001 | HARRIS | -0.00077629 | 0.0025034 | -0.0074524 | 0.024032 |  | 69
_JP | _JP | 40860 | JACNTO 8 | 25.5 |  |  |  | SOUTH2001 | HARRIS | -0.00075385 | 0.0024244 | -0.019223 | 0.061821 |  | 138
KNY | KNY | 40870 | KENNY_ | 28.3 |  |  |  | SOUTH2001 | CHAMBERS | -0.00074032 | 0.0023914 | -0.020951 | 0.067677 |  | 138
_KG | _KG | 40900 | KING 5 |  |  |  |  | SOUTH2001 | HARRIS | -0.0014108 | 0.0047448 | 0 | 0 |  | 345
_KW | _KW | 40930 | KINGWD 8 | 141.1 |  |  |  | SOUTH2001 | HARRIS | -0.0010115 | 0.0031655 | -0.14272 | 0.44666 |  | 138
_LP | _LP | 40941 | LAPORT 8 | 26.1 |  |  |  | SOUTH2001 | HARRIS | -0.0006449 | 0.0020719 | -0.016832 | 0.054077 |  | 138
_LP | _LP | 40942 | LAPORT 8 | 24.8 |  |  |  | SOUTH2001 | HARRIS | -0.00063775 | 0.0020486 | -0.015816 | 0.050805 |  | 138
_LB | _LB | 40961 | LIBRTY 8 | 31 |  |  |  | SOUTH2001 | HARRIS | -0.00082569 | 0.002633 | -0.025597 | 0.081622 |  | 138
_LB | _LB | 40962 | LIBRTY 8 | 21.6 |  |  |  | SOUTH2001 | HARRIS | -0.00084537 | 0.0027057 | -0.01826 | 0.058443 |  | 138
|  | 40970 | LPEENY |  |  |  |  | SOUTH2001 | HARRIS | -0.00070176 | 0.0022629 | 0 | 0 |  | 138
_LZ | _LZ | 40980 | LUBZOL | 12.3 |  |  |  | SOUTH2001 | HARRIS | -0.0006903 | 0.0022219 | -0.0084907 | 0.02733 |  | 138
LHM | LHM | 40990 | LYCHEM | 62.1 |  |  |  | SOUTH2001 | HARRIS | -0.00087792 | 0.0028256 | -0.054519 | 0.17547 | 21 | 138
LYD | LYD | 41000 | LYDELL | 109.7 |  |  |  | SOUTH2001 | HARRIS | -0.00078901 | 0.0025527 | -0.086555 | 0.28003 |  | 138
_LH | _LH | 41010 | LYNCH_ | 8 |  |  |  | SOUTH2001 | HARRIS | -0.00077826 | 0.0025062 | -0.0062261 | 0.02005 |  | 138
_LY | _LY | 41021 | LYONDL 8 | 15.5 |  |  |  | SOUTH2001 | HARRIS | -0.0008883 | 0.0028544 | -0.013769 | 0.044243 |  | 138
_LY | _LY | 41022 | LYONDL 8 | 14.2 |  |  |  | SOUTH2001 | HARRIS | -0.00088109 | 0.0028415 | -0.012511 | 0.04035 |  | 138
_MD | _MD | 41040 | MCDONO | 10.6 |  |  |  | SOUTH2001 | HARRIS | -0.00066788 | 0.0021389 | -0.0070795 | 0.022672 |  | 69
MTL | MTL | 41050 | METALS | 2.5 |  |  |  | SOUTH2001 | HARRIS | -0.00091656 | 0.0029211 | -0.0022914 | 0.0073029 |  | 138
MIN | MIN | 41061 | MINING | 12.7 |  |  |  | SOUTH2001 | HARRIS | -0.00064639 | 0.0020779 | -0.0082092 | 0.026389 |  | 69
MOC | MOC | 41080 | MOCHEM | 12.3 |  |  |  | SOUTH2001 | HARRIS | -0.00063044 | 0.0020227 | -0.0077544 | 0.02488 |  | 69
MNT | MNT | 41090 | MOMENT | 59.9 |  |  |  | SOUTH2001 | HARRIS | -0.00068341 | 0.0021979 | -0.040936 | 0.13165 |  | 138
MRN | MRN | 41100 | MORGPT 8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00065635 | 0.0021093 | 0 | 0 |  | 138
_MB | _MB | 41111 | MT_BEL 8 | 10 |  |  |  | SOUTH2001 | CHAMBERS | -0.00077597 | 0.0024994 | -0.0077597 | 0.024994 |  | 138
_MB | _MB | 41112 | MT_BEL 9 | 25 |  |  |  | SOUTH2001 | CHAMBERS | -0.0007909 | 0.002541 | -0.019773 | 0.063526 |  | 69
_MB | _MB | 41120 | MT_BEL 9 | 15 |  |  |  | SOUTH2001 | CHAMBERS | -0.00079092 | 0.0025411 | -0.011864 | 0.038116 |  | 69
NDL | NDL | 41140 | NEEDLE | 4.7 |  |  |  | SOUTH2001 | HARRIS | -0.00079558 | 0.0025541 | -0.0037392 | 0.012004 |  | 69
_NP | _NP | 41150 | NEWPRT 8 | 31.4 |  |  |  | SOUTH2001 | HARRIS | -0.00082422 | 0.0026108 | -0.025881 | 0.081979 |  | 138
NTH | NTH | 41160 | NINTH_ | 10.9 |  |  |  | SOUTH2001 | HARRIS | -0.00067917 | 0.0021825 | -0.007403 | 0.02379 |  | 138
|  | 41165 | NOBEL 8 | 2 |  |  |  | SOUTH2001 | HARRIS | -0.00069273 | 0.0022281 | -0.0013855 | 0.0044562 |  | 138
_NM | _NM | 41171 | NORMDY 8 | 25.2 |  |  |  | SOUTH2001 | HARRIS | -0.00080463 | 0.0026066 | -0.020277 | 0.065686 |  | 138
_NM | _NM | 41172 | NORMDY 8 | 18 |  |  |  | SOUTH2001 | HARRIS | -0.00078229 | 0.0025316 | -0.014081 | 0.045568 |  | 138
_OA | _OA | 41191 | OATES 98 | 18 |  |  |  | SOUTH2001 | HARRIS | -0.00079301 | 0.0025662 | -0.014274 | 0.046192 |  | 138
_OA | _OA | 41192 | OATES 98 | 26.5 |  |  |  | SOUTH2001 | HARRIS | -0.00072479 | 0.0023305 | -0.019207 | 0.06176 |  | 69
ORION | ORION | 41205 | ORION_ | 6.7 |  |  |  | SOUTH2001 | HARRIS | -0.00061576 | 0.0019769 | -0.0041256 | 0.013245 |  | 138
PIR | PIR | 41210 | PAIR__ | 64.4 |  |  |  | SOUTH2001 | HARRIS | -0.0007012 | 0.0022606 | -0.045158 | 0.14558 |  | 138
_PW | _PW | 41221 | PARKWY 8 | 22.8 |  |  |  | SOUTH2001 | HARRIS | -0.00094568 | 0.0030388 | -0.021562 | 0.069285 |  | 138
_PW | _PW | 41222 | PARKWY 8 | 24.8 |  |  |  | SOUTH2001 | HARRIS | -0.00096025 | 0.0030853 | -0.023814 | 0.076515 |  | 138
PSG | PSG | 41240 | PASGEN |  |  |  |  | SOUTH2001 | HARRIS | -0.00067984 | 0.0021898 | 0 | 0 |  | 138
PL | PL | 41250 | PHILIP | 3.2 |  |  |  | SOUTH2001 | HARRIS | -0.00067995 | 0.0021895 | -0.0021758 | 0.0070064 | 8 | 138
PRT | PRT | 41260 | PORT__ | 10 |  |  |  | SOUTH2001 | HARRIS | -0.00076925 | 0.0024739 | -0.0076925 | 0.024739 |  | 138
PSA | PSA | 41300 | PSARCO | 0 |  |  |  | SOUTH2001 | HARRIS | -0.00087467 | 0.0028093 | 0 | 0 | 9 | 138
QAB | QAB | 41310 | QUANAB | 47.8 |  |  |  | SOUTH2001 | HARRIS | -0.00064484 | 0.0020727 | -0.030823 | 0.099074 |  | 138
QAL | QAL | 41320 | QUANAL | 12.1 |  |  |  | SOUTH2001 | HARRIS | -0.0006639 | 0.002135 | -0.0080332 | 0.025833 |  | 69
QNM | QNM | 41330 | QUANUM | 25.7 |  |  |  | SOUTH2001 | HARRIS | -0.00070667 | 0.0022794 | -0.018161 | 0.058582 | 10 | 138
_RD | _RD | 41340 | REED__ | 5.3 |  |  |  | SOUTH2001 | HARRIS | -0.0006677 | 0.0021383 | -0.0035388 | 0.011333 |  | 69
_RH | _RH | 41350 | ROHMAS | 63.7 |  |  |  | SOUTH2001 | HARRIS | -0.00070285 | 0.0022661 | -0.044772 | 0.14435 |  | 138
ROL | ROL | 41360 | ROLLEN | 4.6 |  |  |  | SOUTH2001 | HARRIS | -0.00069574 | 0.0022385 | -0.0032004 | 0.010297 |  | 138
_SC | _SC | 41370 | S_CHAN 8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00068264 | 0.0021986 | 0 | 0 |  | 138
_SC | _SC | 41380 | S_CHAN 9 |  |  |  |  | SOUTH2001 | HARRIS | -0.00065826 | 0.0021173 | 0 | 0 |  | 69
_SC | _SC | 41390 | CS_CHAN8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00068254 | 0.0021983 | 0 | 0 |  | 138
SRB | SRB | 41400 | S_R_B_E8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00067135 | 0.0021591 | 0 | 0 |  | 138
SRB | SRB | 41405 | S_R_B_W8 |  |  |  |  | SOUTH2001 | HARRIS | -0.0007008 | 0.0022538 | 0 | 0 |  | 138
SRB | SRB | 41410 | S_R_B_E9 |  |  |  |  | SOUTH2001 | HARRIS | -0.00066491 | 0.0021381 | 0 | 0 |  | 69
SRB | SRB | 41415 | S_R_B_W9 |  |  |  |  | SOUTH2001 | HARRIS | -0.00066279 | 0.0021311 | 0 | 0 |  | 69
SRB | SRB | 41420 | SRB MID |  |  |  |  | SOUTH2001 | HARRIS | -0.00066141 | 0.0021266 | 0 | 0 |  | 0
|  | 41430 | SHELDN 5 |  |  |  |  | SOUTH2001 | HARRIS | -0.0013358 | 0.0044753 | 0 | 0 |  | 345
_SL | _SL | 41450 | SHELL_ | 7.5 |  |  |  | SOUTH2001 | HARRIS | -0.00068972 | 0.0022224 | -0.0051729 | 0.016668 | 11 | 138
SIM | SIM | 41460 | SIMSON | 17.5 |  |  |  | SOUTH2001 | HARRIS | -0.00062362 | 0.0020022 | -0.010913 | 0.035039 | 12 | 69
SOL | SOL | 41480 | SOLMER | 57.6 |  |  |  | SOUTH2001 | HARRIS | -0.00068052 | 0.0021886 | -0.039198 | 0.12606 |  | 138
STA | STA | 41490 | STATE_ | 11.5 |  |  |  | SOUTH2001 | HARRIS | -0.00069107 | 0.0022228 | -0.0079473 | 0.025562 |  | 138
RNG | RNG | 41500 | STRANG | 112.5 |  |  |  | SOUTH2001 | HARRIS | -0.00069171 | 0.0022281 | -0.077818 | 0.25066 |  | 138
_SB | _SB | 41510 | STRAW T8 | 67.6 |  |  |  | SOUTH2001 | HARRIS | -0.00076265 | 0.0024539 | -0.051555 | 0.16588 |  | 138
SLV | SLV | 41520 | SYLVAN | 2.1 |  |  |  | SOUTH2001 | HARRIS | -0.00063237 | 0.0020311 | -0.001328 | 0.0042652 |  | 138
|  | 41530 | TAYLOR8 | 10 |  |  |  | SOUTH2001 | HARRIS | -0.00076712 | 0.002467 | -0.0076712 | 0.02467 |  | 138
_TX | _TX | 41550 | TEXAS_ | 2.3 |  |  |  | SOUTH2001 | HARRIS | -0.00080683 | 0.0025855 | -0.0018557 | 0.0059467 |  | 69
_PR | _PR | 41560 | TEXPET | 2 |  |  |  | SOUTH2001 | HARRIS | -0.00063117 | 0.002025 | -0.0012623 | 0.00405 | 13 | 69
_TS | _TS | 41570 | TEXWAL | 0.4 |  |  |  | SOUTH2001 | BRAZORIA | -0.00072925 | 0.002347 | -0.0002917 | 0.0009388 |  | 69
TID | TID | 41580 | TIDAL_ | 35 |  |  |  | SOUTH2001 | HARRIS | -0.00069098 | 0.002224 | -0.024184 | 0.07784 | 14 | 138
TRV | TRV | 41590 | TRAVIS | 42.6 |  |  |  | SOUTH2001 | HARRIS | -0.00068545 | 0.0022072 | -0.0292 | 0.094026 |  | 138
TRI | TRI | 41600 | TRIBAY | 12.5 |  |  |  | SOUTH2001 | HARRIS | -0.00063068 | 0.0020256 | -0.0078835 | 0.025319 |  | 138
TRM | TRM | 41610 | TRINTY 8 | 8.3 |  |  |  | SOUTH2001 | CHAMBERS | -0.00073646 | 0.0023788 | -0.0061126 | 0.019744 |  | 138
TKR | TKR | 41620 | TUCKER | 7.9 |  |  |  | SOUTH2001 | HARRIS | -0.00069497 | 0.0022361 | -0.0054902 | 0.017665 |  | 138
_UW | _UW | 41631 | UNDRWD 8 | 21.8 |  |  |  | SOUTH2001 | HARRIS | -0.00059944 | 0.0019247 | -0.013068 | 0.041959 |  | 138
_UW | _UW | 41632 | UNDRWD 8 | 13 |  |  |  | SOUTH2001 | HARRIS | -0.00070752 | 0.0022759 | -0.0091977 | 0.029586 |  | 138
_UV | _UV | 41651 | UVALDE 8 | 32.4 |  |  |  | SOUTH2001 | HARRIS | -0.00088658 | 0.0028692 | -0.028725 | 0.092962 |  | 138
_UV | _UV | 41652 | UVALDE 8 | 27.1 |  |  |  | SOUTH2001 | HARRIS | -0.00091621 | 0.0029468 | -0.024829 | 0.079858 |  | 138
WAS | WAS | 41670 | WABURN | 4.7 |  |  |  | SOUTH2001 | HARRIS | -0.00075681 | 0.0024335 | -0.003557 | 0.011437 |  | 138
_WV | _WV | 41681 | WALSVL 9 | 4.4 |  |  |  | SOUTH2001 | HARRIS | -0.00072925 | 0.002347 | -0.0032087 | 0.010327 |  | 69
_WV | _WV | 41682 | WALSVL 9 | 16.6 |  |  |  | SOUTH2001 | HARRIS | -0.00068769 | 0.002205 | -0.011416 | 0.036603 |  | 69
WRN | WRN | 41700 | WARVUE | 5.1 |  |  |  | SOUTH2001 | CHAMBERS | -0.00077527 | 0.0024974 | -0.0039539 | 0.012737 |  | 138
_WE | _WE | 41711 | WITTER 8 | 21.8 |  |  |  | SOUTH2001 | HARRIS | -0.00048575 | 0.00155 | -0.010589 | 0.03379 |  | 138
_WE | _WE | 41712 | WITTER 8 | 25.9 |  |  |  | SOUTH2001 | HARRIS | -0.00078793 | 0.0025355 | -0.020407 | 0.065671 |  | 138
PHR | PHR | 42000 | P_H_R_ 5 |  |  |  |  | SOUTH2001 | GALVESTON | 0.00010286 | -0.00032331 | 0 | 0 |  | 345
PHR | PHR | 42010 | P_H_R_N8 |  |  |  |  | SOUTH2001 | GALVESTON | -0.00057387 | 0.0018397 | 0 | 0 |  | 138
PHR | PHR | 42015 | P_H_R_S8 |  |  |  |  | SOUTH2001 | GALVESTON | 3.8e-14 | 4.8e-14 | 0 | 0 |  | 138
PHR | PHR | 42020 | P_H_R_ 8 | 12.6 |  |  |  | SOUTH2001 | GALVESTON | -0.00057387 | 0.0018397 | -0.0072307 | 0.02318 |  | 138
_AM | _AM | 42041 | ALMEDA 8 | 9.1 |  |  |  | SOUTH2001 | HARRIS | -0.00010818 | 0.00027704 | -0.0009844 | 0.0025211 |  | 138
_AM | _AM | 42042 | ALMEDA 8 | 18.2 |  |  |  | SOUTH2001 | HARRIS | -0.00041648 | 0.0013227 | -0.00758 | 0.024073 |  | 138
_AL | _AL | 42061 | ALTA_L98 | 19.5 |  |  |  | SOUTH2001 | GALVESTON | -5.8412e-05 | 0.00018203 | -0.001139 | 0.0035497 |  | 138
_AL | _AL | 42062 | ALTA_L98 | 22 |  |  |  | SOUTH2001 | GALVESTON | -8.819e-05 | 0.00024589 | -0.0019402 | 0.0054096 |  | 69
_AV | _AV | 42080 | ALVIN 9 | 11 |  |  |  | SOUTH2001 | BRAZORIA | -3.2209e-05 | 4.7489e-05 | -0.0003543 | 0.00052238 |  | 69
_AK | _AK | 42090 | AMKOE_ | 40.2 |  |  |  | SOUTH2001 | BRAZORIA | 0.00050641 | -0.0016389 | 0.020358 | -0.065885 | 15 | 138
AMP | AMP | 42100 | AMPORT | 9.8 |  |  |  | SOUTH2001 | BRAZORIA | 0.0019361 | -0.0062009 | 0.018974 | -0.060768 |  | 138
_AE | _AE | 42110 | ANGLTN 8 | 7.6 |  |  |  | SOUTH2001 | BRAZORIA | 0.0012433 | -0.0040058 | 0.0094487 | -0.030444 |  | 138
ARM | ARM | 42120 | ARMAND | 6.5 |  |  |  | SOUTH2001 | HARRIS | -0.0005365 | 0.0017194 | -0.0034873 | 0.011176 |  | 138
_AA | _AA | 42130 | AVAUTO 8 |  |  |  |  | SOUTH2001 | BRAZORIA | -0.00014807 | 0.00043811 | 0 | 0 |  | 138
_AA | _AA | 42140 | AVAUTO 9 |  |  |  |  | SOUTH2001 | BRAZORIA | -6.3719e-05 | 0.00015409 | 0 | 0 |  | 69
BSF | BSF | 42150 | BASF__ | 30 |  |  |  | SOUTH2001 | BRAZORIA | 0.0018937 | -0.0060621 | 0.056812 | -0.18186 | 16 | 138
BYU | BYU | 42160 | BAYOU_ |  |  |  |  | SOUTH2001 | HARRIS | -0.0006117 | 0.0019637 | 0 | 0 |  | 138
_BW | _BW | 42170 | BAYWAY 8 | 67.7 |  |  |  | SOUTH2001 | HARRIS | -0.00056906 | 0.001825 | -0.038525 | 0.12355 |  | 138
BBP | BBP | 42180 | BIGBAY | 59.2 |  |  |  | SOUTH2001 | HARRIS | -0.0006096 | 0.0019569 | -0.036088 | 0.11585 |  | 138
BFP | BFP | 42190 | BIPORT | 31.9 |  |  |  | SOUTH2001 | BRAZORIA | 0.0019465 | -0.0062337 | 0.062093 | -0.19885 |  | 138
BYN | BYN | 42200 | BRYAN_ | 5.2 |  |  |  | SOUTH2001 | HARRIS | 0.0019562 | -0.0062728 | 0.010172 | -0.032619 |  | 69
_BZ | _BZ | 42210 | BRZPRT 8 | 52 |  |  |  | SOUTH2001 | BRAZORIA | 0.0019346 | -0.0061929 | 0.1006 | -0.32203 |  | 138
BYR | BYR | 42220 | BYPARK | 13 |  |  |  | SOUTH2001 | HARRIS | -0.00054683 | 0.0017529 | -0.0071088 | 0.022788 |  | 138
CTL | CTL | 42230 | CAPTOL | 0 |  |  |  | SOUTH2001 | HARRIS | -0.00055864 | 0.0017912 | 0 | 0 | 17 | 138
_CA | _CA | 42241 | CARDIF 8 | 38.2 |  |  |  | SOUTH2001 | HARRIS | -0.00067493 | 0.0021677 | -0.025782 | 0.082807 |  | 138
_CA | _CA | 42242 | CARDIF 8 | 10.9 |  |  |  | SOUTH2001 | HARRIS | -0.00066369 | 0.0021312 | -0.0072342 | 0.02323 |  | 138
_CN | _CN | 42260 | CELNEC | 0.1 |  |  |  | SOUTH2001 | HARRIS | -0.00055889 | 0.001792 | -5.5889e-05 | 0.0001792 |  | 138
_CC | _CC | 42271 | CHOC_B 8 | 18 |  |  |  | SOUTH2001 | HARRIS | -0.00010913 | 0.00028023 | -0.0019644 | 0.0050441 |  | 138
_CC | _CC | 42272 | CHOC_B 8 | 14.9 |  |  |  | SOUTH2001 | HARRIS | -0.00041696 | 0.0013242 | -0.0062127 | 0.019731 |  | 138
_CK | _CK | 42291 | CLEAR 8 | 25.3 |  |  |  | SOUTH2001 | HARRIS | -0.00063623 | 0.0020421 | -0.016097 | 0.051665 |  | 138
_CK | _CK | 42292 | CLEAR 8 | 25.5 |  |  |  | SOUTH2001 | HARRIS | -0.00052946 | 0.0016965 | -0.013501 | 0.04326 |  | 138
_CG | _CG | 42311 | COLEGE 8 | 23.6 |  |  |  | SOUTH2001 | HARRIS | -0.00046884 | 0.0014931 | -0.011065 | 0.035236 |  | 138
_CG | _CG | 42312 | COLEGE 8 | 27.1 |  |  |  | SOUTH2001 | HARRIS | -0.00059334 | 0.0019037 | -0.016079 | 0.05159 |  | 138
_WC | _WC | 42330 | CW_COL_8 |  |  |  |  | SOUTH2001 | BRAZORIA | 0.0014883 | -0.0047633 | 0 | 0 |  | 138
_DA | _DA | 42340 | DAMON 9 | 7.3 |  |  |  | SOUTH2001 | BRAZORIA | 0.0011961 | -0.0040556 | 0.0087314 | -0.029606 |  | 69
DOW | DOW | 42500 | DOW345 5 |  |  |  |  | SOUTH2001 | BRAZORIA | 0.0023985 | -0.007713 | 0 | 0 |  | 345
DOW | DOW | 42510 | DOW138 8 |  |  |  |  | SOUTH2001 | BRAZORIA | 0.0020377 | -0.006525 | 0 | 0 |  | 138
DOW | DOW | 42515 | DOW_A_ | 235.6 |  |  |  | SOUTH2001 | BRAZORIA | 0.0023985 | -0.007713 | 0.56509 | -1.8172 |  | 138
|  | 42520 | DOW_B 8 | 0 |  |  |  | SOUTH2001 | BRAZORIA | 0.0023985 | -0.007713 | 0 | 0 | 18 | 138
|  | 42525 | DOW_E 8 | 0 |  |  |  | SOUTH2001 | BRAZORIA | 0.0023985 | -0.007713 | 0 | 0 | 19 | 138
_DR | _DR | 42550 | DROUET 8 | 70.6 |  |  |  | SOUTH2001 | HARRIS | -0.00048942 | 0.0015601 | -0.034553 | 0.11014 |  | 138
_ED | _ED | 42561 | ELDORA 8 | 31 |  |  |  | SOUTH2001 | HARRIS | -0.00018902 | 0.00059901 | -0.0058597 | 0.018569 |  | 138
_ED | _ED | 42562 | ELDORA 8 | 30.8 |  |  |  | SOUTH2001 | HARRIS | -0.00051779 | 0.0016541 | -0.015948 | 0.050946 |  | 138
_EL | _EL | 42581 | ELLING 9 | 26.2 |  |  |  | SOUTH2001 | HARRIS | -0.00021372 | 0.0006741 | -0.0055994 | 0.017661 |  | 69
_EL | _EL | 42582 | ELLING 9 | 18.9 |  |  |  | SOUTH2001 | HARRIS | -0.00038318 | 0.0012231 | -0.0072422 | 0.023117 |  | 69
EXW | EXW | 42600 | EXTER_ | 1.1 |  |  |  | SOUTH2001 | HARRIS | -0.00020064 | 0.00063038 | -0.00022071 | 0.00069342 |  | 69
_FT | _FT | 42610 | FAIRMT28 |  |  |  |  | SOUTH2001 | HARRIS | -0.00052408 | 0.0016791 | 0 | 0 |  | 138
_FT | _FT | 42611 | FAIRMT 8 | 7.8 |  |  |  | SOUTH2001 | HARRIS | -0.0006457 | 0.0020728 | -0.0050365 | 0.016168 |  | 138
_FT | _FT | 42612 | FAIRMT 8 | 47 |  |  |  | SOUTH2001 | HARRIS | -0.00052408 | 0.0016791 | -0.024632 | 0.07892 |  | 138
_FP | _FP | 42640 | FREEPT 9 | 21.6 |  |  |  | SOUTH2001 | BRAZORIA | 0.0019562 | -0.0062728 | 0.042254 | -0.13549 |  | 69
_FW | _FW | 42651 | FRIEND 8 | 25.8 |  |  |  | SOUTH2001 | HARRIS | -0.0001655 | 0.00051557 | -0.0042699 | 0.013302 |  | 138
_FW | _FW | 42652 | FRIEND 8 | 15.6 |  |  |  | SOUTH2001 | HARRIS | -0.00010517 | 0.00032556 | -0.0016406 | 0.0050787 |  | 138
_GL | _GL | 42670 | GALVES 8 | 80.8 |  |  |  | SOUTH2001 | GALVESTON | -0.00012447 | 0.00038816 | -0.010057 | 0.031363 |  | 138
_GV | _GV | 42680 | GARDEN 8 | 4.5 |  |  |  | SOUTH2001 | HARRIS | -0.00045233 | 0.0014374 | -0.0020355 | 0.0064685 |  | 138
_GV | _GV | 42690 | GARDEN 9 | 38.4 |  |  |  | SOUTH2001 | HARRIS | -0.00046109 | 0.0014583 | -0.017706 | 0.055998 |  | 69
_GV | _GV | 42700 | CGARDEN8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00045186 | 0.0014359 | 0 | 0 |  | 138
|  | 42705 | CUST_4 8 | 7 |  |  |  | SOUTH2001 | HARRIS | -0.00056775 | 0.0018208 | -0.0039743 | 0.012746 |  | 138
GNO | GNO | 42711 | GENOA_ |  |  |  |  | SOUTH2001 | HARRIS | -0.00063635 | 0.0020425 | 0 | 0 |  | 138
GNO | GNO | 42712 | GENOA_ | 7.3 |  |  |  | SOUTH2001 | HARRIS | -0.00052937 | 0.0016962 | -0.0038644 | 0.012382 |  | 138
_GM | _GM | 42730 | GULFCM | 0.1 |  |  |  | SOUTH2001 | GALVESTON | -0.00012709 | 0.00038443 | -1.2709e-05 | 3.8443e-05 |  | 69
_GG | _GG | 42741 | GULFGT 8 | 15.9 |  |  |  | SOUTH2001 | HARRIS | -0.00049041 | 0.0015541 | -0.0077976 | 0.02471 |  | 138
_GG | _GG | 42742 | GULFGT 8 | 59.1 |  |  |  | SOUTH2001 | HARRIS | -0.00024329 | 0.0007565 | -0.014379 | 0.044709 |  | 138
_HA | _HA | 42761 | HALL 8 | 33.8 |  |  |  | SOUTH2001 | HARRIS | -0.00016176 | 0.00050298 | -0.0054675 | 0.017001 |  | 138
_HA | _HA | 42762 | HALL 8 | 19.5 |  |  |  | SOUTH2001 | HARRIS | -0.00029365 | 0.00093057 | -0.0057262 | 0.018146 |  | 138
HAN | HAN | 42780 | HANNA | 10 |  |  |  | SOUTH2001 | HARRIS | -0.00057073 | 0.0018301 | -0.0057073 | 0.018301 |  | 138
HIM | HIM | 42790 | HIMONT | 21.8 |  |  |  | SOUTH2001 | HARRIS | -0.0005528 | 0.0017723 | -0.012051 | 0.038636 |  | 138
_HX | _HX | 42800 | HITCOK 8 | 10.6 |  |  |  | SOUTH2001 | GALVESTON | -7.4488e-05 | 0.00023213 | -0.00078957 | 0.0024606 |  | 138
_HN | _HN | 42810 | HOFMAN | 4.7 |  |  |  | SOUTH2001 | BRAZORIA | 0.0018312 | -0.0058617 | 0.0086066 | -0.02755 |  | 138
HSS | HSS | 42820 | HS_TAP69 |  |  |  |  | SOUTH2001 | BRAZORIA | -3.9868e-05 | 7.3782e-05 | 0 | 0 |  | 69
HUN | HUN | 42830 | HUNTER | 35.3 |  |  |  | SOUTH2001 | HARRIS | -0.00057018 | 0.0018284 | -0.020127 | 0.064543 |  | 138
|  | 42835 | JONES 8 | 4.5 |  |  |  | SOUTH2001 | BRAZORIA | 0.0021174 | -0.0067214 | 0.0095283 | -0.030246 |  | 138
_KM | _KM | 42841 | KEMAH 8 | 31.9 |  |  |  | SOUTH2001 | GALVESTON | -0.00058998 | 0.001892 | -0.01882 | 0.060354 |  | 138
_KM | _KM | 42842 | KEMAH 8 | 32.2 |  |  |  | SOUTH2001 | GALVESTON | -0.00055592 | 0.0017803 | -0.017901 | 0.057324 |  | 138
_LM | _LM | 42860 | LAMARQ 9 | 10.5 |  |  |  | SOUTH2001 | GALVESTON | -0.00012709 | 0.00038443 | -0.0013344 | 0.0040365 |  | 69
_LV | _LV | 42870 | LIVRPL 8 | 9.8 |  |  |  | SOUTH2001 | BRAZORIA | 0.00085919 | -0.0027721 | 0.00842 | -0.027167 |  | 138
_LJ | _LJ | 42880 | LKJACK 8 | 65.9 |  |  |  | SOUTH2001 | BRAZORIA | 0.001731 | -0.0055407 | 0.11407 | -0.36513 |  | 138
LOM | LOM | 42890 | LOMAX_ | 31.5 |  |  |  | SOUTH2001 | HARRIS | -0.00054429 | 0.0017447 | -0.017145 | 0.054958 |  | 138
LZB | LZB | 42900 | LUZBAY | 4.4 |  |  |  | SOUTH2001 | HARRIS | -0.00055017 | 0.0017638 | -0.0024208 | 0.0077605 |  | 138
LYP | LYP | 42910 | LYNPOL | 7 |  |  |  | SOUTH2001 | HARRIS | -0.00053533 | 0.0017156 | -0.0037473 | 0.012009 |  | 138
_MY | _MY | 42921 | MARYCK 8 | 23.2 |  |  |  | SOUTH2001 | BRAZORIA | -0.00016206 | 0.00050392 | -0.0037599 | 0.011691 |  | 138
_MY | _MY | 42922 | MARYCK 8 | 24 |  |  |  | SOUTH2001 | BRAZORIA | -0.0002942 | 0.00093232 | -0.0070609 | 0.022376 |  | 138
MSN | MSN | 42940 | MONSAN | 65.4 |  |  |  | SOUTH2001 | BRAZORIA | 0.0006405 | -0.0020697 | 0.041889 | -0.13536 | 20 | 138
MDY | MDY | 42950 | MOODY 8 | 18 |  |  |  | SOUTH2001 | GALVESTON | -0.0001264 | 0.00039436 | -0.0022753 | 0.0070984 |  | 138
|  | 42951 | TERM_A 8 |  |  |  |  | SOUTH2001 | GALVESTON | -0.00012648 | 0.00039461 | 0 | 0 |  | 138
|  | 42952 | OPN@T_A8 |  |  |  |  | SOUTH2001 | GALVESTON | -0.00012681 | 0.00039566 | 0 | 0 |  | 138
|  | 42953 | TERM_B 8 |  |  |  |  | SOUTH2001 | GALVESTON | -0.00012681 | 0.00039566 | 0 | 0 |  | 138
_MU | _MU | 42960 | MUSTNG 8 | 13.9 |  |  |  | SOUTH2001 | BRAZORIA | 0.00022441 | -0.0007331 | 0.0031193 | -0.01019 |  | 138
_NA | _NA | 42970 | NASA__ | 24.1 |  |  |  | SOUTH2001 | HARRIS | -0.00032443 | 0.0010334 | -0.0078188 | 0.024904 |  | 138
NSH | NSH | 42981 | NASH 98 | 1.1 |  |  |  | SOUTH2001 | BRAZORIA | 0.0010922 | -0.0035452 | 0.0012014 | -0.0038997 |  | 138
NSH | NSH | 42982 | NASH 98 | 4.7 |  |  |  | SOUTH2001 | BRAZORIA | 0.0012866 | -0.0042982 | 0.0060469 | -0.020201 |  | 69
_NV | _NV | 43000 | NEEDVL 9 | 19.1 |  |  |  | SOUTH2001 | FORT BEND | 0.0009339 | -0.0033527 | 0.017837 | -0.064037 |  | 69
NEW | NEW | 43011 | NEWGLF 8 | 0.9 |  |  |  | SOUTH2001 | WHARTON | 0.0031088 | -0.0096353 | 0.002798 | -0.0086718 |  | 138
NEW | NEW | 43012 | NEWGLF 8 | 5.9 |  |  |  | SOUTH2001 | WHARTON | 0.0036091 | -0.011139 | 0.021293 | -0.065721 |  | 138
_PA | _PA | 43040 | PASDNA 8 | 68 |  |  |  | SOUTH2001 | HARRIS | -0.0005919 | 0.001899 | -0.040249 | 0.12913 |  | 138
_PE | _PE | 43051 | PEARLD 8 | 24.8 |  |  |  | SOUTH2001 | BRAZORIA | -0.00021005 | 0.00065314 | -0.0052094 | 0.016198 |  | 138
_PE | _PE | 43052 | PEARLD 8 | 13.9 |  |  |  | SOUTH2001 | BRAZORIA | -0.00038142 | 0.0012087 | -0.0053017 | 0.016801 |  | 138
PET | PET | 43070 | PETSON | 20.3 |  |  |  | SOUTH2001 | BRAZORIA | 0.00067452 | -0.0021789 | 0.013693 | -0.044232 |  | 138
_PJ | _PJ | 43081 | PILGRM 8 | 21.3 |  |  |  | SOUTH2001 | HARRIS | -0.00011189 | 0.0003479 | -0.0023832 | 0.0074102 |  | 138
_PJ | _PJ | 43082 | PILGRM 8 | 11.2 |  |  |  | SOUTH2001 | HARRIS | -0.00023433 | 0.00073969 | -0.0026245 | 0.0082845 |  | 138
PO | PO | 43101 | PLARIS 8 | 42.1 |  |  |  | SOUTH2001 | HARRIS | -0.00062107 | 0.0019929 | -0.026147 | 0.083901 |  | 138
PO | PO | 43102 | PLARIS 8 | 43.5 |  |  |  | SOUTH2001 | HARRIS | -0.00053784 | 0.0017235 | -0.023396 | 0.074972 |  | 138
_PG | _PG | 43120 | PLEDGR 8 | 0.9 |  |  |  | SOUTH2001 | MATAGORDA | 0.0025711 | -0.0080187 | 0.002314 | -0.0072168 |  | 138
PWL | PWL | 43130 | POWELL | 6.8 |  |  |  | SOUTH2001 | HARRIS | -0.00059906 | 0.0019226 | -0.0040736 | 0.013074 |  | 138
_RT | _RT | 43140 | RETREV 9 | 4.8 |  |  |  | SOUTH2001 | BRAZORIA | 0.0016981 | -0.0054898 | 0.008151 | -0.026351 |  | 69
RIC | RIC | 43150 | RIWOOD | 2.1 |  |  |  | SOUTH2001 | BRAZORIA | 0.0017644 | -0.0056568 | 0.0037052 | -0.011879 |  | 138
_SH | _SH | 43170 | S_HOUS 9 | 48.2 |  |  |  | SOUTH2001 | HARRIS | -0.00048685 | 0.001559 | -0.023466 | 0.075142 |  | 69
_SH | _SH | 43171 | S_HOUS98 |  |  |  |  | SOUTH2001 | HARRIS | -0.000487 | 0.0015595 | 0 | 0 |  | 69
_SH | _SH | 43172 | S_HOUS98 | 27.6 |  |  |  | SOUTH2001 | HARRIS | -0.00050209 | 0.0016021 | -0.013858 | 0.044218 |  | 138
_LC | _LC | 43190 | S_LANE 8 | 2.5 |  |  |  | SOUTH2001 | WHARTON | 0.0040563 | -0.012484 | 0.010141 | -0.031209 |  | 138
SCW | SCW | 43201 | SEAWAL 8 | 20.5 |  |  |  | SOUTH2001 | GALVESTON | -0.00012447 | 0.00038816 | -0.0025516 | 0.0079572 |  | 138
SCW | SCW | 43202 | SEAWAL 8 | 20.3 |  |  |  | SOUTH2001 | GALVESTON | -0.00012447 | 0.00038816 | -0.0025267 | 0.0078796 |  | 138
_SI | _SI | 43220 | SEAWAY | 0.9 |  |  |  | SOUTH2001 | BRAZORIA | 0.0021194 | -0.0067267 | 0.0019075 | -0.006054 |  | 138
|  | 43225 | SEPTON 8 | 3.84 |  |  |  | SOUTH2001 | HARRIS | -0.00058742 | 0.0018847 | -0.0022557 | 0.0072374 |  | 138
SHR | SHR | 43230 | SHORE_ | 7 |  |  |  | SOUTH2001 | HARRIS | -0.00059441 | 0.0019075 | -0.0041609 | 0.013352 |  | 138
_SN | _SN | 43240 | SINTEK | 41.1 |  |  |  | SOUTH2001 | BRAZORIA | 0.0019683 | -0.0063028 | 0.080898 | -0.25905 |  | 138
SOE | SOE | 43250 | SOUTH_ | 3.3 |  |  |  | SOUTH2001 | HARRIS | -0.00066931 | 0.0021495 | -0.0022087 | 0.0070933 |  | 138
SO | SO | 43260 | SOWYCK 8 | 48.8 |  |  |  | SOUTH2001 | BRAZORIA | -0.00015442 | 0.00044476 | -0.0075358 | 0.021704 |  | 138
_SP | _SP | 43271 | SPENCR 8 | 31.1 |  |  |  | SOUTH2001 | HARRIS | -0.00059274 | 0.0019017 | -0.018434 | 0.059144 |  | 138
_SP | _SP | 43272 | SPENCR 8 | 67.4 |  |  |  | SOUTH2001 | HARRIS | -0.00050195 | 0.0016017 | -0.033832 | 0.10795 |  | 138
STW | STW | 43290 | STEWRT 8 | 30.1 |  |  |  | SOUTH2001 | GALVESTON | -0.00013193 | 0.00041204 | -0.0039712 | 0.012402 |  | 138
STR | STR | 43300 | STRATT | 15.4 |  |  |  | SOUTH2001 | BRAZORIA | 0.0017419 | -0.0055854 | 0.026825 | -0.086015 |  | 138
SRF | SRF | 43310 | SURFSI | 5.4 |  |  |  | SOUTH2001 | BRAZORIA | 0.0019562 | -0.0062728 | 0.010564 | -0.033873 |  | 69
_TE | _TE | 43321 | TELPHN 8 | 28.2 |  |  |  | SOUTH2001 | HARRIS | -0.00019044 | 0.00059215 | -0.0053704 | 0.016699 |  | 138
_TE | _TE | 43322 | TELPHN 8 | 30.2 |  |  |  | SOUTH2001 | HARRIS | -0.00034577 | 0.0010957 | -0.010442 | 0.033091 |  | 138
TGF | TGF | 43340 | TEXGLF | 0.6 |  |  |  | SOUTH2001 | WHARTON | 0.0033589 | -0.010387 | 0.0020154 | -0.0062323 |  | 138
_TP | _TP | 43350 | TEXWES | 0.4 |  |  |  | SOUTH2001 | BRAZORIA | 0.0014479 | -0.0047307 | 0.00057917 | -0.0018923 |  | 69
|  | 43355 | TIKIIS 8 | 4.1 |  |  |  | SOUTH2001 | GALVESTON | -0.00013573 | 0.00042419 | -0.0005565 | 0.0017392 |  | 138
_VL | _VL | 43360 | VLASCO 8 | 15.6 |  |  |  | SOUTH2001 | BRAZORIA | 0.0020186 | -0.0064622 | 0.031491 | -0.10081 |  | 138
_VL | _VL | 43370 | VLASCO 9 | 15.1 |  |  |  | SOUTH2001 | BRAZORIA | 0.0019562 | -0.0062728 | 0.029539 | -0.09472 |  | 69
_WC | _WC | 43380 | W_COL_ 8 |  |  |  |  | SOUTH2001 | BRAZORIA | 0.0014888 | -0.0047649 | 0 | 0 |  | 138
_WC | _WC | 43390 | W_COL_ 9 | 1.1 |  |  |  | SOUTH2001 | BRAZORIA | 0.0014479 | -0.0047307 | 0.0015927 | -0.0052038 |  | 69
_GA | _GA | 43400 | W_GALV 8 |  |  |  |  | SOUTH2001 | GALVESTON | -0.00012111 | 0.00037742 | 0 | 0 |  | 138
_GA | _GA | 43410 | W_GALV 9 | 69.3 |  |  |  | SOUTH2001 | GALVESTON | -0.00012226 | 0.00037877 | -0.0084726 | 0.026249 |  | 69
WEB | WEB | 43500 | WEBSTR 8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00016857 | 0.00052922 | 0 | 0 |  | 138
WEB | WEB | 43501 | WEBSTRT8 | 30.8 |  |  |  | SOUTH2001 | HARRIS | -0.00015409 | 0.00048375 | -0.0047459 | 0.014899 |  | 138
WEB | WEB | 43502 | WEBSTRT8 | 39.2 |  |  |  | SOUTH2001 | HARRIS | -0.00053258 | 0.001703 | -0.020877 | 0.066758 |  | 138
WEB | WEB | 43503 | WEBSTRD8 | 14.6 |  |  |  | SOUTH2001 | GALVESTON | -0.00054582 | 0.0017492 | -0.0079689 | 0.025539 |  | 138
WEB | WEB | 43504 | WEBSTRD8 |  |  |  |  | SOUTH2001 | GALVESTON | -0.00053245 | 0.0017026 | 0 | 0 |  | 138
WEB | WEB | 43505 | WEB MID |  |  |  |  | SOUTH2001 | HARRIS | -0.0002234 | 0.00070518 | 0 | 0 |  | 0
WEB | WEB | 43510 | WEBSTR 9 |  |  |  |  | SOUTH2001 | HARRIS | -0.00021372 | 0.0006741 | 0 | 0 |  | 69
_WR | _WR | 43570 | WHARTN 8 | 37.8 |  |  |  | SOUTH2001 | WHARTON | 0.0033142 | -0.01088 | 0.12528 | -0.41127 |  | 138
WAP | WAP | 44000 | W_A_P_ 5 |  |  |  |  | SOUTH2001 | FORT BEND | -0.00012686 | 0.00051407 | 0 | 0 |  | 345
WAP | WAP | 44001 | WAP_C710 |  |  |  |  | SOUTH2001 | FORT BEND | 0.0006823 | -0.0021907 | 0 | 0 |  | 345
WAP | WAP | 44010 | W_A_P_ 8 |  |  |  |  | SOUTH2001 | FORT BEND | 0.0002121 | -0.00083875 | 0 | 0 |  | 138
_AF | _AF | 44020 | ALIEF 8 | 101.8 |  |  |  | SOUTH2001 | HARRIS | -0.00029008 | 0.00078029 | -0.02953 | 0.079434 |  | 138
_AR | _AR | 44031 | ARCOLA 8 | 7.3 |  |  |  | SOUTH2001 | FORT BEND | 0.00025131 | -0.00092588 | 0.0018346 | -0.006759 |  | 138
_AR | _AR | 44032 | ARCOLA 8 | 15 |  |  |  | SOUTH2001 | FORT BEND | 0.00025129 | -0.00092584 | 0.0037694 | -0.013888 |  | 138
BAR | BAR | 44051 | BARKER 8 | 86.4 |  |  |  | SOUTH2001 | HARRIS | -0.00032804 | 0.00095915 | -0.028343 | 0.082871 |  | 138
BAR | BAR | 44052 | BARKER 8 | 69.6 |  |  |  | SOUTH2001 | HARRIS | -0.00036878 | 0.0010773 | -0.025667 | 0.074981 |  | 138
_BC | _BC | 44070 | BG_CRK 9 | 5.7 |  |  |  | SOUTH2001 | FORT BEND | 0.00072948 | -0.0028047 | 0.0041581 | -0.015987 |  | 69
_BL | _BL | 44081 | BLURIG 8 | 24 |  |  |  | SOUTH2001 | HARRIS | -7.9095e-05 | 0.00016902 | -0.0018983 | 0.0040564 |  | 138
_BL | _BL | 44082 | BLURIG 8 | 32.3 |  |  |  | SOUTH2001 | HARRIS | -7.982e-05 | 0.00017153 | -0.0025782 | 0.0055404 |  | 138
_BV | _BV | 44100 | BRAZOS 8 | 23 |  |  |  | SOUTH2001 | FORT BEND | 0.00033307 | -0.0016655 | 0.0076605 | -0.038305 |  | 138
_BS | _BS | 44110 | BRISCO | 0.7 |  |  |  | SOUTH2001 | FORT BEND | 2.0784e-05 | -0.00015296 | 1.4549e-05 | -0.00010707 |  | 69
_BM | _BM | 44120 | BRITMR 8 | 60.2 |  |  |  | SOUTH2001 | HARRIS | -0.00050228 | 0.0014644 | -0.030237 | 0.08816 |  | 138
CAC | CAC | 44130 | CANEY_ | 10.9 |  |  |  | SOUTH2001 | WHARTON | 0.0032307 | -0.0107 | 0.035215 | -0.11663 |  | 138
_CE | _CE | 44140 | CLODIN 8 | 92.2 |  |  |  | SOUTH2001 | HARRIS | -0.00032804 | 0.00095915 | -0.030245 | 0.088434 |  | 138
_CE | _CE | 44150 | CCLODIN |  |  |  |  | SOUTH2001 | HARRIS | -0.00032803 | 0.00095912 | 0 | 0 |  | 138
CIN | CIN | 44160 | COLLIN | 1.7 |  |  |  | SOUTH2001 | FORT BEND | 0.00057547 | -0.0023918 | 0.00097829 | -0.0040661 |  | 69
CRB | CRB | 44170 | CRABB 8 | 109.4 |  |  |  | SOUTH2001 | FORT BEND | 0.00044841 | -0.0018544 | 0.049056 | -0.20287 |  | 138
_DL | _DL | 44180 | DEWALT 8 | 96 |  |  |  | SOUTH2001 | FORT BEND | 3.8456e-06 | -0.00011802 | 0.00036918 | -0.01133 |  | 138
_EB | _EB | 44190 | E_BERN 8 | 11 |  |  |  | SOUTH2001 | WHARTON | 0.0022389 | -0.0085566 | 0.024628 | -0.094122 |  | 138
_EC | _EC | 44210 | ECHO 8 | 62.6 |  |  |  | SOUTH2001 | HARRIS | -0.00047513 | 0.0013941 | -0.029743 | 0.087273 |  | 138
_EC | _EC | 44211 | ECHO T8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00047532 | 0.0013946 | 0 | 0 |  | 138
_EC | _EC | 44212 | ECHO T8 | 42.1 |  |  |  | SOUTH2001 | HARRIS | -0.00047388 | 0.0013909 | -0.01995 | 0.058556 |  | 138
_FL | _FL | 44230 | FLEWLN 8 | 12.9 |  |  |  | SOUTH2001 | FORT BEND | 8.0522e-05 | -0.00085144 | 0.0010387 | -0.010984 |  | 138
_FL | _FL | 44240 | FLEWLN 9 |  |  |  |  | SOUTH2001 | FORT BEND | 0.00025397 | -0.0013913 | 0 | 0 |  | 69
FOS | FOS | 44250 | FOSTER | 0.1 |  |  |  | SOUTH2001 | FORT BEND | 0.00025429 | -0.0013923 | 2.5429e-05 | -0.00013923 |  | 69
FZ | FZ | 44261 | FRANZ 8 | 76.6 |  |  |  | SOUTH2001 | HARRIS | 8.0522e-05 | -0.00085144 | 0.006168 | -0.06522 |  | 138
FZ | FZ | 44262 | FRANZ 8 | 65.8 |  |  |  | SOUTH2001 | HARRIS | -0.00025355 | 0.00016789 | -0.016684 | 0.011047 |  | 138
_FB | _FB | 44280 | FTBEND 8 |  |  |  |  | SOUTH2001 | FORT BEND | 0.00061852 | -0.0025855 | 0 | 0 |  | 138
_FB | _FB | 44290 | FTBEND 9 |  |  |  |  | SOUTH2001 | FORT BEND | 0.00058008 | -0.0024126 | 0 | 0 |  | 69
_FB | _FB | 44300 | CFTBEND8 |  |  |  |  | SOUTH2001 | FORT BEND | 0.00062076 | -0.0025938 | 0 | 0 |  | 138
_HY | _HY | 44310 | HAYES 8 | 68.3 |  |  |  | SOUTH2001 | HARRIS | -0.00040528 | 0.0011517 | -0.027681 | 0.078661 |  | 138
_HY | _HY | 44311 | HAYES T8 | 31.2 |  |  |  | SOUTH2001 | HARRIS | -0.0004274 | 0.0012521 | -0.013335 | 0.039067 |  | 138
_HY | _HY | 44312 | HAYES T8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00040424 | 0.0011483 | 0 | 0 |  | 138
IM | IM | 44341 | IMPERL 8 | 58.4 |  |  |  | SOUTH2001 | FORT BEND | 0.0002121 | -0.00083875 | 0.012387 | -0.048983 |  | 138
IM | IM | 44342 | IMPERL 8 | 84.6 |  |  |  | SOUTH2001 | FORT BEND | 5.01e-05 | -0.00027669 | 0.0042384 | -0.023408 |  | 138
_IR | _IR | 44361 | INTERM 8 | 17.3 |  |  |  | SOUTH2001 | HARRIS | -0.00015859 | 0.00044912 | -0.0027435 | 0.0077698 |  | 138
_IR | _IR | 44362 | INTERM 8 | 15 |  |  |  | SOUTH2001 | HARRIS | -5.8092e-05 | 0.00011076 | -0.00087138 | 0.0016614 |  | 138
_JU | _JU | 44380 | JULIFF | 1.6 |  |  |  | SOUTH2001 | FORT BEND | 3.9915e-05 | -0.00021555 | 6.3864e-05 | -0.00034488 |  | 69
_KR | _KR | 44390 | KARSTN 8 |  |  |  |  | SOUTH2001 | BRAZORIA | 0.00025987 | -0.0009449 | 0 | 0 |  | 138
_KR | _KR | 44400 | KARSTN 9 |  |  |  |  | SOUTH2001 | BRAZORIA | 0.00013526 | -0.00052745 | 0 | 0 |  | 69
_KR | _KR | 44410 | CKARSTN8 |  |  |  |  | SOUTH2001 | BRAZORIA | 0.0002613 | -0.00094936 | 0 | 0 |  | 138
_KT | _KT | 44421 | KATY 8 | 69.1 |  |  |  | SOUTH2001 | WALLER | 8.0522e-05 | -0.00085144 | 0.0055641 | -0.058835 |  | 138
_KT | _KT | 44422 | KATY 8 | 45.7 |  |  |  | SOUTH2001 | WALLER | -0.000129 | -0.00021214 | -0.0058952 | -0.0096949 |  | 138
_MV | _MV | 44440 | MANVEL 9 | 15.4 |  |  |  | SOUTH2001 | BRAZORIA | 6.7598e-05 | -0.00029516 | 0.001041 | -0.0045455 |  | 69
MAR | MAR | 44450 | MASON 8 | 115.9 |  |  |  | SOUTH2001 | HARRIS | -0.00019972 | 0.00039186 | -0.023147 | 0.045416 |  | 138
_ME | _ME | 44461 | MEMORL 8 | 35.9 |  |  |  | SOUTH2001 | HARRIS | -0.00050228 | 0.0014644 | -0.018032 | 0.052574 |  | 138
_ME | _ME | 44462 | MEMORL 8 | 55.7 |  |  |  | SOUTH2001 | HARRIS | -0.00043285 | 0.0012631 | -0.02411 | 0.070355 |  | 138
_MC | _MC | 44481 | MOCITY 8 | 18 |  |  |  | SOUTH2001 | FORT BEND | -3.6405e-05 | 2.1278e-05 | -0.0006553 | 0.000383 |  | 138
_MC | _MC | 44482 | MOCITY 8 | 19 |  |  |  | SOUTH2001 | FORT BEND | 4.9521e-05 | -0.00027468 | 0.0009409 | -0.0052189 |  | 138
MLA | MLA | 44490 | MULA__ | 8.6 |  |  |  | SOUTH2001 | FORT BEND | 3.8456e-06 | -0.00011802 | 3.3072e-05 | -0.001015 |  | 138
_OB | _OB | 44500 | OBRIEN 5 |  |  |  |  | SOUTH2001 | FORT BEND | -0.00060028 | 0.0021712 | 0 | 0 |  | 345
_OB | _OB | 44510 | OBRIEN 8 |  |  |  |  | SOUTH2001 | FORT BEND | -0.00032639 | 0.00095385 | 0 | 0 |  | 138
_OB | _OB | 44511 | OBTR1 | 19.1 |  |  |  | SOUTH2001 | FORT BEND | -0.0003264 | 0.00095389 | -0.0062343 | 0.018219 |  | 138
_OB | _OB | 44512 | OBTR2 | 19.1 |  |  |  | SOUTH2001 | FORT BEND | -0.0003264 | 0.00095389 | -0.0062343 | 0.018219 |  | 138
_OR | _OR | 44540 | ORCHRD 8 | 5.2 |  |  |  | SOUTH2001 | FORT BEND | 0.0016463 | -0.0063729 | 0.0085608 | -0.033139 |  | 138
_QV | _QV | 44551 | QUAIL 8 | 30.5 |  |  |  | SOUTH2001 | FORT BEND | 1.1074e-05 | -0.00014304 | 0.00033777 | -0.0043627 |  | 138
_QV | _QV | 44552 | QUAIL 8 | 40.1 |  |  |  | SOUTH2001 | FORT BEND | 8.4946e-06 | -0.00011031 | 0.00034064 | -0.0044234 |  | 138
_RE | _RE | 44570 | READNG 8 | 60.1 |  |  |  | SOUTH2001 | FORT BEND | 0.00054888 | -0.0022862 | 0.032988 | -0.1374 |  | 138
_RI | _RI | 44580 | RICHMN | 0.5 |  |  |  | SOUTH2001 | FORT BEND | 0.00057547 | -0.0023918 | 0.00028773 | -0.0011959 |  | 69
_RO | _RO | 44590 | ROARK 8 | 143.1 |  |  |  | SOUTH2001 | HARRIS | -0.00027343 | 0.00080148 | -0.039127 | 0.11469 |  | 138
_RZ | _RZ | 44600 | ROSHRN 8 | 17.7 |  |  |  | SOUTH2001 | BRAZORIA | 0.00077081 | -0.0025353 | 0.013643 | -0.044874 |  | 138
_RS | _RS | 44610 | ROSNBG 9 | 48.3 |  |  |  | SOUTH2001 | FORT BEND | 0.00057547 | -0.0023918 | 0.027795 | -0.11553 |  | 69
_SR | _SR | 44620 | SAUER 8 | 113.6 |  |  |  | SOUTH2001 | HARRIS | -0.00048944 | 0.0014312 | -0.055601 | 0.16258 |  | 138
SOT | SOT | 44630 | SCOTT_ | 7.9 |  |  |  | SOUTH2001 | FORT BEND | 0.0010369 | -0.0041271 | 0.0081912 | -0.032604 |  | 138
_SE | _SE | 44640 | SEALY 8 | 31.9 |  |  |  | SOUTH2001 | AUSTIN | 0.0027247 | -0.012377 | 0.086918 | -0.39484 |  | 138
|  | 44651 | SIENNA 8 | 40.8 |  |  |  | SOUTH2001 | FORT BEND | 0.00012768 | -0.00054658 | 0.0052093 | -0.022301 |  | 138
|  | 44652 | SIENNA 8 | 40.8 |  |  |  | SOUTH2001 | FORT BEND | 0.00012761 | -0.00054635 | 0.0052065 | -0.022291 |  | 138
STF | STF | 44670 | STAFRD 8 | 72.8 |  |  |  | SOUTH2001 | FORT BEND | 1.3245e-05 | -0.00014882 | 0.00096422 | -0.010834 |  | 138
_TV | _TV | 44691 | TELVEW 8 | 14 |  |  |  | SOUTH2001 | FORT BEND | 1.0446e-05 | -0.00014086 | 0.00014624 | -0.0019721 |  | 138
_TV | _TV | 44692 | TELVEW 8 | 16.8 |  |  |  | SOUTH2001 | FORT BEND | 9.4541e-06 | -0.00011349 | 0.00015883 | -0.0019067 |  | 138
_TI | _TI | 44710 | TEXINS | 15.3 |  |  |  | SOUTH2001 | FORT BEND | -2.7081e-05 | -8.9056e-06 | -0.00041435 | -0.00013626 |  | 138
_TM | _TM | 44721 | THOMSN 8 | 0.4 |  |  |  | SOUTH2001 | FORT BEND | 0.00022362 | -0.00086434 | 8.9447e-05 | -0.00034574 |  | 138
_TM | _TM | 44722 | THOMSN 8 | 2.2 |  |  |  | SOUTH2001 | FORT BEND | 0.00022359 | -0.00086428 | 0.0004919 | -0.0019014 |  | 138
_WA | _WA | 44740 | WALLIS 8 | 8.4 |  |  |  | SOUTH2001 | AUSTIN | 0.0024337 | -0.010088 | 0.020443 | -0.084741 |  | 138
_WZ | _WZ | 44760 | WCHASE 8 | 37.7 |  |  |  | SOUTH2001 | HARRIS | -0.00017323 | 0.00049815 | -0.0065307 | 0.01878 |  | 138
_WZ | _WZ | 44761 | WCHASET8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00016976 | 0.00048611 | 0 | 0 |  | 138
_WZ | _WZ | 44762 | WCHASET8 | 99.2 |  |  |  | SOUTH2001 | HARRIS | -0.00036115 | 0.0010643 | -0.035826 | 0.10558 |  | 138
_WI | _WI | 44780 | WESTIM 8 | 96.4 |  |  |  | SOUTH2001 | HARRIS | -0.00039652 | 0.0011577 | -0.038224 | 0.11161 |  | 138
_WT | _WT | 44790 | WIRT 8 | 84.2 |  |  |  | SOUTH2001 | HARRIS | -0.00045778 | 0.0013492 | -0.038545 | 0.1136 |  | 138
_WD | _WD | 44801 | WOODCK 8 | 52.3 |  |  |  | SOUTH2001 | HARRIS | -0.00050228 | 0.0014644 | -0.026269 | 0.076591 |  | 138
_WD | _WD | 44802 | WOODCK 8 | 63.6 |  |  |  | SOUTH2001 | HARRIS | -0.00045336 | 0.0013226 | -0.028834 | 0.084115 |  | 138
THW | THW | 45500 | T_H_W_ 5 |  |  |  |  | SOUTH2001 | HARRIS | -0.0011173 | 0.0030571 | 0 | 0 |  | 345
THW | THW | 45510 | T_H_W_E8 |  |  |  |  | SOUTH2001 | HARRIS | -0.0012263 | 0.0035682 | 0 | 0 |  | 138
THW | THW | 45511 | T_H_W_D5 | 99.2 |  |  |  | SOUTH2001 | HARRIS | -0.0012261 | 0.0035683 | -0.12162 | 0.35398 |  | 138
THW | THW | 45512 | T_H_W_D5 | 72.1 |  |  |  | SOUTH2001 | HARRIS | -0.001226 | 0.0035683 | -0.088397 | 0.25728 |  | 138
THW | THW | 45515 | T_H_W_W8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00082157 | 0.0023261 | 0 | 0 |  | 138
THW | THW | 45520 | THW MID |  |  |  |  | SOUTH2001 | HARRIS | -0.0010135 | 0.0029583 | 0 | 0 |  | 0
THW | THW | 45530 | T_H_W_ 9 |  |  |  |  | SOUTH2001 | HARRIS | -0.0010178 | 0.0029708 | 0 | 0 |  | 69
ADK | ADK | 45600 | ADICKS 5 |  |  |  |  | SOUTH2001 | HARRIS | -0.00073043 | 0.0021733 | 0 | 0 |  | 345
ADK | ADK | 45610 | ADICKS 8 | 87.8 |  |  |  | SOUTH2001 | HARRIS | -0.00059423 | 0.001751 | -0.052173 | 0.15374 |  | 138
ADK | ADK | 45620 | CADICKS8 |  |  |  |  | SOUTH2001 | HARRIS | -0.0005945 | 0.001752 | 0 | 0 |  | 138
_AN | _AN | 45630 | AIRLIN 8 | 79.3 |  |  |  | SOUTH2001 | HARRIS | -0.00075715 | 0.002314 | -0.060042 | 0.1835 |  | 138
_AD | _AD | 45640 | ALDINE 8 | 76.2 |  |  |  | SOUTH2001 | HARRIS | -0.00080731 | 0.0024959 | -0.061517 | 0.19019 |  | 138
_BA | _BA | 45651 | BAMMEL 8 | 84.8 |  |  |  | SOUTH2001 | HARRIS | -0.0012257 | 0.0035686 | -0.10394 | 0.30261 |  | 138
_BA | _BA | 45652 | BAMMEL 8 | 102 |  |  |  | SOUTH2001 | HARRIS | -0.0012364 | 0.0035969 | -0.12611 | 0.36688 |  | 138
_BY | _BY | 45670 | BERRY 8 | 71.5 |  |  |  | SOUTH2001 | HARRIS | -0.00088256 | 0.0026945 | -0.063103 | 0.19266 |  | 138
_CB | _CB | 45681 | CAMBEL 8 | 29.7 |  |  |  | SOUTH2001 | HARRIS | -0.00062945 | 0.0018757 | -0.018695 | 0.055709 |  | 138
_CB | _CB | 45682 | CAMBEL 8 | 68.1 |  |  |  | SOUTH2001 | HARRIS | -0.00062949 | 0.0018758 | -0.042868 | 0.12774 |  | 138
CI | CI | 45700 | CAMRON | 9.5 |  |  |  | SOUTH2001 | HARRIS | -0.00073773 | 0.002114 | -0.0070084 | 0.020083 |  | 138
CYF | CYF | 45711 | CYFAIR 8 | 54.5 |  |  |  | SOUTH2001 | HARRIS | -0.00073512 | 0.0021074 | -0.040064 | 0.11485 |  | 138
CYF | CYF | 45712 | CYFAIR 8 | 54.5 |  |  |  | SOUTH2001 | HARRIS | -0.00074034 | 0.0021206 | -0.040348 | 0.11557 |  | 138
_DH | _DH | 45730 | DEIHL 8 | 82.9 |  |  |  | SOUTH2001 | HARRIS | -0.00073806 | 0.0021775 | -0.061185 | 0.18052 |  | 138
_DQ | _DQ | 45740 | DRILCO | 13.2 |  |  |  | SOUTH2001 | HARRIS | -0.0012932 | 0.0038554 | -0.01707 | 0.050891 |  | 138
_EU | _EU | 45750 | EUREKA 8 | 91.2 |  |  |  | SOUTH2001 | HARRIS | -0.00037768 | 0.0011267 | -0.034444 | 0.10276 |  | 138
_FR | _FR | 45760 | FAIRBK 8 | 160.2 |  |  |  | SOUTH2001 | HARRIS | -0.00077967 | 0.0022515 | -0.1249 | 0.36069 |  | 138
_FM | _FM | 45770 | FREMAN 8 | 6 |  |  |  | SOUTH2001 | HARRIS | -0.00043878 | 0.00073307 | -0.0026327 | 0.0043984 |  | 138
_GZ | _GZ | 45781 | GEARS 8 | 66.8 |  |  |  | SOUTH2001 | HARRIS | -0.0012091 | 0.003581 | -0.080765 | 0.23921 |  | 138
_GZ | _GZ | 45782 | GEARS 8 | 39.2 |  |  |  | SOUTH2001 | HARRIS | -0.0012092 | 0.0035809 | -0.0474 | 0.14037 |  | 138
GE | GE | 45801 | GERTIE 8 | 99.9 |  |  |  | SOUTH2001 | HARRIS | -0.00073996 | 0.0021196 | -0.073922 | 0.21175 |  | 138
GE | GE | 45802 | GERTIE 8 | 49 |  |  |  | SOUTH2001 | HARRIS | -0.0007355 | 0.0021084 | -0.03604 | 0.10331 |  | 138
_GR | _GR | 45821 | GREENS 8 | 10.1 |  |  |  | SOUTH2001 | HARRIS | -0.00081107 | 0.0025214 | -0.0081918 | 0.025467 |  | 138
_GR | _GR | 45822 | GREENS 8 | 10.9 |  |  |  | SOUTH2001 | HARRIS | -0.0011958 | 0.0035908 | -0.013035 | 0.03914 |  | 138
_HR | _HR | 45840 | HARDY 8 | 29.2 |  |  |  | SOUTH2001 | HARRIS | -0.00080308 | 0.0024671 | -0.02345 | 0.072041 |  | 138
_HR | _HR | 45850 | CHARDY 8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00080232 | 0.0024646 | 0 | 0 |  | 138
_HV | _HV | 45861 | HIDDEN 8 | 29.8 |  |  |  | SOUTH2001 | HARRIS | -0.0012079 | 0.0035818 | -0.035995 | 0.10674 |  | 138
_HV | _HV | 45862 | HIDDEN 8 | 36 |  |  |  | SOUTH2001 | HARRIS | -0.001208 | 0.0035818 | -0.043487 | 0.12894 |  | 138
_HK | _HK | 45880 | HOCKLY 8 | 24.1 |  |  |  | SOUTH2001 | HARRIS | -0.00094622 | 0.0022814 | -0.022804 | 0.054982 |  | 138
_HK | _HK | 45890 | HOCKLY 9 | 12.8 |  |  |  | SOUTH2001 | HARRIS | -0.00030415 | -0.00036208 | -0.0038931 | -0.0046346 |  | 69
INT | INT | 45900 | INTEQ_ | 4.5 |  |  |  | SOUTH2001 | HARRIS | -0.0013375 | 0.0039756 | -0.0060186 | 0.01789 |  | 138
_IT | _IT | 45910 | INTER 8 | 21.3 |  |  |  | SOUTH2001 | HARRIS | -0.0013929 | 0.0041263 | -0.029669 | 0.087889 |  | 138
JES | JES | 45921 | JESTER 8 | 27 |  |  |  | SOUTH2001 | HARRIS | -0.0012256 | 0.0035686 | -0.033092 | 0.096353 |  | 138
JES | JES | 45922 | JESTER 8 |  |  |  |  | SOUTH2001 | HARRIS | -0.0012373 | 0.0035995 | 0 | 0 |  | 138
KI | KI | 45940 | KLEIN 8 | 123.2 |  |  |  | SOUTH2001 | HARRIS | -0.0014438 | 0.0041848 | -0.17787 | 0.51556 |  | 138
KL | KL | 45951 | KLUGE 8 | 89.1 |  |  |  | SOUTH2001 | HARRIS | -0.00074072 | 0.0021215 | -0.065998 | 0.18903 |  | 138
KL | KL | 45952 | KLUGE 8 | 57.3 |  |  |  | SOUTH2001 | HARRIS | -0.0014447 | 0.0041874 | -0.08278 | 0.23994 |  | 138
|  | 45971 | KUYDAL 5 | 25 |  |  |  | SOUTH2001 | HARRIS | -0.0021545 | 0.0063637 | -0.053862 | 0.15909 |  | 345
|  | 45972 | KUYDAL 5 | 25 |  |  |  | SOUTH2001 | HARRIS | -0.0023366 | 0.0097777 | -0.058414 | 0.24444 |  | 345
_LK | _LK | 45990 | L_YORK 9 | 78.6 |  |  |  | SOUTH2001 | HARRIS | -0.00068158 | 0.0020071 | -0.053572 | 0.15776 |  | 69
_LA | _LA | 46001 | LAUDER 8 | 15.2 |  |  |  | SOUTH2001 | HARRIS | -0.0011958 | 0.0035908 | -0.018177 | 0.05458 |  | 138
_LA | _LA | 46002 | LAUDER 8 | 19.1 |  |  |  | SOUTH2001 | HARRIS | -0.0011159 | 0.003362 | -0.021313 | 0.064215 |  | 138
LEG | LEG | 46020 | LIMEST 5 |  |  |  |  | SOUTH2001 | LIMESTONE | -0.0070066 | 0.042985 | 0 | 0 |  | 345
_LW | _LW | 46031 | LOCKWD 8 | 36 |  |  |  | SOUTH2001 | HARRIS | -0.0011958 | 0.0035908 | -0.04305 | 0.12927 |  | 138
_LW | _LW | 46032 | LOCKWD 8 | 26 |  |  |  | SOUTH2001 | HARRIS | -0.00081378 | 0.0025398 | -0.021158 | 0.066036 |  | 138
_LU | _LU | 46051 | LOUETA 8 | 71.6 |  |  |  | SOUTH2001 | HARRIS | -0.0017058 | 0.0049693 | -0.12213 | 0.3558 |  | 138
_LU | _LU | 46052 | LOUETA 8 | 73.6 |  |  |  | SOUTH2001 | HARRIS | -0.0017057 | 0.0049692 | -0.12554 | 0.36573 |  | 138
|  | 46070 | MINMAX 8 | 19.2 |  |  |  | SOUTH2001 | HARRIS | -0.00043681 | 0.0012949 | -0.0083868 | 0.024862 |  | 138
_NB | _NB | 46100 | N_BELT 5 |  |  |  |  | SOUTH2001 | HARRIS | -0.0012031 | 0.0037036 | 0 | 0 |  | 345
_NB | _NB | 46110 | N_BELT 8 | 110 |  |  |  | SOUTH2001 | HARRIS | -0.0011958 | 0.0035908 | -0.13154 | 0.39499 |  | 138
_PT | _PT | 46220 | PETERS 8 |  |  |  |  | SOUTH2001 | AUSTIN | 0.0028461 | -0.013332 | 0 | 0 |  | 138
_PT | _PT | 46230 | PETERS 9 | 2 |  |  |  | SOUTH2001 | AUSTIN | 0.0015627 | -0.008048 | 0.0031253 | -0.016096 |  | 69
_PI | _PI | 46240 | PINHUR 8 | 68.9 |  |  |  | SOUTH2001 | MONTGOMERY | -0.0017554 | 0.0050682 | -0.12095 | 0.3492 |  | 138
_RB | _RB | 46250 | RACOON 9 | 1.3 |  |  |  | SOUTH2001 | AUSTIN | 0.00085853 | -0.005149 | 0.0011161 | -0.0066937 |  | 69
_RA | _RA | 46261 | RAYFRD 8 | 60.3 |  |  |  | SOUTH2001 | MONTGOMERY | -0.0017695 | 0.0051386 | -0.1067 | 0.30986 |  | 138
_RA | _RA | 46262 | RAYFRD 8 | 30.1 |  |  |  | SOUTH2001 | MONTGOMERY | -0.0017693 | 0.0051382 | -0.053256 | 0.15466 |  | 138
_RU | _RU | 46281 | RITTEN 8 | 15.9 |  |  |  | SOUTH2001 | HARRIS | -0.00080547 | 0.0024834 | -0.012807 | 0.039486 |  | 138
_RU | _RU | 46282 | RITTEN 8 | 25.2 |  |  |  | SOUTH2001 | HARRIS | -0.00095308 | 0.0028963 | -0.024018 | 0.072986 |  | 138
_SA | _SA | 46300 | SATSUM 8 | 179.7 |  |  |  | SOUTH2001 | HARRIS | -0.00065136 | 0.0018667 | -0.11705 | 0.33545 |  | 138
_SA | _SA | 46301 | SATSUMT8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00065224 | 0.0018691 | 0 | 0 |  | 138
_SA | _SA | 46302 | SATSUMT8 | 49 |  |  |  | SOUTH2001 | HARRIS | -0.000639 | 0.0018643 | -0.031311 | 0.09135 |  | 138
_SW | _SW | 46331 | SCENIC 8 | 25.3 |  |  |  | SOUTH2001 | HARRIS | -0.00081376 | 0.0025397 | -0.020588 | 0.064254 |  | 138
_SW | _SW | 46332 | SCENIC 8 | 23.5 |  |  |  | SOUTH2001 | HARRIS | -0.0011958 | 0.0035908 | -0.028102 | 0.084384 |  | 138
_TO | _TO | 46351 | TODD 8 | 58.7 |  |  |  | SOUTH2001 | HARRIS | -0.0006569 | 0.0019728 | -0.03856 | 0.11581 |  | 138
_TO | _TO | 46352 | TODD 8 | 28.1 |  |  |  | SOUTH2001 | HARRIS | -0.00065676 | 0.0019723 | -0.018455 | 0.055423 |  | 138
_TB | _TB | 46500 | TOMBAL 5 |  |  |  |  | SOUTH2001 | HARRIS | -0.0023464 | 0.0067815 | 0 | 0 |  | 345
_TB | _TB | 46510 | TOMBAL 8 |  |  |  |  | SOUTH2001 | HARRIS | -0.001943 | 0.0056 | 0 | 0 |  | 138
_TB | _TB | 46511 | TOMBALT8 | 46.8 |  |  |  | SOUTH2001 | HARRIS | -0.0019409 | 0.0055931 | -0.090836 | 0.26176 |  | 138
_TB | _TB | 46512 | TOMBALT8 | 41.2 |  |  |  | SOUTH2001 | HARRIS | -0.0019417 | 0.0055965 | -0.079997 | 0.23058 |  | 138
_TB | _TB | 46520 | CTOMBAL8 |  |  |  |  | SOUTH2001 | HARRIS | -0.0019421 | 0.0055974 | 0 | 0 |  | 138
TWG | TWG | 46550 | TRSWIG 8 | 103.7 |  |  |  | SOUTH2001 | HARRIS | -0.0013768 | 0.0041155 | -0.14277 | 0.42677 |  | 138
_WL | _WL | 46560 | WALLER 8 | 12 |  |  |  | SOUTH2001 | WALLER | -0.00094622 | 0.0022814 | -0.011355 | 0.027377 |  | 138
_WF | _WF | 46570 | WESFLD 8 | 100.7 |  |  |  | SOUTH2001 | HARRIS | -0.0015839 | 0.0046452 | -0.15949 | 0.46777 |  | 138
_WO | _WO | 46600 | WHITOK 5 |  |  |  |  | SOUTH2001 | HARRIS | -0.00051182 | 0.0015452 | 0 | 0 |  | 345
_WO | _WO | 46610 | WHITOKN8 | 62.8 |  |  |  | SOUTH2001 | HARRIS | -0.00069115 | 0.0020941 | -0.043404 | 0.13151 |  | 138
_WO | _WO | 46611 | WHITOKD8 | 25.8 |  |  |  | SOUTH2001 | HARRIS | -0.00042109 | 0.0012542 | -0.010864 | 0.032358 |  | 138
_WO | _WO | 46612 | WHITOKD8 | 31.4 |  |  |  | SOUTH2001 | HARRIS | -0.00069088 | 0.0020931 | -0.021694 | 0.065723 |  | 138
_WO | _WO | 46615 | WHITOKS8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00042091 | 0.0012537 | 0 | 0 |  | 138
_WO | _WO | 46620 | WHITOK 9 |  |  |  |  | SOUTH2001 | HARRIS | -0.00051562 | 0.0015315 | 0 | 0 |  | 69
WLO | WLO | 46660 | WILLOW | 17.5 |  |  |  | SOUTH2001 | HARRIS | -0.0013817 | 0.0040087 | -0.024179 | 0.070153 |  | 138
_BI | _BI | 47000 | BELAIR 5 |  |  |  |  | SOUTH2001 | HARRIS | -9.7962e-05 | 0.00031993 | 0 | 0 |  | 345
_BI | _BI | 47010 | BELAIRN8 | 74.1 |  |  |  | SOUTH2001 | HARRIS | -0.0002244 | 0.00067661 | -0.016628 | 0.050137 |  | 138
_BI | _BI | 47011 | BELAIRD8 | 50.4 |  |  |  | SOUTH2001 | HARRIS | -0.0002244 | 0.00067661 | -0.01131 | 0.034101 |  | 138
_BI | _BI | 47012 | BELAIRD8 | 24.8 |  |  |  | SOUTH2001 | HARRIS | -0.00022794 | 0.00068668 | -0.005653 | 0.01703 |  | 138
_BI | _BI | 47015 | BELAIRS8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00022752 | 0.00069452 | 0 | 0 |  | 138
_BI | _BI | 47016 | C_BELAIR |  |  |  |  | SOUTH2001 | HARRIS | -0.0002286 | 0.00069795 | 0 | 0 |  | 138
_BR | _BR | 47050 | BRAYS 8 | 93.8 |  |  |  | SOUTH2001 | HARRIS | -0.00019154 | 0.00056363 | -0.017966 | 0.052868 |  | 138
COP | COP | 47060 | COOPER | 3 |  |  |  | SOUTH2001 | FORT BEND | -0.00027059 | 0.00081104 | -0.00081177 | 0.0024331 |  | 69
_DV | _DV | 47071 | DUNVAL 8 | 26.5 |  |  |  | SOUTH2001 | HARRIS | -0.00020226 | 0.00059904 | -0.0053598 | 0.015874 |  | 138
_DV | _DV | 47072 | DUNVAL 8 | 60.8 |  |  |  | SOUTH2001 | HARRIS | -0.00030188 | 0.0008963 | -0.018354 | 0.054495 |  | 138
FAN | FAN | 47090 | FANNIN 8 | 54.3 |  |  |  | SOUTH2001 | GALVESTON | -0.00028439 | 0.00086638 | -0.015442 | 0.047045 |  | 138
_FD | _FD | 47100 | FONDRN 8 | 139.1 |  |  |  | SOUTH2001 | HARRIS | -0.00017814 | 0.0005135 | -0.02478 | 0.071428 |  | 138
_GN | _GN | 47110 | GRANT 8 | 136.2 |  |  |  | SOUTH2001 | HARRIS | -0.00032145 | 0.00099069 | -0.043781 | 0.13493 |  | 138
HOC | HOC | 47150 | H_O_C_ 8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00016066 | 0.00045129 | 0 | 0 |  | 138
HOC | HOC | 47160 | H_O_C_A9 | 61.5 |  |  |  | SOUTH2001 | HARRIS | -0.00027059 | 0.00081104 | -0.016641 | 0.049879 |  | 69
HOC | HOC | 47165 | H_O_C_B9 |  |  |  |  | SOUTH2001 | HARRIS | -0.00018394 | 0.00051678 | 0 | 0 |  | 69
HOC | HOC | 47170 | CH_O_C_8 |  |  |  |  | SOUTH2001 | HARRIS | -0.0001597 | 0.0004481 | 0 | 0 |  | 138
HT | HT | 47191 | HILCRF 8 | 42 |  |  |  | SOUTH2001 | HARRIS | -0.00027905 | 0.00083157 | -0.01172 | 0.034926 |  | 138
HT | HT | 47192 | HILCRF 8 | 37.8 |  |  |  | SOUTH2001 | HARRIS | -0.0002085 | 0.0006209 | -0.0078811 | 0.02347 |  | 138
_HM | _HM | 47210 | HOLMES 8 | 70 |  |  |  | SOUTH2001 | HARRIS | -0.00037588 | 0.0011802 | -0.026312 | 0.082611 |  | 138
_JN | _JN | 47300 | JENETA 5 |  |  |  |  | SOUTH2001 | HARRIS | -0.00019975 | 0.00064693 | 0 | 0 |  | 345
_JN | _JN | 47310 | JENETA 8 | 90.8 |  |  |  | SOUTH2001 | HARRIS | -0.00019735 | 0.00058186 | -0.01792 | 0.052833 |  | 138
_KB | _KB | 47320 | KIRBY 8 | 149.7 |  |  |  | SOUTH2001 | HARRIS | -0.0003055 | 0.00094162 | -0.045733 | 0.14096 |  | 138
_KN | _KN | 47331 | KNIGHT 8 | 20.1 |  |  |  | SOUTH2001 | HARRIS | -0.00023548 | 0.00070231 | -0.0047332 | 0.014116 |  | 138
_KN | _KN | 47332 | KNIGHT 8 | 11.5 |  |  |  | SOUTH2001 | HARRIS | -0.0003054 | 0.0009496 | -0.0035121 | 0.01092 |  | 138
_PZ | _PZ | 47350 | PLAZA 8 | 54.9 |  |  |  | SOUTH2001 | HARRIS | -0.00033143 | 0.0010305 | -0.018195 | 0.056577 |  | 138
_SF | _SF | 47380 | SANFLP 8 | 73.8 |  |  |  | SOUTH2001 | HARRIS | -0.0002805 | 0.00084137 | -0.020701 | 0.062093 |  | 138
_SF | _SF | 47381 | SANFLP28 | 37.1 |  |  |  | SOUTH2001 | HARRIS | -0.0002244 | 0.00067661 | -0.0083251 | 0.025102 |  | 138
_SF | _SF | 47382 | SANFLP28 |  |  |  |  | SOUTH2001 | HARRIS | -0.00027952 | 0.00083849 | 0 | 0 |  | 138
_SF | _SF | 47383 | SANFLP58 | 68.6 |  |  |  | SOUTH2001 | HARRIS | -0.00028148 | 0.00084426 | -0.01931 | 0.057916 |  | 138
_SF | _SF | 47384 | SANFLP58 | 32.7 |  |  |  | SOUTH2001 | HARRIS | -0.0002244 | 0.00067661 | -0.0073377 | 0.022125 |  | 138
_ST | _ST | 47411 | SHARPS 8 | 62.2 |  |  |  | SOUTH2001 | HARRIS | -0.00021195 | 0.00063302 | -0.013183 | 0.039374 |  | 138
_ST | _ST | 47412 | SHARPS 8 | 57.7 |  |  |  | SOUTH2001 | HARRIS | -0.00017246 | 0.00049328 | -0.0099508 | 0.028462 |  | 138
_SD | _SD | 47420 | STADIM 8 | 15.6 |  |  |  | SOUTH2001 | HARRIS | -0.00026979 | 0.00081738 | -0.0042086 | 0.012751 |  | 138
_TC | _TC | 47430 | TECO__ | 29 |  |  |  | SOUTH2001 | HARRIS | -0.00032349 | 0.00099719 | -0.0093811 | 0.028919 |  | 138
_UL | _UL | 47441 | ULRICH 8 | 65.8 |  |  |  | SOUTH2001 | HARRIS | -0.0002244 | 0.00067661 | -0.014765 | 0.044521 |  | 138
_UL | _UL | 47442 | ULRICH 8 | 100.3 |  |  |  | SOUTH2001 | HARRIS | -0.00026675 | 0.00079668 | -0.026755 | 0.079907 |  | 138
_WW | _WW | 47461 | WESTWD 8 | 43.7 |  |  |  | SOUTH2001 | HARRIS | -0.00022785 | 0.00066991 | -0.0099572 | 0.029275 |  | 138
_WW | _WW | 47462 | WESTWD 8 | 27.4 |  |  |  | SOUTH2001 | HARRIS | -0.00018968 | 0.00055457 | -0.0051974 | 0.015195 |  | 138
DT | DT | 47500 | DWNTWN 8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00048147 | 0.0015007 | 0 | 0 |  | 138
DT | DT | 47510 | DWNTWN 9 | 85 |  |  |  | SOUTH2001 | HARRIS | -0.00045606 | 0.0014108 | -0.038765 | 0.11991 |  | 69
|  | 47515 | AUSTIN 8 | 23 |  |  |  | SOUTH2001 | HARRIS | -0.0004322 | 0.0013448 | -0.0099406 | 0.03093 |  | 138
_BG | _BG | 47521 | BLOGET89 | 29.3 |  |  |  | SOUTH2001 | HARRIS | -0.00037231 | 0.0011528 | -0.010909 | 0.033778 |  | 138
_BG | _BG | 47522 | BLOGET89 | 19.1 |  |  |  | SOUTH2001 | HARRIS | -0.00056631 | 0.0017947 | -0.010817 | 0.034278 |  | 69
_BH | _BH | 47540 | BRING 98 | 28.4 |  |  |  | SOUTH2001 | HARRIS | -0.00064253 | 0.0020455 | -0.018248 | 0.058092 |  | 69
BRT | BRT | 47550 | BROWN_ | 4.9 |  |  |  | SOUTH2001 | HARRIS | -0.00064189 | 0.0020432 | -0.0031453 | 0.010012 |  | 69
CGR | CGR | 47560 | COUGAR 8 | 26.5 |  |  |  | SOUTH2001 | HARRIS | -0.00053132 | 0.0016842 | -0.01408 | 0.044632 |  | 138
_CR | _CR | 47570 | CRCKET 8 | 55.6 |  |  |  | SOUTH2001 | HARRIS | -0.00059241 | 0.0018463 | -0.032938 | 0.10266 |  | 138
_DN | _DN | 47580 | DUNLVY 9 | 88.7 |  |  |  | SOUTH2001 | HARRIS | -0.0004139 | 0.0012616 | -0.036713 | 0.1119 |  | 69
_ES | _ES | 47600 | E_SIDEB8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00046846 | 0.0014634 | 0 | 0 |  | 138
|  | 47601 | E_SIDE 8 | 21.1 |  |  |  | SOUTH2001 | HARRIS | -0.00046919 | 0.0014659 | -0.0098999 | 0.030931 |  | 138
|  | 47602 | E_SIDE 8 | 25.9 |  |  |  | SOUTH2001 | HARRIS | -0.00046774 | 0.0014608 | -0.012114 | 0.037835 |  | 138
_ES | _ES | 47610 | CE_SIDE8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00046992 | 0.0014685 | 0 | 0 |  | 138
_GS | _GS | 47630 | GABLE 8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00066441 | 0.0020957 | 0 | 0 |  | 138
_GS | _GS | 47640 | GABLE 9 | 51.8 |  |  |  | SOUTH2001 | HARRIS | -0.00062413 | 0.0019795 | -0.03233 | 0.10254 |  | 69
_GS | _GS | 47641 | GABLED9 | 6.7 |  |  |  | SOUTH2001 | HARRIS | -0.00062421 | 0.0019798 | -0.0041822 | 0.013264 |  | 69
_GS | _GS | 47650 | OPEN@G 9 |  |  |  |  | SOUTH2001 | HARRIS | -0.00045606 | 0.0014108 | 0 | 0 |  | 69
_GT | _GT | 47660 | GARROT 8 | 85.8 |  |  |  | SOUTH2001 | HARRIS | -0.00039679 | 0.0012309 | -0.034044 | 0.10561 |  | 138
_GF | _GF | 47670 | GENRAL | 12.1 |  |  |  | SOUTH2001 | HARRIS | -0.00059226 | 0.0018778 | -0.0071663 | 0.022721 |  | 69
_HE | _HE | 47680 | HIGHTS 9 | 74.9 |  |  |  | SOUTH2001 | HARRIS | -0.00041947 | 0.0012613 | -0.031418 | 0.094471 |  | 69
_HP | _HP | 47690 | HYDEPK 9 | 21.8 |  |  |  | SOUTH2001 | HARRIS | -0.00043332 | 0.0013303 | -0.0094465 | 0.029 |  | 69
_MP | _MP | 47700 | MAG_PK 8 | 67.1 |  |  |  | SOUTH2001 | HARRIS | -0.00064889 | 0.0020805 | -0.04354 | 0.1396 |  | 138
_NS | _NS | 47711 | N_SIDE 8 | 23.3 |  |  |  | SOUTH2001 | HARRIS | -0.00069887 | 0.00216 | -0.016284 | 0.050329 |  | 138
_NS | _NS | 47712 | N_SIDE 8 | 24.7 |  |  |  | SOUTH2001 | HARRIS | -0.00070106 | 0.0022193 | -0.017316 | 0.054815 |  | 138
_PK | _PK | 47730 | POLK 8 | 181.6 |  |  |  | SOUTH2001 | HARRIS | -0.00046221 | 0.0014414 | -0.083938 | 0.26175 |  | 138
_UN | _UN | 47750 | UNIVER 8 |  |  |  |  | SOUTH2001 | HARRIS | -0.00052877 | 0.0016757 | 0 | 0 |  | 138
_UN | _UN | 47751 | UNIVER98 | 16.4 |  |  |  | SOUTH2001 | HARRIS | -0.00053259 | 0.0016885 | -0.0087345 | 0.027692 |  | 138
_UN | _UN | 47752 | UNIVER98 | 39.1 |  |  |  | SOUTH2001 | HARRIS | -0.00053088 | 0.0016819 | -0.020757 | 0.065764 |  | 69
APD | APD | 48500 | AES1 |  |  | 140 | 150 | SOUTH2001 | HARRIS | -0.00078073 | 0.0025248 | -0.11711 | 0.37872 |  | 13.8
_AK | _AK | 48510 | AMO1 |  |  | 32.3 | -7.6294e-07 | SOUTH2001 | BRAZORIA | 0.00050641 | -0.0016389 | -3.8636e-10 | 1.2504e-09 | 15 | 13.8
|  | 48511 | APRO1 |  | 52 |  |  | SOUTH2001 | HARRIS | -0.00070176 | 0.0022629 | -0.036491 | 0.11767 |  | 13.8
|  | 48512 | APRO2 |  | 52 |  |  | SOUTH2001 | HARRIS | -0.00070176 | 0.0022629 | -0.036491 | 0.11767 |  | 13.8
|  | 48513 | APRO3 |  | 52 |  |  | SOUTH2001 | HARRIS | -0.00070176 | 0.0022629 | -0.036491 | 0.11767 |  | 13.8
|  | 48514 | APRO4 |  | 52 |  |  | SOUTH2001 | HARRIS | -0.00070176 | 0.0022629 | -0.036491 | 0.11767 |  | 13.8
BSF | BSF | 48520 | BASF1 |  | 10 | 64.2 | -3.0518e-06 | SOUTH2001 | BRAZORIA | 0.0018937 | -0.0060621 | 0.018937 | -0.06062 | 16 | 13.8
BYU | BYU | 48531 | BYU1 |  |  | 67.5 | 78 | SOUTH2001 | HARRIS | -0.0006117 | 0.0019637 | -0.047713 | 0.15317 |  | 13.8
BYU | BYU | 48532 | BYU2 |  |  | 67.5 | 78 | SOUTH2001 | HARRIS | -0.0006117 | 0.0019637 | -0.047713 | 0.15317 |  | 13.8
BYU | BYU | 48533 | BYU3 |  |  | 67.5 | 78 | SOUTH2001 | HARRIS | -0.0006117 | 0.0019637 | -0.047713 | 0.15317 |  | 13.8
BYU | BYU | 48534 | BYU4 |  |  | 67.5 | 78 | SOUTH2001 | HARRIS | -0.0006117 | 0.0019637 | -0.047713 | 0.15317 |  | 13.8
CAL | CAL | 48551 | CALGT |  |  | 163.9 | 121.8592 | SOUTH2001 | HARRIS | -0.00067995 | 0.0021895 | -0.082858 | 0.26681 | 8 | 13.8
CAL | CAL | 48552 | CALST |  |  | 86 | 63.9408 | SOUTH2001 | HARRIS | -0.00067995 | 0.0021895 | -0.043477 | 0.14 | 8 | 13.8
CTL | CTL | 48561 | CAP1 |  |  | 82.399 | 70.3802 | SOUTH2001 | HARRIS | -0.00055864 | 0.0017912 | -0.039317 | 0.12607 | 17 | 13.8
CTL | CTL | 48562 | CAP2 |  |  | 82.504 | 70.4699 | SOUTH2001 | HARRIS | -0.00055864 | 0.0017912 | -0.039368 | 0.12623 | 17 | 13.8
CTL | CTL | 48563 | CAP3 |  |  | 82.771 | 70.6979 | SOUTH2001 | HARRIS | -0.00055864 | 0.0017912 | -0.039495 | 0.12664 | 17 | 13.8
CTL | CTL | 48564 | CAP4 |  |  | 45.54 | 38.8975 | SOUTH2001 | HARRIS | -0.00055864 | 0.0017912 | -0.02173 | 0.069675 | 17 | 13.8
CTL | CTL | 48565 | CAP5 |  |  | 11.185 | 9.5535 | SOUTH2001 | HARRIS | -0.00055864 | 0.0017912 | -0.005337 | 0.017113 | 17 | 13.8
CBY | CBY | 48581 | CB 1 |  |  | 750 | 750 | SOUTH2001 | CHAMBERS | -0.00075703 | 0.0024465 | -0.56777 | 1.8349 |  | 20
CBY | CBY | 48582 | CB 2 |  |  | 522 | 750 | SOUTH2001 | CHAMBERS | -0.00072936 | 0.0023557 | -0.54702 | 1.7668 |  | 24
CBY | CBY | 48583 | CB 3 |  |  | 760 | 760 | SOUTH2001 | CHAMBERS | -0.00075646 | 0.0024569 | -0.57491 | 1.8673 |  | 24
CHS | CHS | 48590 | CHM1 |  |  | 59 | 0 | SOUTH2001 | HARRIS | -0.00092084 | 0.0029326 | 0 | 0 | 3 | 13.8
CHL | CHL | 48601 | CHN1 |  |  | 14.8 | 1.9073e-07 | SOUTH2001 | HARRIS | -0.00063272 | 0.0020298 | -1.2068e-10 | 3.8715e-10 | 4 | 13.8
CHL | CHL | 48602 | CHN2 |  |  | 14.8 | 1.9073e-07 | SOUTH2001 | HARRIS | -0.00063272 | 0.0020298 | -1.2068e-10 | 3.8715e-10 | 4 | 13.8
DIB | DIB | 48611 | DIB1 |  |  | 68.033 | 0.00036913 | SOUTH2001 | HARRIS | -0.00068749 | 0.002211 | -2.5378e-07 | 8.1615e-07 | 5 | 13.8
DIB | DIB | 48612 | DIB2 |  |  | 68.033 | 0.00036913 | SOUTH2001 | HARRIS | -0.00068749 | 0.002211 | -2.5378e-07 | 8.1615e-07 | 5 | 13.8
DIB | DIB | 48613 | DIB3 |  |  | 47.435 | 0.00025737 | SOUTH2001 | HARRIS | -0.00068749 | 0.002211 | -1.7694e-07 | 5.6905e-07 | 5 | 13.8
DOW | DOW | 48621 | DOW1 |  |  | 743.048 | 278.748 | SOUTH2001 | BRAZORIA | 0.0023985 | -0.007713 | 0.66858 | -2.15 | 19 | 14.4
DOW | DOW | 48622 | DOW2 |  |  | 507.552 | 43.252 | SOUTH2001 | BRAZORIA | 0.0023985 | -0.007713 | 0.10374 | -0.3336 | 18 | 14.4
DPW | DPW | 48630 | DPW7 |  |  | 170.234 | 174 | SOUTH2001 | HARRIS | -0.00062015 | 0.0019908 | -0.10791 | 0.3464 |  | 20
_EP | _EP | 48651 | EP1 |  |  | 5 | 0 | SOUTH2001 | CHAMBERS | -0.00079208 | 0.0025443 | 0 | 0 | 6 | 12.47
EXN | EXN | 48660 | EXN7 |  |  | 138.452 | -1.2456e-06 | SOUTH2001 | HARRIS | -0.00073298 | 0.0023563 | 9.1303e-10 | -2.9351e-09 | 7 | 13.8
EXN | EXN | 48661 | EXXON1 |  |  | 100.374 | -9.0306e-07 | SOUTH2001 | HARRIS | -0.00073298 | 0.0023563 | 6.6192e-10 | -2.1279e-09 | 7 | 13.8
EXN | EXN | 48662 | EXXON2 |  |  | 100.374 | -9.0306e-07 | SOUTH2001 | HARRIS | -0.00073298 | 0.0023563 | 6.6192e-10 | -2.1279e-09 | 7 | 13.8
FTR | FTR | 48671 | FTR1 |  |  | 150 | 150 | SOUTH2001 | GRIMES | -0.0037855 | 0.017654 | -0.56782 | 2.6481 |  | 21
FTR | FTR | 48672 | FTR2 |  |  | 150 | 150 | SOUTH2001 | GRIMES | -0.0037855 | 0.017654 | -0.56782 | 2.6481 |  | 21
FTR | FTR | 48673 | FTR3 |  |  | 150 | 150 | SOUTH2001 | GRIMES | -0.0037855 | 0.017654 | -0.56782 | 2.6481 |  | 21
FTR | FTR | 48674 | FTR4 |  |  | 380 | 380 | SOUTH2001 | GRIMES | -0.0037855 | 0.017654 | -1.4385 | 6.7085 |  | 21
GBY | GBY | 48690 | GB 5 |  |  | 330.839 | 406 | SOUTH2001 | HARRIS | -0.00095356 | 0.0030704 | -0.38715 | 1.2466 |  | 24
GBY | GBY | 48691 | GB 73 74 |  |  | 108 | 108 | SOUTH2001 | HARRIS | -0.000894 | 0.0029066 | -0.096552 | 0.31391 |  | 13.8
GBY | GBY | 48692 | GB 81 82 |  |  | 118 | 118 | SOUTH2001 | HARRIS | -0.000894 | 0.0029066 | -0.10549 | 0.34297 |  | 13.8
GBY | GBY | 48693 | GB 83 84 |  |  | 128 | 128 | SOUTH2001 | HARRIS | -0.000894 | 0.0029066 | -0.11443 | 0.37204 |  | 13.8
HOC | HOC | 48701 | HOCG 1 2 |  |  | 10 | 26 | SOUTH2001 | HARRIS | -0.00027059 | 0.00081104 | -0.0070353 | 0.021087 |  | 13.2
HOC | HOC | 48702 | HOCG 3 4 |  |  | 10 | 26 | SOUTH2001 | HARRIS | -0.00027059 | 0.00081104 | -0.0070353 | 0.021087 |  | 13.2
HOC | HOC | 48703 | HOCG 5 6 |  |  | 10 | 26 | SOUTH2001 | HARRIS | -0.00027059 | 0.00081104 | -0.0070353 | 0.021087 |  | 13.2
LEG | LEG | 48721 | LIM1 |  |  | 766 | 766 | SOUTH2001 | LIMESTONE | -0.0070066 | 0.042985 | -5.367 | 32.9265 |  | 25
LEG | LEG | 48722 | LIM2 |  |  | 766 | 766 | SOUTH2001 | LIMESTONE | -0.0070066 | 0.042985 | -5.367 | 32.9265 |  | 25
MSN | MSN | 48730 | MNSN1 |  |  | 8.8 | 1.9073e-07 | SOUTH2001 | BRAZORIA | 0.0006405 | -0.0020697 | 1.2217e-10 | -3.9475e-10 | 20 | 13.8
PSG | PSG | 48740 | PAS2ST |  |  | 166 | 166 | SOUTH2001 | HARRIS | -0.00067984 | 0.0021898 | -0.11285 | 0.3635 |  | 18
PSG | PSG | 48741 | PAS2GT1 |  |  | 179.55 | 180 | SOUTH2001 | HARRIS | -0.00067984 | 0.0021898 | -0.12237 | 0.39416 |  | 18
PSG | PSG | 48742 | PAS2GT2 |  |  | 179.55 | 180 | SOUTH2001 | HARRIS | -0.00067984 | 0.0021898 | -0.12237 | 0.39416 |  | 18
_PR | _PR | 48761 | PET1 |  |  | 24 | 0 | SOUTH2001 | HARRIS | -0.00063117 | 0.002025 | 0 | 0 | 13 | 13.8
PHR | PHR | 48771 | PHR1 |  |  | 461 | 461 | SOUTH2001 | GALVESTON | -0.00057387 | 0.0018397 | -0.26455 | 0.84809 |  | 19
PHR | PHR | 48772 | PHR2 |  |  | 453.634 | 461 | SOUTH2001 | GALVESTON | -0.00057387 | 0.0018397 | -0.26455 | 0.84809 |  | 22
PHR | PHR | 48773 | PHR3 |  |  | 529.759 | 552 | SOUTH2001 | GALVESTON | 0 | 0 | 0 | 0 |  | 22
PHR | PHR | 48774 | PHR4 |  |  | 713.901 | 739 | SOUTH2001 | GALVESTON | 0.00010286 | -0.00032331 | 0.076014 | -0.23892 |  | 20
PSA | PSA | 48791 | PWR1 |  |  | 56.6 | 48.3788 | SOUTH2001 | HARRIS | -0.00087467 | 0.0028093 | -0.042316 | 0.13591 | 9 | 13.8
PSA | PSA | 48792 | PWR2 |  |  | 56.6 | 48.3788 | SOUTH2001 | HARRIS | -0.00087467 | 0.0028093 | -0.042316 | 0.13591 | 9 | 13.8
PSA | PSA | 48793 | PWR3 |  |  | 56.6 | 48.3788 | SOUTH2001 | HARRIS | -0.00087467 | 0.0028093 | -0.042316 | 0.13591 | 9 | 13.8
PSA | PSA | 48794 | PWR4 |  |  | 56.6 | 48.3788 | SOUTH2001 | HARRIS | -0.00087467 | 0.0028093 | -0.042316 | 0.13591 | 9 | 13.8
PSA | PSA | 48795 | PWR5 |  |  | 56.6 | 48.3788 | SOUTH2001 | HARRIS | -0.00087467 | 0.0028093 | -0.042316 | 0.13591 | 9 | 13.8
PSA | PSA | 48796 | PWR6 |  |  | 69 | 58.9777 | SOUTH2001 | HARRIS | -0.00087467 | 0.0028093 | -0.051586 | 0.16568 | 9 | 13.8
PSA | PSA | 48797 | PWR8 |  |  | 48 | 41.028 | SOUTH2001 | HARRIS | -0.00087467 | 0.0028093 | -0.035886 | 0.11526 | 9 | 13.8
QNM | QNM | 48810 | QNM1 |  |  | 3.3 | -4.7684e-08 | SOUTH2001 | HARRIS | -0.00070667 | 0.0022794 | 3.3697e-11 | -1.0869e-10 | 10 | 12.47
|  | 48815 | SHLDN 5 |  |  | 152.5 | 98.8 | SOUTH2001 | HARRIS | -0.00087792 | 0.0028256 | -0.086739 | 0.27917 | 21 | 16
_SL | _SL | 48820 | SHELL_ |  |  | 80.007 | 3.4935e-06 | SOUTH2001 | HARRIS | -0.00068972 | 0.0022224 | -2.4095e-09 | 7.764e-09 | 11 | 13.8
_SL | _SL | 48821 | SHELL_ |  |  | 80.007 | 3.4935e-06 | SOUTH2001 | HARRIS | -0.00068972 | 0.0022224 | -2.4095e-09 | 7.764e-09 | 11 | 13.8
_SL | _SL | 48822 | SHL_CPS |  |  | 32.186 | 1.4054e-06 | SOUTH2001 | HARRIS | -0.00068972 | 0.0022224 | -9.6932e-10 | 3.1234e-09 | 11 | 12.5
SIM | SIM | 48831 | SIM1 |  |  | 7 | 0 | SOUTH2001 | HARRIS | -0.00062362 | 0.0020022 | 0 | 0 | 12 | 13.8
SIM | SIM | 48832 | SIM2 |  |  | 7 | 0 | SOUTH2001 | HARRIS | -0.00062362 | 0.0020022 | 0 | 0 | 12 | 13.8
SJS | SJS | 48841 | SJSES_1 |  |  | 81 | 81 | SOUTH2001 | HARRIS | -0.00065635 | 0.0021093 | -0.053165 | 0.17085 |  | 13.8
SJS | SJS | 48842 | SJSES_2 |  |  | 81 | 81 | SOUTH2001 | HARRIS | -0.00065635 | 0.0021093 | -0.053165 | 0.17085 |  | 13.8
SRB | SRB | 48851 | SRB1 |  |  | 163.902 | 174 | SOUTH2001 | HARRIS | -0.00066491 | 0.0021381 | -0.11569 | 0.37203 |  | 20
SRB | SRB | 48852 | SRB2 |  |  | 174 | 174 | SOUTH2001 | HARRIS | -0.00066279 | 0.0021311 | -0.11533 | 0.37081 |  | 20
SRB | SRB | 48853 | SRB3 |  |  | 171.759 | 230 | SOUTH2001 | HARRIS | -0.00067135 | 0.0021591 | -0.15441 | 0.49659 |  | 16.5
SRB | SRB | 48854 | SRB4 |  |  | 230 | 230 | SOUTH2001 | HARRIS | -0.0007008 | 0.0022538 | -0.16118 | 0.51838 |  | 16.5
SRB | SRB | 48855 | SRB21 |  | 23 |  |  | SOUTH2001 | HARRIS | -0.00066141 | 0.0021266 | -0.015212 | 0.048911 |  | 13.2
SRB | SRB | 48856 | SRB22 |  | 13 |  |  | SOUTH2001 | HARRIS | -0.00066279 | 0.0021311 | -0.0086163 | 0.027704 |  | 13.2
THW | THW | 48872 | THW2 |  |  | 183.388 | 229 | SOUTH2001 | HARRIS | -0.0012263 | 0.0035682 | -0.28081 | 0.81711 |  | 20
THW | THW | 48873 | THW3 |  |  | 104 | 104 | SOUTH2001 | HARRIS | -0.00082157 | 0.0023261 | -0.085444 | 0.24191 |  | 13.8
THW | THW | 48874 | THW4 |  |  | 104 | 104 | SOUTH2001 | HARRIS | -0.00082157 | 0.0023261 | -0.085444 | 0.24191 |  | 13.8
THW | THW | 48875 | THW3 1 2 |  |  | 114 | 114 | SOUTH2001 | HARRIS | -0.00082157 | 0.0023261 | -0.093659 | 0.26517 |  | 13.8
THW | THW | 48877 | THW3 3 4 |  |  | 114 | 114 | SOUTH2001 | HARRIS | -0.00082157 | 0.0023261 | -0.093659 | 0.26517 |  | 13.8
THW | THW | 48879 | THW4 1 2 |  |  | 114 | 114 | SOUTH2001 | HARRIS | -0.00082157 | 0.0023261 | -0.093659 | 0.26517 |  | 13.8
THW | THW | 48881 | THW4 3 4 |  |  | 114 | 114 | SOUTH2001 | HARRIS | -0.00082157 | 0.0023261 | -0.093659 | 0.26517 |  | 13.8
THW | THW | 48883 | THW21 |  | 13 |  |  | SOUTH2001 | HARRIS | -0.0010135 | 0.0029583 | -0.013175 | 0.038458 |  | 13.2
THW | THW | 48885 | THW5 1 2 |  |  | 116 | 116 | SOUTH2001 | HARRIS | -0.0011173 | 0.0030571 | -0.12961 | 0.35463 |  | 13.8
THW | THW | 48886 | THW5 3 4 |  |  | 116 | 116 | SOUTH2001 | HARRIS | -0.0011173 | 0.0030571 | -0.12961 | 0.35463 |  | 13.8
THW | THW | 48887 | THW5 5 6 |  |  | 116 | 116 | SOUTH2001 | HARRIS | -0.0011173 | 0.0030571 | -0.12961 | 0.35463 |  | 13.8
TID | TID | 48901 | TID1 |  |  | 36.406 | -1.1732e-06 | SOUTH2001 | HARRIS | -0.00069098 | 0.002224 | 8.1066e-10 | -2.6092e-09 | 14 | 13.8
TID | TID | 48902 | TID2 |  |  | 58.294 | -1.8786e-06 | SOUTH2001 | HARRIS | -0.00069098 | 0.002224 | 1.298e-09 | -4.1779e-09 | 14 | 13.8
TGF | TGF | 48911 | TXG1 |  | 69.2 |  |  | SOUTH2001 | WHARTON | 0.0033589 | -0.010387 | 0.23244 | -0.71879 |  | 13.8
TGF | TGF | 48912 | TXG2 |  | 12.5 |  |  | SOUTH2001 | WHARTON | 0.0033589 | -0.010387 | 0.041987 | -0.12984 |  | 11.5
WAP | WAP | 48921 | WAP1 |  |  | 133.085 | 174 | SOUTH2001 | FORT BEND | 0.0002121 | -0.00083875 | 0.036905 | -0.14594 |  | 20
WAP | WAP | 48922 | WAP2 |  |  | 174 | 174 | SOUTH2001 | FORT BEND | 0.0002121 | -0.00083875 | 0.036905 | -0.14594 |  | 20
WAP | WAP | 48923 | WAP3 |  |  | 250.173 | 278 | SOUTH2001 | FORT BEND | 0.0002121 | -0.00083875 | 0.058964 | -0.23317 |  | 24
WAP | WAP | 48924 | WAP4 |  |  | 517.86 | 552 | SOUTH2001 | FORT BEND | 0.0002121 | -0.00083875 | 0.11708 | -0.46299 |  | 22
WAP | WAP | 48925 | WAP5 |  |  | 700 | 700 | SOUTH2001 | FORT BEND | 0.0002121 | -0.00083875 | 0.14847 | -0.58712 |  | 20
WAP | WAP | 48926 | WAP6 |  |  | 700 | 700 | SOUTH2001 | FORT BEND | -0.00012686 | 0.00051407 | -0.088799 | 0.35985 |  | 20
WAP | WAP | 48927 | WAP7 |  |  | 597 | 597 | SOUTH2001 | FORT BEND | -0.00012686 | 0.00051407 | -0.075733 | 0.3069 |  | 20
WAP | WAP | 48928 | WAP8 |  |  | 595 | 595 | SOUTH2001 | FORT BEND | -0.00012686 | 0.00051407 | -0.075479 | 0.30587 |  | 20
WAP | WAP | 48929 | WAP21 |  | 13 |  |  | SOUTH2001 | FORT BEND | 0.0002121 | -0.00083875 | 0.0027573 | -0.010904 |  | 13.2
WEB | WEB | 48940 | WEB3 |  |  | 374 | 374 | SOUTH2001 | HARRIS | -0.00016857 | 0.00052922 | -0.063046 | 0.19793 |  | 18
WEB | WEB | 48941 | WEB21 |  | 13 |  |  | SOUTH2001 | HARRIS | -0.0002234 | 0.00070518 | -0.0029042 | 0.0091673 |  | 13.2
MORTNVLY | MORTNVLY | 270 | MORTNVLY | 0.44 |  |  |  | WEST2001 | EASTLAND | 0.18654 | -0.10963 | 0.082078 | -0.048237 |  | 69
GORMAN | GORMAN | 274 | GORMAN | 1.29 |  |  |  | WEST2001 | EASTLAND | 0.18654 | -0.10963 | 0.24064 | -0.14142 |  | 69
LNPLNTRD | LNPLNTRD | 275 | LNPLNTRD | 1.94 |  |  |  | WEST2001 | EASTLAND | 0.17772 | -0.10973 | 0.34478 | -0.21287 |  | 138
HGHWY101 | HGHWY101 | 276 | HGHWY101 | 2.53 |  |  |  | WEST2001 | EASTLAND | 0.18932 | -0.11052 | 0.47898 | -0.27961 |  | 138
EOLIANRD | EOLIANRD | 282 | EOLIANRD | 0.19 |  |  |  | WEST2001 | STEPHENS | 0.22792 | -0.11321 | 0.043305 | -0.02151 |  | 138
CARBON | CARBON | 286 | CARBON | 0.55 |  |  |  | WEST2001 | EASTLAND | 0.18654 | -0.10963 | 0.1026 | -0.060296 |  | 69
|  | 310 | IVAN | 0.28 |  |  |  | WEST2001 | STEPHENS | 0.22496 | -0.11405 | 0.062989 | -0.031933 |  | 69
|  | 719 | WFEC 12G |  |  | 40 | 40 | WEST2001 | WICHITA | 0.2305 | -0.1155 | 9.2201 | -4.6201 |  | 13.8
|  | 720 | WFEC 34G |  | 20 | 20 | 20 | WEST2001 | WICHITA | 0.2305 | -0.1155 | 9.2201 | -4.6201 |  | 13.8
|  | 721 | WICHSUTH |  |  |  |  | WEST2001 | WICHITA | 0.2305 | -0.1155 | 0 | 0 |  | 138
SMS_SW_9 | SMS SW 9 | 724 | SMS SW |  |  |  |  | WEST2001 | STONEWALL | 0.27221 | -0.11177 | 0 | 0 |  | 69
BRYSON | BRYSON | 732 | BRYSON |  |  |  |  | WEST2001 | JACK | 0.22191 | -0.11473 | 0 | 0 |  | 69
PADUCAR2 | PADUCAR2 | 733 | PADUCAR2 | 1.15 |  |  |  | WEST2001 | COTTLE | 0.26131 | -0.11232 | 0.30051 | -0.12916 |  | 69
MCADMSR2 | MCADMSR2 | 734 | MCADMSR2 | 0.88 |  |  |  | WEST2001 | FOARD | 0.25904 | -0.11249 | 0.22795 | -0.098988 |  | 69
LIBERTR2 | LIBERTR2 | 736 | LIBERTR2 | 1.6 |  |  |  | WEST2001 | HARDEMAN | 0.2567 | -0.11283 | 0.41072 | -0.18053 |  | 69
SMS | SMS | 737 | SMS9 | 0.71 |  |  |  | WEST2001 | KENT | 0.27221 | -0.11177 | 0.19327 | -0.079356 |  | 69
CHILDRES | CHILDRES | 739 | CHILDRES | 1.08 |  |  |  | WEST2001 | CHILDRESS | 0.25889 | -0.11257 | 0.2796 | -0.12157 |  | 69
SCK | SCK | 743 | SALTCK4 | 34.14 |  |  |  | WEST2001 | KENT | 0.27812 | -0.11171 | 9.4951 | -3.8137 |  | 138
KNG | KNG | 745 | KING9 | 6.65 |  |  |  | WEST2001 | KING | 0.26767 | -0.11172 | 1.78 | -0.74291 |  | 69
KAL | KAL | 747 | KALGRY9 | 2.93 |  |  |  | WEST2001 | CROSBY | 0.27221 | -0.11177 | 0.79757 | -0.32748 |  | 69
JAYTON9 | JAYTON9 | 748 | JAYTON9 | 0.93 |  |  |  | WEST2001 | KENT | 0.27035 | -0.11166 | 0.25142 | -0.10384 |  | 69
GLENN | GLENN | 749 | GLENN | 1.47 |  |  |  | WEST2001 | DICKENS | 0.26914 | -0.11192 | 0.39564 | -0.16453 |  | 69
ESPULA9 | ESPULA9 | 751 | ESPULA9 | 1.62 |  |  |  | WEST2001 | DICKENS | 0.27121 | -0.11182 | 0.43937 | -0.18115 |  | 69
CLARMNT | CLARMNT | 752 | CLARMNT | 0.23 |  |  |  | WEST2001 | KENT | 0.27038 | -0.11154 | 0.062188 | -0.025655 |  | 69
BIS | BIS | 753 | BISSET9 | 1.64 |  |  |  | WEST2001 | KING | 0.26767 | -0.11172 | 0.43898 | -0.18321 |  | 69
ASPERM9 | ASPERM9 | 755 | ASPERM9 | 2.29 |  |  |  | WEST2001 | STONEWALL | 0.26767 | -0.11172 | 0.61297 | -0.25583 |  | 69
BUSHKNOB | BUSHKNOB | 757 | BUSHKNOB | 1.99 |  |  |  | WEST2001 | THROCKMORTON | 0.24945 | -0.11101 | 0.4964 | -0.22091 |  | 69
MORAN | MORAN | 759 | MORAN | 0.87 |  |  |  | WEST2001 | BOSQUE | 0.23463 | -0.10964 | 0.20413 | -0.095386 |  | 69
ALBANY1 | ALBANY1 | 760 | ALBANY | 1.05 |  |  |  | WEST2001 | SHACKLEFORD | 0.24547 | -0.11016 | 0.25774 | -0.11566 |  | 69
TRUSCOTT | TRUSCOTT | 761 | TRUSCOTT | 0.37 |  |  |  | WEST2001 | KNOX | 0.25672 | -0.11247 | 0.094986 | -0.041615 |  | 69
ROCHSTER | ROCHSTER | 763 | ROCHSTER | 2.56 |  |  |  | WEST2001 | HASKELL | 0.25997 | -0.11205 | 0.66553 | -0.28686 |  | 69
MUNDAYR2 | MUNDAYR2 | 764 | MUNDAYR2 | 2.66 |  |  |  | WEST2001 | KNOX | 0.25617 | -0.11225 | 0.68141 | -0.2986 |  | 69
KNOX9 | KNOX9 | 765 | KNOX9 | 3.17 |  |  |  | WEST2001 | HASKELL | 0.25875 | -0.11212 | 0.82024 | -0.35541 |  | 69
HENRIETA | HENRIETA | 767 | HENRIETA | 0.55 |  |  |  | WEST2001 | CLAY | 0.17517 | -0.11715 | 0.096343 | -0.064433 |  | 69
JOY | JOY | 768 | JOY | 3.37 |  |  |  | WEST2001 | CLAY | 0.14254 | -0.11789 | 0.48037 | -0.3973 |  | 69
POSTOKSW | POSTOKSW | 769 | POSTOKSW |  |  |  |  | WEST2001 | CLAY | 0.15061 | -0.11756 | 0 | 0 |  | 69
AROWHEAD | AROWHEAD | 770 | AROWHEAD | 2.32 |  |  |  | WEST2001 | ARCHER | 0.2253 | -0.11565 | 0.5227 | -0.26831 |  | 138
POSTOAK | POSTOAK | 771 | POSTOAK | 1.96 |  |  |  | WEST2001 | JACK | 0.15061 | -0.11756 | 0.29519 | -0.23041 |  | 69
SHANNON | SHANNON | 772 | SHANNON | 2.86 |  |  |  | WEST2001 | CLAY | 0.15984 | -0.11717 | 0.45713 | -0.3351 |  | 69
SCL | SCL | 773 | SCOTLAND | 4.75 |  |  |  | WEST2001 | ARCHER | 0.23046 | -0.1154 | 1.0947 | -0.54815 |  | 138
KATZP | KATZP | 774 | KATZP | 3.17 |  |  |  | WEST2001 | KING | 0.25875 | -0.11212 | 0.82024 | -0.35541 |  | 69
LANHAM | LANHAM | 775 | LANHAM | 2.28 |  |  |  | WEST2001 | CLAY | 0.18603 | -0.11682 | 0.42415 | -0.26634 |  | 69
BRIDWELL | BRIDWELL | 776 | BRIDWELL | 1.1 |  |  |  | WEST2001 | ARCHER | 0.17273 | -0.11663 | 0.19 | -0.12829 |  | 69
GOREE | GOREE | 777 | GOREE | 0.64 |  |  |  | WEST2001 | KNOX | 0.25542 | -0.11229 | 0.16347 | -0.071868 |  | 69
GILESPIE | GILESPIE | 778 | GILESPIE | 1.95 |  |  |  | WEST2001 | KNOX | 0.25781 | -0.11217 | 0.50272 | -0.21873 |  | 69
SMR | SMR | 779 | SEYMOUR | 11.58 |  |  |  | WEST2001 | BAYLOR | 0.23362 | -0.11391 | 2.7054 | -1.3191 |  | 69
ELBERT | ELBERT | 780 | ELBERT | 0.56 |  |  |  | WEST2001 | THROCKMORTON | 0.20998 | -0.11503 | 0.11759 | -0.064418 |  | 69
ELBERTSW | ELBERTSW | 781 | ELBERTSW |  |  |  |  | WEST2001 | YOUNG | 0.20998 | -0.11503 | 0 | 0 |  | 69
LKKEMPSW | LKKEMPSW | 782 | LKKEMPSW |  |  |  |  | WEST2001 | BAYLOR | 0.22676 | -0.11424 | 0 | 0 |  | 69
LAKEKEMP | LAKEKEMP | 783 | LAKEKEMP | 1.27 |  |  |  | WEST2001 | BAYLOR | 0.22676 | -0.11424 | 0.28798 | -0.14508 |  | 69
WESTOVER | WESTOVER | 784 | WESTOVER | 0.79 |  |  |  | WEST2001 | BAYLOR | 0.22016 | -0.11455 | 0.17392 | -0.090495 |  | 69
BOMARTON | BOMARTON | 786 | BOMARTON | 0.42 |  |  |  | WEST2001 | BAYLOR | 0.24441 | -0.11311 | 0.10265 | -0.047507 |  | 69
OLN | OLN | 787 | OLNEY |  |  |  |  | WEST2001 | YOUNG | 0.23243 | -0.11504 | 0 | 0 |  | 138
OLN | OLN | 788 | OLNEY | 9.2 |  |  |  | WEST2001 | YOUNG | 0.2028 | -0.11537 | 1.8657 | -1.0614 |  | 69
SEYMORMP | SEYMORMP | 789 | SEYMORMP | 1.07 |  |  |  | WEST2001 | BAYLOR | 0.23363 | -0.11391 | 0.24998 | -0.12189 |  | 69
BENJAMIN | BENJAMIN | 790 | BENJAMIN | 0.43 |  |  |  | WEST2001 | KNOX | 0.25612 | -0.11239 | 0.11013 | -0.048328 |  | 69
JEAN | JEAN | 791 | JEAN | 2.97 |  |  |  | WEST2001 | YOUNG | 0.1769 | -0.11544 | 0.5254 | -0.34286 |  | 69
MURRAY | MURRAY | 792 | MURRAY | 1.63 |  |  |  | WEST2001 | YOUNG | 0.25595 | -0.11374 | 0.4172 | -0.1854 |  | 138
JACKSBRO | JACKSBRO | 794 | JACKSBRO | 0.34 |  |  |  | WEST2001 | YOUNG | 0.22809 | -0.11479 | 0.07755 | -0.039029 |  | 138
STHBNDSW | STHBNDSW | 795 | STHBNDSW |  |  |  |  | WEST2001 | YOUNG | 0.15855 | -0.11549 | 0 | 0 |  | 69
SOTHBEND | SOTHBEND | 796 | SOTHBEND | 1.94 |  |  |  | WEST2001 | YOUNG | 0.15855 | -0.11549 | 0.30759 | -0.22405 |  | 69
MARKLEY | MARKLEY | 797 | MARKLEY | 0.77 |  |  |  | WEST2001 | YOUNG | 0.23784 | -0.1151 | 0.18313 | -0.088626 |  | 138
|  | 856 | BTU3783 | 9.63 |  |  |  | WEST2001 | YOUNG | 0.22778 | -0.11496 | 2.1935 | -1.107 |  | 69
PBSES | PBSES | 1002 | PBCT A G |  |  | 70 | 73 | WEST2001 | WARD | 0.28605 | -0.11047 | 20.8818 | -8.0643 |  | 13.8
PBSES | PBSES | 1003 | PBCT B G |  |  | 68 | 73 | WEST2001 | WARD | 0.28605 | -0.11047 | 20.8818 | -8.0643 |  | 13.8
PBSES | PBSES | 1004 | PBCT C G |  |  | 71 | 73 | WEST2001 | WARD | 0.28605 | -0.11047 | 20.8818 | -8.0643 |  | 13.8
PBSES | PBSES | 1005 | PBCT D G |  |  | 71 | 73 | WEST2001 | WARD | 0.28605 | -0.11047 | 20.8818 | -8.0643 |  | 13.8
PBSES | PBSES | 1006 | PBCT E G |  |  | 72 | 73 | WEST2001 | WARD | 0.28605 | -0.11047 | 20.8818 | -8.0643 |  | 13.8
PBSES | PBSES | 1007 | PB5 G |  |  | 101 | 117 | WEST2001 | WARD | 0.28605 | -0.11047 | 33.4681 | -12.925 |  | 13.8
PBSES | PBSES | 1008 | PB6 G |  |  | 507 | 543 | WEST2001 | WARD | 0.28605 | -0.11047 | 155.3262 | -59.9852 |  | 18
PBSES | PBSES | 1010 | PERMIANB |  |  |  |  | WEST2001 | WARD | 0.28605 | -0.11047 | 0 | 0 |  | 138
PBSES | PBSES | 1015 | PERMIANB |  |  |  |  | WEST2001 | WARD | 0.28563 | -0.11037 | 0 | 0 |  | 69
MOSSW | MOSSW | 1018 | MOSS |  |  |  |  | WEST2001 | ECTOR | 0.28958 | -0.1113 | 0 | 0 |  | 345
MOSSW | MOSSW | 1019 | MOSS |  |  |  |  | WEST2001 | ECTOR | 0.28833 | -0.11102 | 0 | 0 |  | 138
ODEHV | ODEHV | 1020 | EHV TIET |  |  |  |  | WEST2001 | ECTOR | 0.28973 | -0.11132 | 0 | 0 |  | 345
MDLNE | MDLNE | 1021 | MIDL E T |  |  |  |  | WEST2001 | MIDLAND | 0.29022 | -0.11146 | 0 | 0 |  | 345
MDLNE | MDLNE | 1022 | MIDLND E |  |  |  |  | WEST2001 | MIDLAND | 0.29022 | -0.11146 | 0 | 0 |  | 345
MDLNE | MDLNE | 1023 | MIDLND E | 37.075 |  |  |  | WEST2001 | MIDLAND | 0.28879 | -0.11121 | 10.7068 | -4.123 |  | 138
FLCNS | FLCNS | 1024 | FS COGEN |  |  |  |  | WEST2001 | HOWARD | 0.29192 | -0.11182 | 0 | 0 |  | 138
FLCNS | FLCNS | 1025 | FS COGEN |  |  |  |  | WEST2001 | HOWARD | 0.29192 | -0.11182 | 0 | 0 |  | 345
ODEHV | ODEHV | 1026 | ODES EHV |  |  |  |  | WEST2001 | ECTOR | 0.28974 | -0.11132 | 0 | 0 |  | 345
ODEHV | ODEHV | 1027 | ODES EHV |  |  |  |  | WEST2001 | ECTOR | 0.28821 | -0.11098 | 0 | 0 |  | 138
ODEHV | ODEHV | 1028 | ODEHV 1T |  |  |  |  | WEST2001 | ECTOR | 0.28974 | -0.11133 | 0 | 0 |  | 345
ODEHV | ODEHV | 1029 | ODEHV 2T |  |  |  |  | WEST2001 | ECTOR | 0.28973 | -0.11132 | 0 | 0 |  | 345
MGSES | MGSES | 1030 | MRGN CRK |  |  |  |  | WEST2001 | MITCHELL | 0.29319 | -0.11209 | 0 | 0 |  | 345
MGSES | MGSES | 1031 | MRGN 6 G |  |  | 477 | 514 | WEST2001 | MITCHELL | 0.29319 | -0.11209 | 150.6988 | -57.6122 |  | 22
MGSES | MGSES | 1032 | MRGN CRK |  |  |  |  | WEST2001 | MITCHELL | 0.28853 | -0.11175 | 0 | 0 |  | 138
MGSES | MGSES | 1033 | MRGN CRK |  |  |  |  | WEST2001 | MITCHELL | 0.28666 | -0.11158 | 0 | 0 |  | 69
MGSES | MGSES | 1034 | MCTMODEL |  |  |  |  | WEST2001 | MITCHELL | 0.28677 | -0.11159 | 0 | 0 |  | 69
MGSES | MGSES | 1035 | MORGAN2G |  |  | 20 | 22 | WEST2001 | MITCHELL | 0.28853 | -0.11175 | 6.3477 | -2.4585 |  | 13.2
MGSES | MGSES | 1036 | MORGAN4G |  |  | 63 | 77 | WEST2001 | MITCHELL | 0.28853 | -0.11175 | 22.217 | -8.6048 |  | 13.8
MGSES | MGSES | 1037 | MORGAN5G |  |  | 168 | 182 | WEST2001 | MITCHELL | 0.28853 | -0.11175 | 52.5129 | -20.3386 |  | 20
MGSES | MGSES | 1038 | MORGAN3G |  |  | 37 | 46 | WEST2001 | MITCHELL | 0.28677 | -0.11159 | 13.1916 | -5.1333 |  | 13.2
MGSES | MGSES | 1039 | MRGN A G |  |  | 70 | 74 | WEST2001 | MITCHELL | 0.28853 | -0.11175 | 21.3514 | -8.2695 |  | 13.8
MGSES | MGSES | 1040 | MRGN B G |  |  | 70 | 74 | WEST2001 | MITCHELL | 0.28853 | -0.11175 | 21.3514 | -8.2695 |  | 13.8
MGSES | MGSES | 1041 | MRGN C G |  |  | 70 | 74 | WEST2001 | MITCHELL | 0.28853 | -0.11175 | 21.3514 | -8.2695 |  | 13.8
MGSES | MGSES | 1042 | MRGN D G |  |  | 70 | 74 | WEST2001 | MITCHELL | 0.28853 | -0.11175 | 21.3514 | -8.2695 |  | 13.8
MGSES | MGSES | 1043 | MRGN E G |  | 74 |  |  | WEST2001 | MITCHELL | 0.28853 | -0.11175 | 21.3514 | -8.2695 |  | 13.8
MGSES | MGSES | 1044 | MRGN F G |  | 74 |  |  | WEST2001 | MITCHELL | 0.28853 | -0.11175 | 21.3514 | -8.2695 |  | 13.8
FLCNS | FLCNS | 1045 | CALENG1G |  |  | 70 | 70 | WEST2001 | HOWARD | 0.29192 | -0.11182 | 20.4345 | -7.8273 |  | 13.8
FLCNS | FLCNS | 1046 | CALENG2G |  |  | 70 | 70 | WEST2001 | HOWARD | 0.29192 | -0.11182 | 20.4345 | -7.8273 |  | 13.8
FLCNS | FLCNS | 1047 | CALENG3G |  |  | 60 | 60 | WEST2001 | HOWARD | 0.29192 | -0.11182 | 17.5153 | -6.7091 |  | 13.8
HNTMN | HNTMN | 1051 | HUNTSMAN | 7.626 |  |  |  | WEST2001 | ECTOR | 0.28817 | -0.11097 | 2.1976 | -0.84623 |  | 138
RXALL | RXALL | 1052 | REXALL | 37.634 |  |  |  | WEST2001 | ECTOR | 0.28813 | -0.11096 | 10.8436 | -4.1758 |  | 138
GNTSW | GNTSW | 1053 | GEN RUBR | 6.566 |  |  |  | WEST2001 | ECTOR | 0.28812 | -0.11095 | 1.8918 | -0.72853 |  | 138
OLFSW | OLFSW | 1054 | OLFN/SHL | 33.783 |  |  |  | WEST2001 | ECTOR | 0.28813 | -0.11096 | 9.7339 | -3.7485 |  | 138
NYLNT | NYLNT | 1055 | NYLON T |  |  |  |  | WEST2001 | ECTOR | 0.28814 | -0.11096 | 0 | 0 |  | 138
NYLSW | NYLSW | 1056 | NYLON |  |  |  |  | WEST2001 | ECTOR | 0.28814 | -0.11096 | 0 | 0 |  | 138
MDASW | MDASW | 1059 | MIDESSA |  |  |  |  | WEST2001 | MIDLAND | 0.28845 | -0.11109 | 0 | 0 |  | 138
SUNSW | SUNSW | 1064 | SUN | 16.057 |  |  |  | WEST2001 | SCURRY | 0.28487 | -0.11166 | 4.5742 | -1.793 |  | 138
WINK | WINK_ | 1074 | WINK SS |  |  |  |  | WEST2001 | WINKLER | 0.28609 | -0.1105 | 0 | 0 |  | 138
WINK | WINK_ | 1075 | WINK SS | 5.439 |  |  |  | WEST2001 | WINKLER | 0.28603 | -0.11048 | 1.5557 | -0.6009 |  | 69
HSACH | HSACH | 1087 | WRDGLF T |  |  |  |  | WEST2001 | WARD | 0.28605 | -0.11047 | 0 | 0 |  | 138
WICKT | WICKT | 1088 | WICKETT |  |  |  |  | WEST2001 | WARD | 0.28605 | -0.11047 | 0 | 0 |  | 138
WCKTP | WCKTP | 1089 | WICKET T |  |  |  |  | WEST2001 | WARD | 0.28605 | -0.11047 | 0 | 0 |  | 138
WGLFT | WGLFT | 1091 | WARDGULF | 12.632 |  |  |  | WEST2001 | WARD | 0.28605 | -0.11047 | 3.6134 | -1.3955 |  | 138
LOVNG | LOVNG | 1092 | LOVING | 2.133 |  |  |  | WEST2001 | LOVING | 0.28609 | -0.1105 | 0.61024 | -0.2357 |  | 138
ELMAR | ELMAR | 1093 | EL MAR | 5.227 |  |  |  | WEST2001 | LOVING | 0.28609 | -0.1105 | 1.4954 | -0.57759 |  | 138
MASON | MASON | 1094 | MASON | 3.398 |  |  |  | WEST2001 | REEVES | 0.28609 | -0.1105 | 0.97215 | -0.37548 |  | 138
SBEAN | SBEAN | 1095 | SCRWBEAN | 1.622 |  |  |  | WEST2001 | CULBERSON | 0.28609 | -0.1105 | 0.46404 | -0.17923 |  | 138
BLKRV | BLKRV | 1096 | BLACKRVR | 3.401 |  |  |  | WEST2001 | CULBERSON | 0.28609 | -0.1105 | 0.97301 | -0.37581 |  | 138
|  | 1097 | TWPP MTR |  |  |  |  | WEST2001 | CULBERSON | 0.28609 | -0.1105 | 0 | 0 |  | 138
CWIND | CWIND | 1098 | KWIND RO | 0.706 |  |  |  | WEST2001 | CULBERSON | 0.28609 | -0.1105 | 0.20198 | -0.078014 |  | 138
SPRTP | SPRTP | 1099 | SWPORT T |  |  |  |  | WEST2001 | ECTOR | 0.28739 | -0.11078 | 0 | 0 |  | 138
SWPRT | SWPRT | 1100 | SW PORTL | 10.691 |  |  |  | WEST2001 | ECTOR | 0.28739 | -0.11078 | 3.0725 | -1.1844 |  | 138
EDWDS | EDWDS | 1101 | EDWARDS | 10.898 |  |  |  | WEST2001 | CRANE | 0.28739 | -0.11078 | 3.132 | -1.2073 |  | 138
JDKNS | JDKNS | 1102 | JUDKINS | 7.961 |  |  |  | WEST2001 | ECTOR | 0.2872 | -0.11074 | 2.2864 | -0.8816 |  | 138
SNDHT | SNDHT | 1103 | SANDHL T |  |  |  |  | WEST2001 | ECTOR | 0.28688 | -0.11066 | 0 | 0 |  | 138
SNDHL | SNDHL | 1104 | SANDHILL | 7.511 |  |  |  | WEST2001 | CRANE | 0.28688 | -0.11066 | 2.1548 | -0.8312 |  | 138
MONT1 | MONT1 | 1105 | MONAH 1T |  |  |  |  | WEST2001 | WARD | 0.28606 | -0.11047 | 0 | 0 |  | 138
MNHNS | MNHNS | 1106 | MONAHN 1 | 13.105 |  |  |  | WEST2001 | WARD | 0.28606 | -0.11047 | 3.7488 | -1.4477 |  | 138
MONT2 | MONT2 | 1107 | MONAH 2T |  |  |  |  | WEST2001 | WARD | 0.28624 | -0.11051 | 0 | 0 |  | 138
MNHNS | MNHNS | 1108 | MONAHN 2 | 7.933 |  |  |  | WEST2001 | WARD | 0.28624 | -0.11051 | 2.2707 | -0.8767 |  | 138
BTHOT | BTHOT | 1111 | BIG3OD T |  |  |  |  | WEST2001 | ECTOR | 0.28825 | -0.11099 | 0 | 0 |  | 138
BTHOD | BTHOD | 1112 | BIG 3 OD | 1.049 |  |  |  | WEST2001 | ECTOR | 0.28825 | -0.11099 | 0.30237 | -0.11643 |  | 138
ODESW | ODESW | 1113 | ODESA SW | 11.17 |  |  |  | WEST2001 | ECTOR | 0.28827 | -0.111 | 3.22 | -1.2399 |  | 138
WNDWD | WNDWD | 1116 | WINDWOOD | 30.576 |  |  |  | WEST2001 | MIDLAND | 0.28872 | -0.11118 | 8.828 | -3.3996 |  | 138
MDLNW | MDLNW | 1117 | MIDLND W | 97.966 |  |  |  | WEST2001 | MIDLAND | 0.28859 | -0.11114 | 28.2724 | -10.8882 |  | 138
CRM8T | CRM8T | 1118 | CRMWD8 T |  |  |  |  | WEST2001 | MIDLAND | 0.28836 | -0.11105 | 0 | 0 |  | 138
CRMW8 | CRMW8 | 1119 | CRMWD-8 | 1.122 |  |  |  | WEST2001 | MIDLAND | 0.28836 | -0.11105 | 0.32354 | -0.1246 |  | 138
MDAIR | MDAIR | 1120 | MID AIRP | 14.977 |  |  |  | WEST2001 | MIDLAND | 0.28837 | -0.11105 | 4.3189 | -1.6633 |  | 138
GLNHV | GLNHV | 1121 | GLENHAVN | 67.323 |  |  |  | WEST2001 | ECTOR | 0.28829 | -0.11102 | 19.4087 | -7.474 |  | 138
ODNTH | ODNTH | 1122 | ODESSA N | 37.033 |  |  |  | WEST2001 | ECTOR | 0.28806 | -0.11095 | 10.6679 | -4.1089 |  | 138
ODNTH | ODNTH | 1123 | ODESSA N | 28.065 |  |  |  | WEST2001 | ECTOR | 0.28693 | -0.11069 | 8.0526 | -3.1066 |  | 69
ODESA | ODESA | 1126 | ODESSA 2 | 34.089 |  |  |  | WEST2001 | ECTOR | 0.28817 | -0.11097 | 9.8236 | -3.7829 |  | 138
ODESA | ODESA | 1127 | ODESSA 1 | 33.552 |  |  |  | WEST2001 | ECTOR | 0.28824 | -0.11099 | 9.671 | -3.724 |  | 138
LIQAR | LIQAR | 1128 | LIQD AIR | 6.732 |  |  |  | WEST2001 | ECTOR | 0.28822 | -0.11098 | 1.9403 | -0.74711 |  | 138
WOVER | WOVER | 1129 | WESTOVER | 28.477 |  |  |  | WEST2001 | ECTOR | 0.28822 | -0.11099 | 8.2076 | -3.1608 |  | 138
SFAMO | SFAMO | 1130 | AM SFOST | 5.466 |  |  |  | WEST2001 | ECTOR | 0.2882 | -0.11099 | 1.5753 | -0.60666 |  | 138
MDDTN | MDDTN | 1132 | MIDL DWN | 25.783 |  |  |  | WEST2001 | MIDLAND | 0.28861 | -0.11118 | 7.4412 | -2.8665 |  | 138
TIODE | TIODE | 1137 | T.I. T |  |  |  |  | WEST2001 | MIDLAND | 0.28818 | -0.11103 | 0 | 0 |  | 138
TIODE | TIODE | 1138 | T.I. | 0.287 |  |  |  | WEST2001 | MIDLAND | 0.28832 | -0.11106 | 0.082747 | -0.031875 |  | 138
HLTSW | HLTSW | 1141 | HOLT SS |  |  |  |  | WEST2001 | ECTOR | 0.28727 | -0.11084 | 0 | 0 |  | 138
HLTSW | HLTSW | 1142 | HOLT SS |  |  |  |  | WEST2001 | ECTOR | 0.28702 | -0.11078 | 0 | 0 |  | 69
ANATP | ANATP | 1143 | AMOCNC T |  |  |  |  | WEST2001 | ECTOR | 0.28757 | -0.11089 | 0 | 0 |  | 138
NCWAM | NCWAM | 1144 | AM NCOWD | 16.618 |  |  |  | WEST2001 | ECTOR | 0.28757 | -0.11089 | 4.7789 | -1.8428 |  | 138
GSMAM | GSMAM | 1145 | AM GLDSM | 3.733 |  |  |  | WEST2001 | ECTOR | 0.28706 | -0.11078 | 1.0716 | -0.41353 |  | 138
CHEYT | CHEYT | 1147 | CHEYEN T |  |  |  |  | WEST2001 | WINKLER | 0.28626 | -0.11059 | 0 | 0 |  | 138
CHYNE | CHYNE | 1148 | CHEYENNE | 16.813 |  |  |  | WEST2001 | WINKLER | 0.28626 | -0.11059 | 4.8129 | -1.8593 |  | 138
DHIDE | DHIDE | 1149 | DOLRHIDE | 12.225 |  |  |  | WEST2001 | WINKLER | 0.28644 | -0.11068 | 3.5017 | -1.353 |  | 138
TBAMO | TBAMO | 1150 | AM 3BAR | 1.34 |  |  |  | WEST2001 | ANDREWS | 0.28651 | -0.11072 | 0.38393 | -0.14836 |  | 138
DHUNO | DHUNO | 1152 | UNOCAL | 5.818 |  |  |  | WEST2001 | ANDREWS | 0.28644 | -0.11068 | 1.6665 | -0.64393 |  | 138
ANDWT | ANDWT | 1155 | ANDREW T |  |  |  |  | WEST2001 | ANDREWS | 0.28668 | -0.1108 | 0 | 0 |  | 138
ANDRD | ANDRD | 1156 | ANDREWS | 5.46 |  |  |  | WEST2001 | ANDREWS | 0.28668 | -0.1108 | 1.5653 | -0.60498 |  | 138
|  | 1158 | SLMSA LE | 2.334 |  |  |  | WEST2001 | DAWSON | 0.28621 | -0.11121 | 0.66802 | -0.25956 |  | 69.6
ANDNR | ANDNR | 1159 | N ANDREW | 25.516 |  |  |  | WEST2001 | ANDREWS | 0.28678 | -0.11085 | 7.3176 | -2.8286 |  | 138
ANDNR | ANDNR | 1160 | N ANDREW |  |  |  |  | WEST2001 | ANDREWS | 0.28682 | -0.11084 | 0 | 0 |  | 69
PBLUN | PBLUN | 1161 | UN PKRBK | 4.786 |  |  |  | WEST2001 | ANDREWS | 0.28695 | -0.11085 | 1.3733 | -0.53053 |  | 138
|  | 1162 | LMESA LE | 5.719 |  |  |  | WEST2001 | DAWSON | 0.28625 | -0.1112 | 1.6371 | -0.63597 |  | 138
LMESA | LMESA | 1163 | LAMESA | 1.992 |  |  |  | WEST2001 | DAWSON | 0.28625 | -0.1112 | 0.57022 | -0.22152 |  | 138
LMESA | LMESA | 1164 | LAMESA | 26.315 |  |  |  | WEST2001 | DAWSON | 0.28621 | -0.11121 | 7.5316 | -2.9265 |  | 69.6
EXMTP | EXMTP | 1165 | EXMEAN T |  |  |  |  | WEST2001 | ANDREWS | 0.28676 | -0.11087 | 0 | 0 |  | 138
MNSEX | MNSEX | 1166 | EXMEANS | 14.173 |  |  |  | WEST2001 | ANDREWS | 0.28676 | -0.11087 | 4.0642 | -1.5714 |  | 138
MSTNG | MSTNG | 1167 | MUSTANG | 7.992 |  |  |  | WEST2001 | ANDREWS | 0.28663 | -0.11096 | 2.2908 | -0.88675 |  | 138
PDAVT | PDAVT | 1168 | PAUL D T |  |  |  |  | WEST2001 | DAWSON | 0.28649 | -0.11105 | 0 | 0 |  | 138
PLDAV | PLDAV | 1169 | PAUL DVS | 3.477 |  |  |  | WEST2001 | MARTIN | 0.28649 | -0.11105 | 0.99611 | -0.38612 |  | 138
GVODS | GVODS | 1176 | GRANDVW | 45.48 |  |  |  | WEST2001 | ECTOR | 0.28854 | -0.11111 | 13.1228 | -5.0532 |  | 138
MABTX | MABTX | 1177 | TEXMABEE | 10.311 |  |  |  | WEST2001 | MARTIN | 0.28868 | -0.11116 | 2.9766 | -1.1462 |  | 138
ADMDS | ADMDS | 1178 | ADOBE MD | 7.345 |  |  |  | WEST2001 | MIDLAND | 0.28876 | -0.1112 | 2.121 | -0.81674 |  | 138
TEXTP | TEXTP | 1179 | TEX MA T |  |  |  |  | WEST2001 | MIDLAND | 0.28868 | -0.11116 | 0 | 0 |  | 138
ECTHM | ECTHM | 1180 | ECTR HIL | 18.09 |  |  |  | WEST2001 | ECTOR | 0.28844 | -0.11107 | 5.2179 | -2.0092 |  | 138
MKNGB | MKNGB | 1182 | MOCKNBRD | 28.268 |  |  |  | WEST2001 | MIDLAND | 0.2887 | -0.11117 | 8.161 | -3.1426 |  | 138
GODRD | GODRD | 1184 | GODDARD | 73.288 |  |  |  | WEST2001 | MIDLAND | 0.2887 | -0.11117 | 21.1582 | -8.1475 |  | 138
CRANE | CRANE | 1197 | CRANE |  |  |  |  | WEST2001 | CRANE | 0.27363 | -0.10724 | 0 | 0 |  | 138
CRANE | CRANE | 1198 | CRANE | 10.055 |  |  |  | WEST2001 | CRANE | 0.27935 | -0.10876 | 2.8088 | -1.0936 |  | 69
ACRNT | ACRNT | 1199 | ARCO C T |  |  |  |  | WEST2001 | CRANE | 0.27636 | -0.10794 | 0 | 0 |  | 138
CRNAR | CRNAR | 1201 | ARCO CRN | 17.102 |  |  |  | WEST2001 | CRANE | 0.27636 | -0.10794 | 4.7262 | -1.8459 |  | 138
WRDSW | WRDSW | 1202 | WARD SS |  |  |  |  | WEST2001 | WARD | 0.28364 | -0.10986 | 0 | 0 |  | 69
BRNSY | BRNSY | 1203 | BARNSLEY | 3.336 |  |  |  | WEST2001 | CRANE | 0.28141 | -0.10929 | 0.9388 | -0.36458 |  | 69
EXCRT | EXCRT | 1204 | EXN JC T |  |  |  |  | WEST2001 | CRANE | 0.28082 | -0.10914 | 0 | 0 |  | 69
CRDEX | CRDEX | 1205 | EXN JUAN | 2.45 |  |  |  | WEST2001 | CRANE | 0.28082 | -0.10914 | 0.68801 | -0.26738 |  | 69
CRATT | CRATT | 1206 | CRNATL T |  |  |  |  | WEST2001 | CRANE | 0.28003 | -0.10893 | 0 | 0 |  | 69
CRNAT | CRNAT | 1207 | CRAN ATL | 1.091 |  |  |  | WEST2001 | CRANE | 0.28003 | -0.10893 | 0.30551 | -0.11885 |  | 69
MDKSW | MDKSW | 1210 | MIDKIFF |  |  |  |  | WEST2001 | UPTON | 0.28645 | -0.11073 | 0 | 0 |  | 138
MDKSW | MDKSW | 1211 | MIDKIFF |  |  |  |  | WEST2001 | UPTON | 0.28506 | -0.11041 | 0 | 0 |  | 69
UPTON | UPTON | 1212 | UPTON | 3.364 |  |  |  | WEST2001 | UPTON | 0.28384 | -0.11006 | 0.95484 | -0.37024 |  | 69
|  | 1213 | PEMBRK T |  |  |  |  | WEST2001 | UPTON | 0.28506 | -0.11041 | 0 | 0 |  | 69
PMBRK | PMBRK | 1215 | PEMBROOK | 2.44 |  |  |  | WEST2001 | UPTON | 0.28506 | -0.11041 | 0.69556 | -0.26941 |  | 69
REAGN | REAGN | 1216 | REAGN SH | 0.14 |  |  |  | WEST2001 | REAGAN | 0.28422 | -0.11031 | 0.039791 | -0.015443 |  | 69
GLSCK | GLSCK | 1217 | GLASCOCK | 1.673 |  |  |  | WEST2001 | GLASSCOCK | 0.28373 | -0.11025 | 0.47467 | -0.18445 |  | 69
GRDNC | GRDNC | 1218 | GARD CTY | 2.662 |  |  |  | WEST2001 | GLASSCOCK | 0.28273 | -0.11013 | 0.75264 | -0.29316 |  | 69
TXHRV | TXHRV | 1221 | TEX HARV | 5.335 |  |  |  | WEST2001 | MIDLAND | 0.28498 | -0.11056 | 1.5204 | -0.58982 |  | 69
PCKTP | PCKTP | 1222 | PECK T |  |  |  |  | WEST2001 | MIDLAND | 0.28636 | -0.11082 | 0 | 0 |  | 69
PECK | PECK_ | 1223 | PECK | 8.624 |  |  |  | WEST2001 | MIDLAND | 0.28636 | -0.11082 | 2.4696 | -0.95571 |  | 69
|  | 1226 | MDGULF T |  |  |  |  | WEST2001 | MIDLAND | 0.28637 | -0.11091 | 0 | 0 |  | 69
MDGLF | MDGLF | 1227 | MID GULF | 5.098 |  |  |  | WEST2001 | MIDLAND | 0.28637 | -0.11091 | 1.4599 | -0.56543 |  | 69
MDBSN | MDBSN | 1228 | MIDBASIN | 3.664 |  |  |  | WEST2001 | MIDLAND | 0.28637 | -0.11091 | 1.0493 | -0.40638 |  | 69
STANT | STANT | 1229 | STANTON | 11.481 |  |  |  | WEST2001 | MARTIN | 0.28582 | -0.11094 | 3.2815 | -1.2737 |  | 69.6
CRNHU | CRNHU | 1232 | CRAN HUM | 0.667 |  |  |  | WEST2001 | CRANE | 0.27964 | -0.10883 | 0.18652 | -0.072591 |  | 69
GETTY | GETTY | 1233 | GETTY | 7.46 |  |  |  | WEST2001 | CRANE | 0.28013 | -0.10896 | 2.0898 | -0.81283 |  | 69
PEGTP | PEGTP | 1234 | PGASUS T |  |  |  |  | WEST2001 | ECTOR | 0.28428 | -0.11002 | 0 | 0 |  | 69
PEGAS | PEGAS | 1235 | PEGASUS | 5.606 |  |  |  | WEST2001 | MIDLAND | 0.28428 | -0.11002 | 1.5937 | -0.61675 |  | 69
PEGST | PEGST | 1236 | S PEGS T |  |  |  |  | WEST2001 | MIDLAND | 0.28428 | -0.11002 | 0 | 0 |  | 69
PGSTH | PGSTH | 1237 | S PGASUS | 7.203 |  |  |  | WEST2001 | MIDLAND | 0.28428 | -0.11002 | 2.0477 | -0.79245 |  | 69.6
RYLTY | RYLTY | 1238 | ROYALTY | 7.886 |  |  |  | WEST2001 | WARD | 0.28563 | -0.11037 | 2.2524 | -0.87035 |  | 69
COYAN | COYAN | 1239 | COYANOSA | 4.334 |  |  |  | WEST2001 | PECOS | 0.28563 | -0.11037 | 1.2379 | -0.47833 |  | 69
WLFTP | WLFTP | 1240 | WFCAMP T |  |  |  |  | WEST2001 | PECOS | 0.28563 | -0.11037 | 0 | 0 |  | 69
WFCMP | WFCMP | 1241 | WOLFCAMP | 1.249 |  |  |  | WEST2001 | PECOS | 0.28563 | -0.11037 | 0.35675 | -0.13785 |  | 69
NNTRL | NNTRL | 1242 | NNATURAL | 0.276 |  |  |  | WEST2001 | PECOS | 0.28563 | -0.11037 | 0.078833 | -0.030461 |  | 69
WNKBT | WNKBT | 1245 | WINK BWT |  |  |  |  | WEST2001 | WINKLER | 0.28603 | -0.11048 | 0 | 0 |  | 69
WKBSN | WKBSN | 1246 | WINK BSN | 3.94 |  |  |  | WEST2001 | WINKLER | 0.28603 | -0.11048 | 1.127 | -0.43529 |  | 69
KYSTN | KYSTN | 1249 | KEYSTONE | 5.181 |  |  |  | WEST2001 | WINKLER | 0.28603 | -0.11048 | 1.4819 | -0.57239 |  | 69
VEST | VEST_ | 1252 | VEST | 1.1 |  |  |  | WEST2001 | WINKLER | 0.2862 | -0.11052 | 0.31481 | -0.12157 |  | 69
MIDWY | MIDWY | 1253 | MIDWAY | 9.25 |  |  |  | WEST2001 | ECTOR | 0.28661 | -0.11063 | 2.6511 | -1.0233 |  | 69
ODBSW | ODBSW | 1254 | ODBAS SS |  |  |  |  | WEST2001 | ECTOR | 0.28683 | -0.11069 | 0 | 0 |  | 69
ODBSN | ODBSN | 1255 | ODES BSN | 2.199 |  |  |  | WEST2001 | ECTOR | 0.28685 | -0.1107 | 0.63079 | -0.24343 |  | 69
GSMTH | GSMTH | 1256 | GOLDSMTH | 18.503 |  |  |  | WEST2001 | ECTOR | 0.28694 | -0.11074 | 5.3092 | -2.049 |  | 69
ECTSH | ECTSH | 1257 | ECTR SHL | 0.588 |  |  |  | WEST2001 | ECTOR | 0.28696 | -0.11075 | 0.16873 | -0.06512 |  | 69
NCWDN | NCWDN | 1259 | N COWDEN | 11.123 |  |  |  | WEST2001 | ECTOR | 0.28699 | -0.11075 | 3.1921 | -1.2318 |  | 69
GSCHV | GSCHV | 1260 | GOLDS CG | 0.448 |  |  |  | WEST2001 | ECTOR | 0.28694 | -0.11074 | 0.12855 | -0.04961 |  | 69
EMATP | EMATP | 1262 | EMMA T |  |  |  |  | WEST2001 | ANDREWS | 0.28696 | -0.11079 | 0 | 0 |  | 69
EMMA | EMMA_ | 1263 | EMMA | 7.371 |  |  |  | WEST2001 | ANDREWS | 0.28696 | -0.11079 | 2.1152 | -0.81667 |  | 69
ANDRT | ANDRT | 1264 | SAN AN T |  |  |  |  | WEST2001 | ANDREWS | 0.28696 | -0.11079 | 0 | 0 |  | 69
SNAND | SNAND | 1265 | SAN ANDR | 1.688 |  |  |  | WEST2001 | ANDREWS | 0.28696 | -0.11079 | 0.4844 | -0.18702 |  | 69
MDFRM | MDFRM | 1266 | MIDFARMS | 2.875 |  |  |  | WEST2001 | ANDREWS | 0.28696 | -0.11079 | 0.82502 | -0.31853 |  | 69
ANDRD | ANDRD | 1267 | ANDREWS |  |  |  |  | WEST2001 | ANDREWS | 0.28688 | -0.11082 | 0 | 0 |  | 69
FKLCY | FKLCY | 1270 | FRNKLCTY | 7.44 |  |  |  | WEST2001 | ANDREWS | 0.28686 | -0.11083 | 2.1342 | -0.82457 |  | 69.6
ANPHL | ANPHL | 1273 | PHIL AND | 0.543 |  |  |  | WEST2001 | ANDREWS | 0.28686 | -0.11083 | 0.15576 | -0.060181 |  | 69.6
FLRTN | FLRTN | 1274 | FULERTON | 4.187 |  |  |  | WEST2001 | ANDREWS | 0.28686 | -0.11083 | 1.2011 | -0.46405 |  | 69.6
FLTEX | FLTEX | 1275 | EXXONFUL | 20.243 |  |  |  | WEST2001 | ANDREWS | 0.28686 | -0.11083 | 5.8069 | -2.2435 |  | 69.6
BAKTP | BAKTP | 1277 | BAKKE T |  |  |  |  | WEST2001 | ANDREWS | 0.28685 | -0.11083 | 0 | 0 |  | 69
BAKKE | BAKKE | 1280 | BAKKE | 8.206 |  |  |  | WEST2001 | ANDREWS | 0.28685 | -0.11083 | 2.3539 | -0.90948 |  | 69
AMMFT | AMMFT | 1281 | AMMIDF T |  |  |  |  | WEST2001 | ANDREWS | 0.28718 | -0.11084 | 0 | 0 |  | 138
MDFAM | MDFAM | 1282 | AM MIDFM | 18.013 |  |  |  | WEST2001 | ANDREWS | 0.28718 | -0.11084 | 5.1729 | -1.9966 |  | 138
MEANS | MEANS | 1285 | MEANS | 4.286 |  |  |  | WEST2001 | ANDREWS | 0.28684 | -0.11084 | 1.2294 | -0.47505 |  | 69
ECTHP | ECTHP | 1292 | ECTR HRP | 4.665 |  |  |  | WEST2001 | ECTOR | 0.28817 | -0.11098 | 1.3443 | -0.51774 |  | 138
WCKTP | WCKTP | 1295 | WICKETT | 13.671 |  |  |  | WEST2001 | WARD | 0.28605 | -0.11047 | 3.9106 | -1.5102 |  | 69
NWARD | NWARD | 1296 | NORTHWRD | 1.336 |  |  |  | WEST2001 | WARD | 0.28584 | -0.11043 | 0.38188 | -0.14753 |  | 69
WCKTP | WCKTP | 1297 | WICKET T |  |  |  |  | WEST2001 | WARD | 0.28574 | -0.1104 | 0 | 0 |  | 69
SHRNE | SHRNE | 1300 | EX SHARN | 13.967 |  |  |  | WEST2001 | SCURRY | 0.28582 | -0.11155 | 3.992 | -1.558 |  | 138
SNYDR | SNYDR | 1305 | SNYDER | 13.215 |  |  |  | WEST2001 | SCURRY | 0.28541 | -0.11165 | 3.7717 | -1.4755 |  | 138
SNYDR | SNYDR | 1306 | SNYDER | 19.55 |  |  |  | WEST2001 | SCURRY | 0.28541 | -0.11163 | 5.5797 | -2.1824 |  | 69
KEY | KEY__ | 1307 | KEY LE | 5.011 |  |  |  | WEST2001 | DAWSON | 0.28617 | -0.11127 | 1.434 | -0.55757 |  | 138
GAIL | GAIL_ | 1308 | GAIL LE | 1.298 |  |  |  | WEST2001 | BORDEN | 0.28595 | -0.11145 | 0.37116 | -0.14466 |  | 138
BCKSW | BCKSW | 1309 | BLUFCK T |  |  |  |  | WEST2001 | SCURRY | 0.28577 | -0.11159 | 0 | 0 |  | 138
KNAPP | KNAPP | 1310 | KNAPP | 4.272 |  |  |  | WEST2001 | SCURRY | 0.28561 | -0.1116 | 1.2201 | -0.47677 |  | 138
SACRC | SACRC | 1311 | SACROC | 6.756 |  |  |  | WEST2001 | SCURRY | 0.28496 | -0.11166 | 1.9252 | -0.75438 |  | 138
SCPNZ | SCPNZ | 1312 | SCURY CH | 5.224 |  |  |  | WEST2001 | SCURRY | 0.28515 | -0.11164 | 1.4896 | -0.58321 |  | 138
ENCRT | ENCRT | 1313 | ENISCK T |  |  |  |  | WEST2001 | SCURRY | 0.2851 | -0.11164 | 0 | 0 |  | 138
ECRSW | ECRSW | 1314 | ENNIS CK | 10.099 |  |  |  | WEST2001 | SCURRY | 0.28511 | -0.11164 | 2.8793 | -1.1275 |  | 138
BRAND | BRAND | 1315 | BRAND |  |  |  |  | WEST2001 | SCURRY | 0.285 | -0.11165 | 0 | 0 |  | 138
CGRSW | CGRSW | 1318 | CHINAGRV |  |  |  |  | WEST2001 | MITCHELL | 0.28611 | -0.11165 | 0 | 0 |  | 138
CGRSW | CGRSW | 1319 | CHINAGRV |  |  |  |  | WEST2001 | MITCHELL | 0.28547 | -0.1116 | 0 | 0 |  | 69
BSPSW | BSPSW | 1322 | BIG SPRG | 20.12 |  |  |  | WEST2001 | HOWARD | 0.2867 | -0.11134 | 5.7685 | -2.2403 |  | 138
BSPSW | BSPSW | 1323 | BIG SPRG | 14.278 |  |  |  | WEST2001 | HOWARD | 0.285 | -0.11097 | 4.0692 | -1.5845 |  | 69.6
BSPRW | BSPRW | 1324 | BIG SPGW | 34.015 |  |  |  | WEST2001 | HOWARD | 0.28704 | -0.11132 | 9.7637 | -3.7866 |  | 138
AIRPK | AIRPK | 1325 | AIR PARK | 15.419 |  |  |  | WEST2001 | MARTIN | 0.28704 | -0.11132 | 4.4259 | -1.7165 |  | 138
SBYSW | SBYSW | 1329 | SPRABERY |  |  |  |  | WEST2001 | MIDLAND | 0.28778 | -0.11104 | 0 | 0 |  | 138
SBYSW | SBYSW | 1330 | SPRABERY |  |  |  |  | WEST2001 | MIDLAND | 0.28675 | -0.11089 | 0 | 0 |  | 69
|  | 1331 | U CARBID |  |  |  |  | WEST2001 | HOWARD | 0.28675 | -0.11135 | 0 | 0 |  | 138
COSDN | COSDN | 1332 | COSDEN | 24.218 |  |  |  | WEST2001 | HOWARD | 0.28676 | -0.11136 | 6.9447 | -2.6968 |  | 138
FRSTP | FRSTP | 1335 | FORSAN T |  |  |  |  | WEST2001 | GLASSCOCK | 0.28815 | -0.11139 | 0 | 0 |  | 138
FORSN | FORSN | 1336 | FORSAN | 7.458 |  |  |  | WEST2001 | GLASSCOCK | 0.28815 | -0.11139 | 2.149 | -0.83074 |  | 138
CRM7T | CRM7T | 1337 | CRMWD7 T |  |  |  |  | WEST2001 | MIDLAND | 0.2878 | -0.11106 | 0 | 0 |  | 138
CRMW7 | CRMW7 | 1338 | CRMWD-7 | 1.873 |  |  |  | WEST2001 | MIDLAND | 0.2878 | -0.11106 | 0.53904 | -0.20801 |  | 138
ESKSW | ESKSW | 1339 | ESKOTA |  |  |  |  | WEST2001 | NOLAN | 0.27381 | -0.11084 | 0 | 0 |  | 138
ESKSW | ESKSW | 1340 | ESKOTA | 0.471 |  |  |  | WEST2001 | NOLAN | 0.27374 | -0.11094 | 0.12893 | -0.052255 |  | 69
SWRTP | SWRTP | 1341 | SWTRDT T |  |  |  |  | WEST2001 | NOLAN | 0.27742 | -0.11106 | 0 | 0 |  | 138
SWDTN | SWDTN | 1342 | SWWTR DT | 27.492 |  |  |  | WEST2001 | NOLAN | 0.27742 | -0.11106 | 7.627 | -3.0533 |  | 138
|  | 1343 | TRENTIPP |  |  | 20 | 135 | WEST2001 | NOLAN | 0.27381 | -0.11084 | 36.965 | -14.9628 |  | 138
ESKSW | ESKSW | 1344 | ESKOT TA | 2.145 |  |  |  | WEST2001 | NOLAN | 0.27374 | -0.11094 | 0.58717 | -0.23797 |  | 69
COHMA | COHMA | 1345 | COAHOMA | 4.838 |  |  |  | WEST2001 | HOWARD | 0.2854 | -0.11112 | 1.3808 | -0.5376 |  | 69.6
IHRDT | IHRDT | 1346 | IA/HOW T |  |  |  |  | WEST2001 | HOWARD | 0.2857 | -0.11123 | 0 | 0 |  | 69.6
HOWRD | HOWRD | 1347 | IATN/HOW | 8.352 |  |  |  | WEST2001 | HOWARD | 0.2857 | -0.11123 | 2.3862 | -0.92901 |  | 69.6
WBROK | WBROK | 1348 | WSTBROOK | 3.766 |  |  |  | WEST2001 | MITCHELL | 0.28623 | -0.11143 | 1.078 | -0.41963 |  | 69
|  | 1350 | NWPWR G1 |  |  | 4 | 35 | WEST2001 | HOWARD | 0.28084 | -0.11005 | 9.8294 | -3.8519 |  | 13.8
BSGUL | BSGUL | 1351 | BSPGGULF | 0.827 |  |  |  | WEST2001 | HOWARD | 0.2824 | -0.1104 | 0.23354 | -0.0913 |  | 69.6
CHALK | CHALK | 1352 | CHALK | 9.998 |  |  |  | WEST2001 | HOWARD | 0.2767 | -0.10914 | 2.7664 | -1.0912 |  | 69.6
|  | 1353 | NWPWR T |  |  |  |  | WEST2001 | HOWARD | 0.28084 | -0.11005 | 0 | 0 |  | 69.6
AVMSW | AVMSW | 1355 | ACKRLY V |  |  |  |  | WEST2001 | HOWARD | 0.28617 | -0.11133 | 0 | 0 |  | 138
AVMSW | AVMSW | 1356 | ACKRLY V |  |  |  |  | WEST2001 | HOWARD | 0.28597 | -0.11124 | 0 | 0 |  | 69
BSCRM | BSCRM | 1357 | CRMWD | 0.19 |  |  |  | WEST2001 | HOWARD | 0.28511 | -0.11101 | 0.054171 | -0.021091 |  | 69.6
KNOTT | KNOTT | 1358 | KNOTT | 0.202 |  |  |  | WEST2001 | HOWARD | 0.28561 | -0.11114 | 0.057694 | -0.022451 |  | 69
ACHEV | ACHEV | 1359 | ACK CHEV | 0.097 |  |  |  | WEST2001 | HOWARD | 0.28588 | -0.11122 | 0.02773 | -0.010788 |  | 69
ACRLY | ACRLY | 1362 | ACKERLY | 2.147 |  |  |  | WEST2001 | DAWSON | 0.286 | -0.11124 | 0.61404 | -0.23883 |  | 69
ALYNT | ALYNT | 1363 | ACKR LE | 3.946 |  |  |  | WEST2001 | DAWSON | 0.28607 | -0.11123 | 1.1288 | -0.43891 |  | 69
SNBRG | SNBRG | 1364 | SPARNBRG | 0.2 |  |  |  | WEST2001 | DAWSON | 0.2861 | -0.11123 | 0.05722 | -0.022245 |  | 69
IRA | IRA__ | 1367 | IRA | 1.581 |  |  |  | WEST2001 | SCURRY | 0.28545 | -0.11161 | 0.45129 | -0.17646 |  | 69
SCURY | SCURY | 1368 | SCURRY | 3.626 |  |  |  | WEST2001 | SCURRY | 0.28543 | -0.11162 | 1.035 | -0.40474 |  | 69
LKTMS | LKTMS | 1369 | LKTHOMAS | 9.927 |  |  |  | WEST2001 | SCURRY | 0.28543 | -0.11162 | 2.8335 | -1.1081 |  | 69
SCSFE | SCSFE | 1370 | SANTA FE | 1.705 |  |  |  | WEST2001 | SCURRY | 0.28542 | -0.11163 | 0.48664 | -0.19033 |  | 69
MURRY | MURRY | 1371 | MURRAY M |  |  |  |  | WEST2001 | YOUNG | 0.25595 | -0.11374 | 0 | 0 |  | 138
CLBSN | CLBSN | 1373 | COLBASIN | 6.329 |  |  |  | WEST2001 | SCURRY | 0.28547 | -0.1116 | 1.8067 | -0.70634 |  | 69
CGRGF | CGRGF | 1374 | CHGRGULF | 1.768 |  |  |  | WEST2001 | SCURRY | 0.28547 | -0.1116 | 0.50471 | -0.19732 |  | 69
AMOCO | AMOCO | 1375 | AMOCO | 0.734 |  |  |  | WEST2001 | SCURRY | 0.28547 | -0.1116 | 0.20953 | -0.081918 |  | 69
AMOTP | AMOTP | 1376 | AMOCO T |  |  |  |  | WEST2001 | SCURRY | 0.28547 | -0.11161 | 0 | 0 |  | 69
CLCTY | CLCTY | 1378 | COLO CTY | 15.404 |  |  |  | WEST2001 | MITCHELL | 0.28466 | -0.11151 | 4.385 | -1.7178 |  | 69
LORAN | LORAN | 1379 | LORAINE | 1.1 |  |  |  | WEST2001 | MITCHELL | 0.28184 | -0.11137 | 0.31003 | -0.1225 |  | 69
ROSCO | ROSCO | 1380 | ROSCOE | 4.146 |  |  |  | WEST2001 | NOLAN | 0.2781 | -0.11117 | 1.153 | -0.46092 |  | 69
SWTWR | SWTWR | 1381 | SWEETWTR | 5.286 |  |  |  | WEST2001 | NOLAN | 0.27597 | -0.11106 | 1.4588 | -0.58706 |  | 69
USGTP | USGTP | 1382 | USGYP ST |  |  |  |  | WEST2001 | NOLAN | 0.27499 | -0.11101 | 0 | 0 |  | 69
USGYP | USGYP | 1383 | USGYP 2 |  |  |  |  | WEST2001 | NOLAN | 0.27499 | -0.11101 | 0 | 0 |  | 69
USGYP | USGYP | 1384 | USGYP 1 | 3.241 |  |  |  | WEST2001 | NOLAN | 0.27499 | -0.11101 | 0.89124 | -0.35978 |  | 69
FLNTK | FLNTK | 1385 | FLINTKOT | 1.626 |  |  |  | WEST2001 | NOLAN | 0.27475 | -0.111 | 0.44674 | -0.18048 |  | 69
FLNST | FLNST | 1386 | FLINT ST |  |  |  |  | WEST2001 | NOLAN | 0.27475 | -0.111 | 0 | 0 |  | 69
USGYP | USGYP | 1387 | USGYP T |  |  |  |  | WEST2001 | NOLAN | 0.27499 | -0.11101 | 0 | 0 |  | 69
WELCH | WELCH | 1388 | WELCH LE | 3.389 |  |  |  | WEST2001 | DAWSON | 0.28621 | -0.11121 | 0.96997 | -0.37689 |  | 69.6
WLCHT | WLCHT | 1389 | WELCH T |  |  |  |  | WEST2001 | DAWSON | 0.28621 | -0.11121 | 0 | 0 |  | 69.6
WELCH | WELCH | 1390 | WELCH | 8.728 |  |  |  | WEST2001 | DAWSON | 0.28621 | -0.11121 | 2.498 | -0.97064 |  | 69.6
DWSON | DWSON | 1391 | DAWSON | 0.547 |  |  |  | WEST2001 | DAWSON | 0.28621 | -0.11121 | 0.15656 | -0.060832 |  | 69.6
OXWCH | OXWCH | 1392 | OXY USA | 3.599 |  |  |  | WEST2001 | DAWSON | 0.28621 | -0.11121 | 1.0301 | -0.40024 |  | 69.6
DWSON | DWSON | 1393 | DAWSN LE | 3.651 |  |  |  | WEST2001 | DAWSON | 0.28621 | -0.11121 | 1.045 | -0.40603 |  | 69.6
GVLTP | GVLTP | 1394 | GTTY V T |  |  |  |  | WEST2001 | HOWARD | 0.28642 | -0.11143 | 0 | 0 |  | 138
GYVLM | GYVLM | 1395 | GETTY VL | 2.236 |  |  |  | WEST2001 | HOWARD | 0.28633 | -0.11139 | 0.64023 | -0.24907 |  | 138
|  | 1398 | RADIUM M |  |  |  |  | WEST2001 | JONES | 0.27086 | -0.11162 | 0 | 0 |  | 138
CGDEL | CGDEL | 1400 | TXCO COG | 13.581 |  |  |  | WEST2001 | SCURRY | 0.28534 | -0.11164 | 3.8752 | -1.5161 |  | 69
CGDTP | CGDTP | 1401 | COGDEL T |  |  |  |  | WEST2001 | SCURRY | 0.28534 | -0.11164 | 0 | 0 |  | 69
CGDEL | CGDEL | 1402 | COGDELL | 1.29 |  |  |  | WEST2001 | SCURRY | 0.28534 | -0.11164 | 0.36809 | -0.14401 |  | 69
PLVWT | PLVEW | 1403 | MDWEST M |  |  |  |  | WEST2001 | SCURRY | 0.28533 | -0.11164 | 0 | 0 |  | 69
OAKCK | OAKCK | 1406 | OAKCREEK | 1.086 |  |  |  | WEST2001 | NOLAN | 0.27374 | -0.11094 | 0.29728 | -0.12049 |  | 69.6
LNSTC | LNSTC | 1407 | LONESTAR | 10.519 |  |  |  | WEST2001 | NOLAN | 0.27374 | -0.11094 | 2.8794 | -1.167 |  | 69.6
NOLNW | NOLNW | 1408 | NOLANWTA | 5.279 |  |  |  | WEST2001 | NOLAN | 0.27374 | -0.11094 | 1.4451 | -0.58567 |  | 69.6
NLNWT | NLNWT | 1409 | NOLAN WT |  |  |  |  | WEST2001 | NOLAN | 0.27374 | -0.11094 | 0 | 0 |  | 69.6
ECRSW | ECRSW | 1410 | ENSCRKSS |  |  |  |  | WEST2001 | SCURRY | 0.28511 | -0.11164 | 0 | 0 |  | 138
ECRSW | ECRSW | 1411 | ENSCRKSS |  |  |  |  | WEST2001 | SCURRY | 0.28533 | -0.11164 | 0 | 0 |  | 69
PLVEW | PLVEW | 1412 | PLAINV T |  |  |  |  | WEST2001 | SCURRY | 0.28539 | -0.11163 | 0 | 0 |  | 69
SWCOG | SWCOG | 1416 | ENCOGN1G |  |  | 35 | 35 | WEST2001 | NOLAN | 0.30098 | -0.11291 | 10.5342 | -3.9517 |  | 13.8
SWCOG | SWCOG | 1417 | ENCOGN2G |  |  | 70 | 70 | WEST2001 | NOLAN | 0.30098 | -0.11291 | 21.0685 | -7.9035 |  | 13.8
SWCOG | SWCOG | 1418 | ENCOGN3G |  |  | 70 | 70 | WEST2001 | NOLAN | 0.30098 | -0.11291 | 21.0685 | -7.9035 |  | 13.8
SWCOG | SWCOG | 1419 | ENCOGN4G |  |  | 80 | 80 | WEST2001 | NOLAN | 0.30098 | -0.11291 | 24.0783 | -9.0325 |  | 13.8
SWCOG | SWCOG | 1420 | ENCOGEN |  |  |  |  | WEST2001 | NOLAN | 0.30098 | -0.11291 | 0 | 0 |  | 345
BOMSW | BOMSW | 1422 | BOWMAN |  |  |  |  | WEST2001 | ARCHER | 0.2371 | -0.11538 | 0 | 0 |  | 345
BOMSW | BOMSW | 1423 | BOWMAN A |  |  |  |  | WEST2001 | ARCHER | 0.23027 | -0.11552 | 0 | 0 |  | 138
BOMSW | BOMSW | 1424 | BOWMAN B |  |  |  |  | WEST2001 | ARCHER | 0.2313 | -0.11549 | 0 | 0 |  | 138
FSHSW | FSHSW | 1425 | FISHRDSS |  |  |  |  | WEST2001 | WICHITA | 0.23904 | -0.11511 | 0 | 0 |  | 345
FSHSW | FSHSW | 1426 | FISHRDSS |  |  |  |  | WEST2001 | WICHITA | 0.23195 | -0.11539 | 0 | 0 |  | 138
FSHSW | FSHSW | 1427 | FISHR RD | 14.861 |  |  |  | WEST2001 | WICHITA | 0.23175 | -0.11539 | 3.444 | -1.7149 |  | 138
GRSES | GRSES | 1430 | GRAHAM |  |  |  |  | WEST2001 | YOUNG | 0.32574 | -0.11551 | 0 | 0 |  | 345
GRSES | GRSES | 1431 | GRAHAM P |  |  |  |  | WEST2001 | YOUNG | 0.25218 | -0.11468 | 0 | 0 |  | 138
GRSES | GRSES | 1432 | GRAM 2 G |  |  | 364 | 399 | WEST2001 | YOUNG | 0.32574 | -0.11551 | 129.9683 | -46.0901 |  | 22
GRSES | GRSES | 1433 | GRAM 1 G |  |  | 225 | 241 | WEST2001 | YOUNG | 0.25218 | -0.11468 | 60.7749 | -27.6374 |  | 20
LKWSW | LKWSW | 1446 | LK WICH |  |  |  |  | WEST2001 | WICHITA | 0.22707 | -0.1156 | 0 | 0 |  | 138
LKWSW | LKWSW | 1447 | LK WICH |  |  |  |  | WEST2001 | WICHITA | 0.22665 | -0.1155 | 0 | 0 |  | 69
WFALS | WFALS | 1448 | WFALLS | 60.683 |  |  |  | WEST2001 | WICHITA | 0.22911 | -0.11549 | 13.903 | -7.0084 |  | 138
WFALS | WFALS | 1449 | WFALLS |  |  |  |  | WEST2001 | WICHITA | 0.22296 | -0.11568 | 0 | 0 |  | 69
PLVSW | PLVSW | 1450 | PLEASVAL |  |  |  |  | WEST2001 | WICHITA | 0.2293 | -0.11553 | 0 | 0 |  | 138
PLVSW | PLVSW | 1451 | PLEASVAL |  |  |  |  | WEST2001 | WICHITA | 0.22601 | -0.1156 | 0 | 0 |  | 69
LNMTP | LNMTP | 1452 | LANHAM M |  |  |  |  | WEST2001 | CLAY | 0.18603 | -0.11682 | 0 | 0 |  | 69
WFSSW | WFSSW | 1464 | S WFALLS |  |  |  |  | WEST2001 | ARCHER | 0.22513 | -0.11566 | 0 | 0 |  | 138
NSTAR | NSTAR | 1467 | NORTHSTR | 2.423 |  |  |  | WEST2001 | CLAY | 0.21035 | -0.11619 | 0.50968 | -0.28153 |  | 138
LKARH | LKARH | 1468 | AROWHEAD | 1.584 |  |  |  | WEST2001 | CLAY | 0.20465 | -0.11639 | 0.32416 | -0.18437 |  | 138
NVKSW | NVKSW | 1472 | NAVYK SS |  |  |  |  | WEST2001 | ARCHER | 0.23218 | -0.11525 | 0 | 0 |  | 138
NVKSW | NVKSW | 1473 | NAVYK SS |  |  |  |  | WEST2001 | ARCHER | 0.23068 | -0.11511 | 0 | 0 |  | 69
SCTLD | SCTLD | 1474 | SCOTLD M |  |  |  |  | WEST2001 | ARCHER | 0.23046 | -0.1154 | 0 | 0 |  | 138
WNDSW | WNDSW | 1475 | WINDTHOR |  |  |  |  | WEST2001 | ARCHER | 0.23264 | -0.1153 | 0 | 0 |  | 138
MRKLY | MRKLY | 1476 | MARKLEY | 1.261 |  |  |  | WEST2001 | YOUNG | 0.23784 | -0.1151 | 0.29991 | -0.14514 |  | 138
RICE | RICE_ | 1477 | RICE |  |  |  |  | WEST2001 | YOUNG | 0.24252 | -0.11492 | 0 | 0 |  | 138
AROHD | AROHD | 1478 | AROHD M |  |  |  |  | WEST2001 | ARCHER | 0.2253 | -0.11565 | 0 | 0 |  | 138
RTHGB | RTHGB | 1480 | RATHGBER | 14.071 |  |  |  | WEST2001 | WICHITA | 0.22701 | -0.11558 | 3.1943 | -1.6263 |  | 138
CTYVW | CTYVW | 1483 | CITYVIEW | 30.41 |  |  |  | WEST2001 | WICHITA | 0.23073 | -0.11545 | 7.0164 | -3.5109 |  | 138
WFPPG | WFPPG | 1484 | PPG | 10.842 |  |  |  | WEST2001 | WICHITA | 0.23033 | -0.11547 | 2.4973 | -1.252 |  | 138
CERMC | CERMC | 1485 | ACROCH | 4.568 |  |  |  | WEST2001 | WICHITA | 0.23015 | -0.11548 | 1.0513 | -0.52753 |  | 138
BMTWN | BMTWN | 1486 | BOOMTOWN | 15.275 |  |  |  | WEST2001 | WICHITA | 0.23015 | -0.11548 | 3.5156 | -1.764 |  | 138
|  | 1487 | HEMMERD |  |  |  |  | WEST2001 | WICHITA | 0.23038 | -0.11547 | 0 | 0 |  | 138
SIKES | SIKES | 1489 | SIKES | 14.959 |  |  |  | WEST2001 | WICHITA | 0.22739 | -0.11559 | 3.4015 | -1.729 |  | 138
WRBND | WRBND | 1492 | RVR BEND | 26.936 |  |  |  | WEST2001 | WICHITA | 0.22846 | -0.11555 | 6.1537 | -3.1126 |  | 138
ARTHR | ARTHR | 1493 | ARTHR ST | 64.98 |  |  |  | WEST2001 | WICHITA | 0.22785 | -0.11557 | 14.806 | -7.5099 |  | 138
WFSHP | WFSHP | 1494 | WF HOSP | 3.454 |  |  |  | WEST2001 | WICHITA | 0.22733 | -0.11559 | 0.7852 | -0.39924 |  | 138
CNTED | CNTED | 1496 | CERTEEDW | 8.686 |  |  |  | WEST2001 | WICHITA | 0.2305 | -0.1155 | 2.0021 | -1.0033 |  | 138
CNTED | CNTED | 1497 | CERTEEDE | 24.587 |  |  |  | WEST2001 | WICHITA | 0.2305 | -0.1155 | 5.6673 | -2.8399 |  | 138
WFCOG | WFCOG | 1498 | WF COGEN |  |  |  |  | WEST2001 | WICHITA | 0.2305 | -0.1155 | 0 | 0 |  | 138
PRKWY | PRKWY | 1499 | PARKWY E | 14.111 |  |  |  | WEST2001 | WICHITA | 0.22989 | -0.11552 | 3.244 | -1.6302 |  | 138
PRKWY | PRKWY | 1500 | PARKWY W | 22.486 |  |  |  | WEST2001 | WICHITA | 0.23055 | -0.1155 | 5.1842 | -2.5972 |  | 138
WFNTH | WFNTH | 1503 | N WFALLS | 28.791 |  |  |  | WEST2001 | WICHITA | 0.22421 | -0.11565 | 6.4551 | -3.3296 |  | 69
WFNTP | WFNTP | 1504 | NWF BYPS |  |  |  |  | WEST2001 | WICHITA | 0.22412 | -0.11565 | 0 | 0 |  | 69
WFNTP | WFNTP | 1507 | N WFAL T |  |  |  |  | WEST2001 | WICHITA | 0.22384 | -0.11565 | 0 | 0 |  | 69
WFBTP | WFBTP | 1508 | WF BSN T |  |  |  |  | WEST2001 | WICHITA | 0.22323 | -0.11567 | 0 | 0 |  | 69
PTRTP | PTRTP | 1509 | PETROL M |  |  |  |  | WEST2001 | WICHITA | 0.22323 | -0.11567 | 0 | 0 |  | 69
WFBSN | WFBSN | 1511 | WF BASIN | 5.14 |  |  |  | WEST2001 | WICHITA | 0.22323 | -0.11567 | 1.1474 | -0.59454 |  | 69
DSHAM | DSHAM | 1512 | DIAMNDSH | 0.335 |  |  |  | WEST2001 | WICHITA | 0.22323 | -0.11567 | 0.074782 | -0.038749 |  | 69
SHPRD | SHPRD | 1514 | SHEP AFB | 18.925 |  |  |  | WEST2001 | WICHITA | 0.22384 | -0.11565 | 4.2362 | -2.1888 |  | 69.6
SHPTP | SHPTP | 1515 | SHPRD T1 |  |  |  |  | WEST2001 | WICHITA | 0.22428 | -0.11564 | 0 | 0 |  | 69.6
BKBNT | BKBNT | 1517 | BURKBURN | 13.567 |  |  |  | WEST2001 | WICHITA | 0.225 | -0.11563 | 3.0525 | -1.5687 |  | 69.6
IOWPK | IOWPK | 1518 | IOWAPARK | 12.404 |  |  |  | WEST2001 | WICHITA | 0.22569 | -0.11561 | 2.7994 | -1.4341 |  | 69.6
CRYVC | CRYVC | 1519 | CRYOVAC | 20.974 |  |  |  | WEST2001 | WICHITA | 0.22569 | -0.11561 | 4.7335 | -2.4248 |  | 69.6
NVKPO | NVKPO | 1522 | NAVYKPOO | 1.995 |  |  |  | WEST2001 | ARCHER | 0.23068 | -0.11511 | 0.4602 | -0.22965 |  | 69
ARCTY | ARCTY | 1525 | ARCH CTY | 5.888 |  |  |  | WEST2001 | ARCHER | 0.23093 | -0.11507 | 1.3597 | -0.67754 |  | 69
BKWWF | BKWWF | 1526 | BLACKWEL | 0.255 |  |  |  | WEST2001 | ARCHER | 0.23134 | -0.115 | 0.058991 | -0.029325 |  | 69
HOLDY | HOLDY | 1527 | HOLLIDAY | 7.444 |  |  |  | WEST2001 | ARCHER | 0.23143 | -0.11498 | 1.7228 | -0.85593 |  | 69
BAYSW | BAYSW | 1530 | BAYLOR |  |  |  |  | WEST2001 | BAYLOR | 0.23275 | -0.11434 | 0 | 0 |  | 69
SMBSN | SMBSN | 1531 | SEYMRBAS | 0.922 |  |  |  | WEST2001 | BAYLOR | 0.23275 | -0.11434 | 0.2146 | -0.10542 |  | 69
SMOUR | SMOUR | 1532 | SEYMOUR | 0.385 |  |  |  | WEST2001 | BAYLOR | 0.23363 | -0.11391 | 0.089947 | -0.043857 |  | 69
BMRTN | BMRTN | 1533 | BOMARTON | 0.203 |  |  |  | WEST2001 | BAYLOR | 0.24441 | -0.11311 | 0.049615 | -0.022962 |  | 69
KMATP | KMATP | 1536 | KMA T |  |  |  |  | WEST2001 | WICHITA | 0.23605 | -0.11468 | 0 | 0 |  | 69
KMA | KMA__ | 1537 | KMA | 6.027 |  |  |  | WEST2001 | WICHITA | 0.23605 | -0.11468 | 1.4227 | -0.69119 |  | 69
ELCTR | ELCTR | 1538 | ELECTRA | 4.816 |  |  |  | WEST2001 | WICHITA | 0.24056 | -0.11439 | 1.1586 | -0.55089 |  | 69
RBNTK | RBNTK | 1541 | ROBNTECH | 1.226 |  |  |  | WEST2001 | WICHITA | 0.22522 | -0.11562 | 0.27612 | -0.14175 |  | 69
HNRTA | HNRTA | 1544 | HENRIETA | 8.637 |  |  |  | WEST2001 | CLAY | 0.17517 | -0.11715 | 1.5129 | -1.0118 |  | 69
RNGMT | RNGMT | 1545 | RNGMAG T |  |  |  |  | WEST2001 | CLAY | 0.15627 | -0.11773 | 0 | 0 |  | 69
RNGMG | RNGMG | 1546 | RNGMAG | 1.042 |  |  |  | WEST2001 | MONTAGUE | 0.15627 | -0.11773 | 0.16284 | -0.12268 |  | 69
GRMSW | GRMSW | 1596 | GRAHAMSS |  |  |  |  | WEST2001 | YOUNG | 0.22005 | -0.11483 | 0 | 0 |  | 138
GRMSW | GRMSW | 1597 | GRAHAMSS |  |  |  |  | WEST2001 | YOUNG | 0.22191 | -0.11473 | 0 | 0 |  | 69
GRMES | GRMES | 1601 | GRAHAM E | 19.3 |  |  |  | WEST2001 | YOUNG | 0.22809 | -0.11479 | 4.4021 | -2.2155 |  | 138
GRAHM | GRAHM | 1602 | GRAHAM | 13.861 |  |  |  | WEST2001 | YOUNG | 0.22271 | -0.11468 | 3.087 | -1.5896 |  | 69
OLNEY | OLNEY | 1603 | OLNEY M |  |  |  |  | WEST2001 | YOUNG | 0.22778 | -0.11496 | 0 | 0 |  | 69
ANARN | ANARN | 1604 | ANARENE | 0.85 |  |  |  | WEST2001 | ARCHER | 0.23005 | -0.11508 | 0.19554 | -0.097818 |  | 69
SBEND | SBEND | 1607 | S BEND | 0.749 |  |  |  | WEST2001 | YOUNG | 0.22388 | -0.11435 | 0.16768 | -0.08565 |  | 69
IVAN | IVAN_ | 1608 | IVAN | 8.157 |  |  |  | WEST2001 | STEPHENS | 0.22496 | -0.11405 | 1.835 | -0.93028 |  | 69
BRKNR | BRKNR | 1612 | BRECK N | 9.46 |  |  |  | WEST2001 | STEPHENS | 0.23307 | -0.11352 | 2.2048 | -1.0739 |  | 138
BRKTP | BRKTP | 1613 | BRECK T |  |  |  |  | WEST2001 | STEPHENS | 0.22097 | -0.11268 | 0 | 0 |  | 138
BRKRG | BRKRG | 1614 | BRECK | 28.946 |  |  |  | WEST2001 | STEPHENS | 0.22792 | -0.11321 | 6.5975 | -3.277 |  | 138
BRKRG | BRKRG | 1615 | BRECK | 9.753 |  |  |  | WEST2001 | STEPHENS | 0.22703 | -0.11347 | 2.2142 | -1.1066 |  | 69
SUNTP | SUNTP | 1616 | SUNECH T |  |  |  |  | WEST2001 | STEPHENS | 0.24149 | -0.11403 | 0 | 0 |  | 138
SUNPD | SUNPD | 1617 | SUN ECH | 5.424 |  |  |  | WEST2001 | STEPHENS | 0.24149 | -0.11403 | 1.3099 | -0.61851 |  | 138
CADDO | CADDO | 1618 | CADDO | 1.402 |  |  |  | WEST2001 | STEPHENS | 0.2199 | -0.11261 | 0.30829 | -0.15787 |  | 138
CLCRK | CLCRK | 1619 | COLNY CK | 1.364 |  |  |  | WEST2001 | EASTLAND | 0.18932 | -0.11052 | 0.25823 | -0.15075 |  | 138
ESTLD | ESTLD | 1622 | EASTLAND | 14.451 |  |  |  | WEST2001 | EASTLAND | 0.18654 | -0.10963 | 2.6957 | -1.5842 |  | 69
MRVLY | MRVLY | 1623 | MORT VAL | 1.27 |  |  |  | WEST2001 | EASTLAND | 0.18654 | -0.10963 | 0.23691 | -0.13923 |  | 69
LENSW | LENSW | 1624 | LEON |  |  |  |  | WEST2001 | EASTLAND | 0.17772 | -0.10973 | 0 | 0 |  | 138
LENSW | LENSW | 1625 | LEON 2 | 5.787 |  |  |  | WEST2001 | EASTLAND | 0.18654 | -0.10963 | 1.0795 | -0.63442 |  | 69
LENSW | LENSW | 1626 | LEON 5 |  |  |  |  | WEST2001 | EASTLAND | 0.17772 | -0.10973 | 0 | 0 |  | 69
RNGLF | RNGLF | 1627 | RAN GULF | 1.946 |  |  |  | WEST2001 | EASTLAND | 0.17772 | -0.10973 | 0.34585 | -0.21353 |  | 69
RANGR | RANGR | 1628 | RANGER | 6.399 |  |  |  | WEST2001 | EASTLAND | 0.17772 | -0.10973 | 1.1372 | -0.70214 |  | 69
GORMN | GORMN | 1630 | GORMAN | 4.28 |  |  |  | WEST2001 | EASTLAND | 0.18654 | -0.10963 | 0.79839 | -0.46921 |  | 69.6
DLMTP | DLMTP | 1631 | DLNMAG T |  |  |  |  | WEST2001 | COMANCHE | 0.18654 | -0.10963 | 0 | 0 |  | 69.6
DLMAG | DLMAG | 1632 | DLNMAG |  |  |  |  | WEST2001 | COMANCHE | 0.18654 | -0.10963 | 0 | 0 |  | 69.6
|  | 6000 | SILVRTP1 |  |  |  |  | WEST2001 | COKE | 0.25387 | -0.10507 | 0 | 0 |  | 69
SAJT | SAJT | 6001 | SAJACKT2 |  |  |  |  | WEST2001 | TOM GREEN | 0.23855 | -0.099962 | 0 | 0 |  | 69
MRFA | MRFA | 6002 | MARAIR 2 |  |  |  |  | WEST2001 | PRESIDIO | 0.27158 | -0.10672 | 0 | 0 |  | 69
|  | 6003 | BRNHRTP2 |  |  |  |  | WEST2001 | IRION | 0.23695 | -0.098532 | 0 | 0 |  | 69
|  | 6004 | CCTPATL2 |  |  |  |  | WEST2001 | COLEMAN | 0.23685 | -0.10239 | 0 | 0 |  | 69
STAP | STAP | 6005 | STAMFDP2 |  |  |  |  | WEST2001 | HASKELL | 0.26294 | -0.11181 | 0 | 0 |  | 69
SW_MESA | SW_MESA | 6014 | SWMTP2 |  |  |  |  | WEST2001 | UPTON | 0.25492 | -0.10247 | 0 | 0 |  | 138
SW_MESA | SW_MESA | 6015 | SWMESA2 |  |  |  |  | WEST2001 | UPTON | 0.25492 | -0.10247 | 0 | 0 |  | 138
SW_MESA | SW_MESA | 6016 | SWMESA |  |  | 11 | 75 | WEST2001 | UPTON | 0.25492 | -0.10247 | 19.1189 | -7.6856 |  | 34.5
|  | 6017 | ORNNWP1 |  |  | 4.1 | 125 | WEST2001 | PECOS | 0.25895 | -0.10337 | 32.3691 | -12.9217 |  | 34.5
|  | 6018 | ORNNWP4 |  |  |  |  | WEST2001 | PECOS | 0.25895 | -0.10337 | 0 | 0 |  | 138
|  | 6019 | ORNTP4 |  |  |  |  | WEST2001 | PECOS | 0.25895 | -0.10337 | 0 | 0 |  | 138
|  | 6022 | TAP4 |  |  |  |  | WEST2001 | PECOS | 0.25791 | -0.10308 | 0 | 0 |  | 138
TURK | TURK | 6024 | TURKEY 2 |  |  |  |  | WEST2001 | HALL | 0.26614 | -0.11207 | 0 | 0 |  | 69
CHLD | CHLD | 6028 | CHILD2WT |  |  |  |  | WEST2001 | CHILDRESS | 0.25898 | -0.11255 | 0 | 0 |  | 69
CHLD | CHLD | 6030 | CHILD4WT |  |  |  |  | WEST2001 | CHILDRESS | 0.25981 | -0.11243 | 0 | 0 |  | 138
CH20 | CH20 | 6031 | CHLD20 2 | 4.267 |  |  |  | WEST2001 | CHILDRESS | 0.2589 | -0.11256 | 1.1047 | -0.48031 |  | 69
CHIL | CHIL | 6032 | CHILDLD2 | 7.021 |  |  |  | WEST2001 | CHILDRESS | 0.25889 | -0.11257 | 1.8177 | -0.79032 |  | 69
CH20 | CH20 | 6033 | CHLD20T2 |  |  |  |  | WEST2001 | CHILDRESS | 0.2589 | -0.11256 | 0 | 0 |  | 69
FLOM | FLOM | 6041 | FLOMOTT2 |  |  |  |  | WEST2001 | MOTLEY | 0.26614 | -0.11207 | 0 | 0 |  | 69
FLOM | FLOM | 6042 | FLOMOT 2 | 1.179 |  |  |  | WEST2001 | MOTLEY | 0.26614 | -0.11207 | 0.31378 | -0.13213 |  | 69
TURL | TURL | 6044 | TURKREA2 | 1.953 |  |  |  | WEST2001 | BRISCOE | 0.26614 | -0.11207 | 0.51977 | -0.21888 |  | 69
PAUL | PAUL | 6048 | LKPAULS2 |  |  |  |  | WEST2001 | HARDEMAN | 0.25618 | -0.11297 | 0 | 0 |  | 69
PAUL | PAUL | 6050 | LKPAULS4 |  |  |  |  | WEST2001 | HARDEMAN | 0.25614 | -0.113 | 0 | 0 |  | 138
QUAN | QUAN | 6051 | QUANAH 2 | 6.598 |  |  |  | WEST2001 | HARDEMAN | 0.2567 | -0.11289 | 1.6937 | -0.74483 |  | 69
ACME | ACME | 6052 | ACMEBES2 | 2.907 |  |  |  | WEST2001 | HARDEMAN | 0.25715 | -0.11282 | 0.74752 | -0.32798 |  | 69
KIRK | KIRK | 6053 | KIRKLD 2 | 0.072 |  |  |  | WEST2001 | CHILDRESS | 0.25821 | -0.11267 | 0.018591 | -0.0081119 |  | 69
|  | 6056 | VRNMNTP2 |  |  |  |  | WEST2001 | WILBARGER | 0.25243 | -0.11356 | 0 | 0 |  | 69
CHLC | CHLC | 6057 | CHILE2WT | 2.673 |  |  |  | WEST2001 | HARDEMAN | 0.25447 | -0.11323 | 0.68021 | -0.30268 |  | 69
VERN | VERN | 6058 | VRNMAIN2 | 13.502 |  |  |  | WEST2001 | WILBARGER | 0.25181 | -0.11365 | 3.4 | -1.5346 |  | 69
VERN | VERN | 6060 | VRNMAIN4 |  |  |  |  | WEST2001 | WILBARGER | 0.25351 | -0.11352 | 0 | 0 |  | 138
VRCP | VRCP | 6061 | VERNPLT2 | 1.197 | 9 |  |  | WEST2001 | WILBARGER | 0.25183 | -0.11366 | 2.5679 | -1.159 |  | 69
SANT | SANT | 6062 | VERNTAP2 |  |  |  |  | WEST2001 | WILBARGER | 0.25183 | -0.11366 | 0 | 0 |  | 69
SAND | SAND | 6063 | SANDRD 2 | 9.019 |  |  |  | WEST2001 | WILBARGER | 0.25194 | -0.11369 | 2.2722 | -1.0254 |  | 69
VERS | VERS | 6064 | SW VERN2 |  |  |  |  | WEST2001 | WILBARGER | 0.25201 | -0.11371 | 0 | 0 |  | 69
VERS | VERS | 6066 | SW VERN4 |  |  |  |  | WEST2001 | WILBARGER | 0.25228 | -0.1138 | 0 | 0 |  | 138
GRBC | GRBC | 6070 | GRAYBAC2 | 1.035 |  |  |  | WEST2001 | WILBARGER | 0.24694 | -0.11397 | 0.25558 | -0.11796 |  | 69
GRBC | GRBC | 6071 | GRYBACT2 |  |  |  |  | WEST2001 | WILBARGER | 0.24694 | -0.11397 | 0 | 0 |  | 69
HARR | HARR | 6072 | HARROLD2 | 0.234 |  |  |  | WEST2001 | WILBARGER | 0.24494 | -0.1141 | 0.057315 | -0.0267 |  | 69
WAGR | WAGR | 6075 | WAGONER2 | 0.45 |  |  |  | WEST2001 | WILBARGER | 0.24149 | -0.11433 | 0.10867 | -0.051447 |  | 69
EXTR | EXTR | 6080 | TRUSEXN2 | 0.108 |  |  |  | WEST2001 | KING | 0.25676 | -0.11248 | 0.02773 | -0.012148 |  | 69
CRWL | CRWL | 6082 | CROWELL2 | 2.673 |  |  |  | WEST2001 | FOARD | 0.25762 | -0.1126 | 0.68862 | -0.30098 |  | 69
EXTR | EXTR | 6084 | TRUSEXT2 |  |  |  |  | WEST2001 | KNOX | 0.25676 | -0.11248 | 0 | 0 |  | 69
TRUS | TRUS | 6085 | TRUSCOT2 | 0.279 |  |  |  | WEST2001 | KNOX | 0.25672 | -0.11247 | 0.071625 | -0.03138 |  | 69
BENJ | BENJ | 6086 | BENJTAP2 |  |  |  |  | WEST2001 | KNOX | 0.25612 | -0.11239 | 0 | 0 |  | 69
BENJ | BENJ | 6087 | BENJMN 2 | 0.621 |  |  |  | WEST2001 | KNOX | 0.25612 | -0.11239 | 0.15905 | -0.069795 |  | 69
|  | 6095 | OK1DUM |  |  |  |  | WEST2001 | WILBARGER | 0.25238 | -0.11389 | 0 | 0 |  | 250
DCTM | DCTM | 6096 | NORTHDC7 | 188.6 | 220 |  |  | WEST2001 | WILBARGER | 0.25248 | -0.11386 | 103.1613 | -46.5226 |  | 345
OKLA | OKLA | 6097 | OKLEHV14 | 1.035 |  |  |  | WEST2001 | WILBARGER | 0.25305 | -0.11367 | 0.26191 | -0.11765 |  | 138
OKLA | OKLA | 6098 | OKLEHV24 |  |  |  |  | WEST2001 | WILBARGER | 0.25236 | -0.11382 | 0 | 0 |  | 138
OKLA | OKLA | 6100 | OKLAEHV7 |  |  |  |  | WEST2001 | WILBARGER | 0.25248 | -0.11386 | 0 | 0 |  | 345
MUND | MUND | 6107 | MUNDAY 2 | 2.565 |  |  |  | WEST2001 | KNOX | 0.25542 | -0.11229 | 0.65516 | -0.28803 |  | 69
MUNE | MUNE | 6108 | EMUNDAY2 |  |  |  |  | WEST2001 | KNOX | 0.25599 | -0.11228 | 0 | 0 |  | 69
MUNE | MUNE | 6110 | EMUNDY24 |  |  |  |  | WEST2001 | KNOX | 0.26071 | -0.11215 | 0 | 0 |  | 138
GILL | GILL | 6112 | GILESPR2 | 0.36 |  |  |  | WEST2001 | KNOX | 0.25781 | -0.11217 | 0.09281 | -0.04038 |  | 69
KNXC | KNXC | 6113 | KNOXCIT2 | 3.024 |  |  |  | WEST2001 | KNOX | 0.25845 | -0.11213 | 0.78154 | -0.33909 |  | 69
KNXR | KNXR | 6114 | KNOXREA |  |  |  |  | WEST2001 | KNOX | 0.25875 | -0.11212 | 0 | 0 |  | 69
ROCH | ROCH | 6115 | ROCHEST2 | 2.61 |  |  |  | WEST2001 | HASKELL | 0.25997 | -0.11205 | 0.67853 | -0.29246 |  | 69
|  | 6117 | EMUNDY14 |  |  |  |  | WEST2001 | KNOX | 0.26074 | -0.11215 | 0 | 0 |  | 138
CROW | CROW | 6119 | CRNCENT2 |  |  |  |  | WEST2001 | HASKELL | 0.26159 | -0.11196 | 0 | 0 |  | 69
RULE | RULE | 6120 | RULE 2 | 5.716 |  |  |  | WEST2001 | HASKELL | 0.26178 | -0.11196 | 1.4963 | -0.63995 |  | 69
CROW | CROW | 6121 | CRCENTT2 |  |  |  |  | WEST2001 | HASKELL | 0.26159 | -0.11196 | 0 | 0 |  | 69
HSKL | HSKL | 6122 | HASKELL2 | 7.849 |  |  |  | WEST2001 | HASKELL | 0.26099 | -0.11196 | 2.0485 | -0.8788 |  | 69
JOSS | JOSS | 6123 | JOSSELR2 | 0.352 |  |  |  | WEST2001 | HASKELL | 0.25911 | -0.11208 | 0.091206 | -0.039451 |  | 69
TXHS | TXHS | 6124 | HASTXTP2 |  |  |  |  | WEST2001 | HASKELL | 0.25883 | -0.11209 | 0 | 0 |  | 69
WEIN | WEIN | 6125 | WEINERT2 | 1.071 |  |  |  | WEST2001 | HASKELL | 0.25785 | -0.11215 | 0.27616 | -0.12011 |  | 69
TXHS | TXHS | 6126 | HASTXCO2 | 3.771 |  |  |  | WEST2001 | HASKELL | 0.25883 | -0.11209 | 0.97603 | -0.4227 |  | 69
PADR | PADR | 6131 | PADUCRT2 |  |  |  |  | WEST2001 | COTTLE | 0.26131 | -0.11232 | 0 | 0 |  | 69
PADU | PADU | 6132 | PADUCAH2 | 2.295 |  |  |  | WEST2001 | COTTLE | 0.26089 | -0.11234 | 0.59875 | -0.25782 |  | 69
PADC | PADC | 6133 | PADCLA 2 |  |  |  |  | WEST2001 | COTTLE | 0.26097 | -0.11233 | 0 | 0 |  | 69
PADC | PADC | 6135 | PADCLA 4 |  |  |  |  | WEST2001 | COTTLE | 0.26045 | -0.11233 | 0 | 0 |  | 138
MATA | MATA | 6140 | MATADOR2 | 1.908 |  |  |  | WEST2001 | MOTLEY | 0.26614 | -0.11207 | 0.5078 | -0.21384 |  | 69
ROAR | ROAR | 6141 | RNGSPGS2 | 0.846 |  |  |  | WEST2001 | MOTLEY | 0.26736 | -0.11201 | 0.22619 | -0.094762 |  | 69
AFTO | AFTO | 6142 | AFTON 2 | 2.052 |  |  |  | WEST2001 | DICKENS | 0.26914 | -0.11192 | 0.55228 | -0.22967 |  | 69
ESPU | ESPU | 6143 | ESPULAR2 |  |  |  |  | WEST2001 | DICKENS | 0.27121 | -0.11182 | 0 | 0 |  | 69
GIRA | GIRA | 6147 | GIRARD 2 | 0.063 |  |  |  | WEST2001 | KENT | 0.27097 | -0.1117 | 0.017071 | -0.0070368 |  | 69
SPUR | SPUR | 6148 | SPUR 2 | 1.188 |  |  |  | WEST2001 | DICKENS | 0.27221 | -0.11177 | 0.32338 | -0.13278 |  | 69
SPUR | SPUR | 6150 | SPUR 4 |  |  |  |  | WEST2001 | DICKENS | 0.27471 | -0.11173 | 0 | 0 |  | 138
|  | 6151 | GIRARDT2 |  |  |  |  | WEST2001 | KENT | 0.27097 | -0.1117 | 0 | 0 |  | 69
DKEC | DKEC | 6152 | JAYTONR2 |  |  |  |  | WEST2001 | KENT | 0.27035 | -0.11166 | 0 | 0 |  | 69
JATN | JATN | 6153 | JAYTON 2 | 1.503 |  |  |  | WEST2001 | KENT | 0.27003 | -0.11164 | 0.40586 | -0.16779 |  | 69
PEAC | PEAC | 6154 | PEACOCK2 | 0.144 |  |  |  | WEST2001 | STONEWALL | 0.2688 | -0.11168 | 0.038707 | -0.016082 |  | 69
ASPM | ASPM | 6155 | NASPMNT2 |  |  |  |  | WEST2001 | STONEWALL | 0.26783 | -0.11171 | 0 | 0 |  | 69
ASPM | ASPM | 6156 | ASPERMT2 | 3.195 |  |  |  | WEST2001 | STONEWALL | 0.26767 | -0.11172 | 0.85521 | -0.35693 |  | 69
ASPM | ASPM | 6158 | ASPERMT4 |  |  |  |  | WEST2001 | STONEWALL | 0.26839 | -0.11175 | 0 | 0 |  | 138
PAIP | PAIP | 6159 | PTCREEK2 | 0.927 |  |  |  | WEST2001 | HASKELL | 0.26295 | -0.11181 | 0.24376 | -0.10364 |  | 69
|  | 6160 | PC1DUM |  |  |  |  | WEST2001 | HASKELL | 0.26325 | -0.1118 | 0 | 0 |  | 100
PAIP | PAIP | 6161 | PTCRK1 4 |  |  |  |  | WEST2001 | HASKELL | 0.26381 | -0.1118 | 0 | 0 |  | 138
PAIP | PAIP | 6169 | TCRK2 4 |  |  |  |  | WEST2001 | HASKELL | 0.26376 | -0.11181 | 0 | 0 |  | 138
HASR | HASR | 6170 | HASKELR2 | 1.373 |  |  |  | WEST2001 | HASKELL | 0.26437 | -0.11163 | 0.36298 | -0.15327 |  | 69
HASR | HASR | 6171 | HSKELTP2 |  |  |  |  | WEST2001 | HASKELL | 0.26437 | -0.11163 | 0 | 0 |  | 69
STAM | STAM | 6172 | STAMFRD2 | 12.014 |  |  |  | WEST2001 | JONES | 0.26579 | -0.11146 | 3.1932 | -1.3391 |  | 69
CORN | CORN | 6173 | CORINTH2 | 0.513 |  |  |  | WEST2001 | JONES | 0.26672 | -0.11135 | 0.13683 | -0.057121 |  | 69
HSKL | HSKL | 6174 | HSKREAT2 |  |  |  |  | WEST2001 | HASKELL | 0.26103 | -0.11196 | 0 | 0 |  | 69
ANSN | ANSN | 6175 | ANSON 2 | 3.087 |  |  |  | WEST2001 | JONES | 0.26748 | -0.11126 | 0.8257 | -0.34345 |  | 69
ANSO | ANSO | 6176 | ANSONRE2 | 7.093 |  |  |  | WEST2001 | JONES | 0.2672 | -0.11116 | 1.8952 | -0.78847 |  | 69
SWEN | SWEN | 6177 | SWENSON2 | 0.054 |  |  |  | WEST2001 | STONE WALL | 0.26832 | -0.1117 | 0.014489 | -0.0060315 |  | 69
RADM | RADM | 6180 | RADIUM 2 |  |  |  |  | WEST2001 | JONES | 0.26909 | -0.11144 | 0 | 0 |  | 69
TXHA | TXHA | 6182 | HAMTXCO2 | 4.636 |  |  |  | WEST2001 | FISHER | 0.26875 | -0.11156 | 1.2459 | -0.51719 |  | 69
HAMR | HAMR | 6183 | HAMLINR2 | 1.266 |  |  |  | WEST2001 | JONES | 0.26924 | -0.11148 | 0.34085 | -0.14114 |  | 69
TXHA | TXHA | 6184 | HAMTXTP2 |  |  |  |  | WEST2001 | STONEWALL | 0.26875 | -0.11156 | 0 | 0 |  | 69
HAML | HAML | 6185 | HAMLIN 2 | 4.537 |  |  |  | WEST2001 | JONES | 0.26925 | -0.11149 | 1.2216 | -0.50581 |  | 69
SHHA | SHHA | 6186 | HAMSHEL2 | 0.135 |  |  |  | WEST2001 | JONES | 0.26874 | -0.11156 | 0.036279 | -0.015061 |  | 69
CONA | CONA | 6187 | ASPECON2 | 0.441 |  |  |  | WEST2001 | STONEWALL | 0.26804 | -0.11166 | 0.11821 | -0.049243 |  | 69
|  | 6191 | EXSHRN4 | 3.167 |  |  |  | WEST2001 | SCURRY | 0.28582 | -0.11155 | 0.90519 | -0.35327 |  | 138
ROTP | ROTP | 6192 | RONDTOP2 | 2.538 |  |  |  | WEST2001 | FISHER | 0.2703 | -0.11138 | 0.68601 | -0.28269 |  | 69
PLST | PLST | 6193 | PLASTCO2 | 1.386 |  |  |  | WEST2001 | FISHER | 0.26986 | -0.11143 | 0.37402 | -0.15444 |  | 69
ROTP | ROTP | 6194 | RONDTPT2 |  |  |  |  | WEST2001 | FISHER | 0.2703 | -0.11138 | 0 | 0 |  | 69
ROBY | ROBY | 6195 | ROBY 2 | 1.476 |  |  |  | WEST2001 | FISHER | 0.27132 | -0.11128 | 0.40046 | -0.16426 |  | 69
ROTN | ROTN | 6196 | ROTAN 2 | 9.068 |  |  |  | WEST2001 | FISHER | 0.27106 | -0.11136 | 2.458 | -1.0098 |  | 69
CLAT | CLAT | 6197 | CLARMNT2 |  |  |  |  | WEST2001 | KENT | 0.27038 | -0.11154 | 0 | 0 |  | 69
CLRM | CLRM | 6198 | CLARSUN2 | 0.441 |  |  |  | WEST2001 | KENT | 0.27038 | -0.11154 | 0.11924 | -0.04919 |  | 69
ALBNY_FD | ALBNY_FD | 6202 | ALFNDRY2 | 6.013 |  |  |  | WEST2001 | SHACKEIF | 0.2416 | -0.10997 | 1.4527 | -0.66126 |  | 69
WOOD | WOOD | 6204 | WOODSON2 | 0.468 |  |  |  | WEST2001 | THROCKMORTON | 0.25081 | -0.1113 | 0.11738 | -0.05209 |  | 69
THRM | THRM | 6205 | THROKMT2 | 2.727 |  |  |  | WEST2001 | THROCKMORTON | 0.2501 | -0.11115 | 0.68204 | -0.30311 |  | 69
BUKB | BUKB | 6206 | BUSHKNB2 | 2.448 |  |  |  | WEST2001 | THROCKMORTON | 0.24945 | -0.11101 | 0.61065 | -0.27175 |  | 69
ALBANY | ALBANY | 6207 | ALBANY 2 | 0.45 |  |  |  | WEST2001 | SHACKELFORD | 0.24547 | -0.11016 | 0.11046 | -0.04957 |  | 69
HUB1 | HUB1 | 6208 | WCTMWDT2 |  |  |  |  | WEST2001 | SHACKELFORD | 0.2469 | -0.11017 | 0 | 0 |  | 69
MRAN | MRAN | 6209 | MORAN 2 | 1.332 |  |  |  | WEST2001 | SHACKELFORD | 0.23463 | -0.10964 | 0.31252 | -0.14604 |  | 69
HUB2 | HUB2 | 6210 | WCTMWD22 | 0.783 |  |  |  | WEST2001 | SHACKELFORD | 0.25049 | -0.11019 | 0.19613 | -0.086277 |  | 69
PHAN | PHAN | 6211 | ALBANYT2 |  |  |  |  | WEST2001 | SHACKELFORD | 0.25831 | -0.11024 | 0 | 0 |  | 69
HUB1 | HUB1 | 6212 | WCTMWD12 | 0.657 |  |  |  | WEST2001 | SHACKELFORD | 0.2469 | -0.11017 | 0.16221 | -0.072379 |  | 69
HUB1_TAP | HUB1_TAP | 6213 | WCTMWDT |  |  |  |  | WEST2001 | SHACKELFORD | 0.24356 | -0.11007 | 0 | 0 |  | 69
HUB2 | HUB2 | 6214 | ALBANYT1 |  |  |  |  | WEST2001 | SHACKELFORD | 0.2469 | -0.11017 | 0 | 0 |  | 69
ABRP | ABRP | 6215 | ABRBRSN2 |  |  |  |  | WEST2001 | JONES | 0.26051 | -0.11025 | 0 | 0 |  | 69
FTFP | FTFP | 6217 | FTPHPMP2 | 1.134 |  |  |  | WEST2001 | JONES | 0.25931 | -0.11024 | 0.29406 | -0.12501 |  | 69
NUGE | NUGE | 6218 | NUGENTR2 | 1.958 |  |  |  | WEST2001 | JONES | 0.25831 | -0.11024 | 0.50578 | -0.21584 |  | 69
NUGE | NUGE | 6219 | NUGENTT2 |  |  |  |  | WEST2001 | JONES | 0.25831 | -0.11024 | 0 | 0 |  | 69
FTFP | FTFP | 6220 | FTPHPMT2 |  |  |  |  | WEST2001 | JONES | 0.25931 | -0.11024 | 0 | 0 |  | 69
ABRC | ABRC | 6221 | ABRAINY2 |  |  |  |  | WEST2001 | TAYLOR | 0.26265 | -0.11026 | 0 | 0 |  | 69
FTPP | FTPP | 6222 | PHATM W4 |  |  |  |  | WEST2001 | JONES | 0.26455 | -0.11032 | 0 | 0 |  | 138
ABRC | ABRC | 6223 | ABRAINY4 | 11.926 |  |  |  | WEST2001 | TAYLOR | 0.26653 | -0.11036 | 3.1787 | -1.3162 |  | 138
ABNW | ABNW | 6224 | ABILNW 2 |  |  |  |  | WEST2001 | TAYLOR | 0.26506 | -0.11043 | 0 | 0 |  | 69
ABNW | ABNW | 6225 | ABLNW2 2 |  |  |  |  | WEST2001 | TAYLOR | 0.2664 | -0.11028 | 0 | 0 |  | 69
ABNW | ABNW | 6226 | ABEASTP |  |  |  |  | WEST2001 | TALYOR | 0.26311 | -0.11014 | 0 | 0 |  | 138
ABNW | ABNW | 6228 | ABILNW14 |  |  |  |  | WEST2001 | TAYLOR | 0.26813 | -0.1104 | 0 | 0 |  | 138
ABMB | ABMB | 6230 | ABMULCE7 |  |  |  |  | WEST2001 | JONES | 0.28173 | -0.11135 | 0 | 0 |  | 345
ABMB | ABMB | 6231 | ABMULC24 |  |  |  |  | WEST2001 | JONES | 0.27244 | -0.11073 | 0 | 0 |  | 138
ABMB | ABMB | 6232 | ABMULCK4 |  |  |  |  | WEST2001 | JONES | 0.27056 | -0.11057 | 0 | 0 |  | 138
|  | 6234 | AMCWDUM |  |  |  |  | WEST2001 | JONES | 0.27039 | -0.11058 | 0 | 0 |  | 250
ABMB | ABMB | 6235 | ABMULCW7 |  |  |  |  | WEST2001 | JONES | 0.28141 | -0.11139 | 0 | 0 |  | 345
ABON | ABON | 6236 | ONYXREA2 | 1.206 |  |  |  | WEST2001 | JONES | 0.26545 | -0.11057 | 0.32013 | -0.13334 |  | 69
ONYS | ONYS | 6237 | CLRGKTP2 | 6.058 |  |  |  | WEST2001 | JONES | 0.26562 | -0.11062 | 1.6091 | -0.67016 |  | 69
EXHA | EXHA | 6238 | HAWEXTP2 |  |  |  |  | WEST2001 | JONES | 0.26624 | -0.11083 | 0 | 0 |  | 69
ABVO | ABVO | 6239 | EASTVGT2 |  |  |  |  | WEST2001 | TAYLOR | 0.26433 | -0.11038 | 0 | 0 |  | 69
ABVO | ABVO | 6240 | EASTVGL2 | 13.664 |  |  |  | WEST2001 | TAYLOR | 0.26433 | -0.11038 | 3.6118 | -1.5083 |  | 69
ELYT | ELYT | 6241 | ELYTAP 2 |  |  |  |  | WEST2001 | TAYLOR | 0.2683 | -0.11045 | 0 | 0 |  | 69
MERK | MERK | 6242 | MERKEL 2 | 4.303 |  |  |  | WEST2001 | TAYLOR | 0.26936 | -0.11055 | 1.159 | -0.47568 |  | 69
CLFK | CLFK | 6243 | CLRFKPM |  |  |  |  | WEST2001 | JONES | 0.25831 | -0.11024 | 0 | 0 |  | 69
ABVT | ABVT | 6244 | ABWALTP2 |  |  |  |  | WEST2001 | TAYLOR | 0.26343 | -0.11032 | 0 | 0 |  | 69
|  | 6245 | ABRBPRS2 | 5.752 |  |  |  | WEST2001 | JONES | 0.26051 | -0.11025 | 1.4985 | -0.63415 |  | 69
MKLT | MKLT | 6246 | SCOTTR 2 |  |  |  |  | WEST2001 | TAYLOR | 0.27034 | -0.11064 | 0 | 0 |  | 69
TRNT | TRNT | 6247 | TRENT 2 | 2.425 |  |  |  | WEST2001 | TAYLOR | 0.27101 | -0.1107 | 0.65719 | -0.26844 |  | 69
EXHA | EXHA | 6248 | HAWEXXN2 | 2.304 |  |  |  | WEST2001 | JONES | 0.26624 | -0.11083 | 0.61341 | -0.25536 |  | 69
DELT | DELT | 6249 | DELKREA2 |  |  |  |  | WEST2001 | JONES | 0.26574 | -0.11066 | 0 | 0 |  | 69
|  | 6250 | DELK 2 | 5.253 |  |  |  | WEST2001 | JONES | 0.26574 | -0.11066 | 1.3959 | -0.58132 |  | 69
|  | 6251 | ELY9 | 11.464 |  |  |  | WEST2001 | TAYLOR | 0.2683 | -0.11045 | 3.0757 | -1.2662 |  | 69
|  | 6252 | SCOTT9 | 1.776 |  |  |  | WEST2001 | TAYLO | 0.27034 | -0.11064 | 0.48013 | -0.19649 |  | 69
ABEC | ABEC | 6253 | ABELMCK2 |  |  |  |  | WEST2001 | TAYLOR | 0.2649 | -0.11016 | 0 | 0 |  | 69
ABEC | ABEC | 6255 | ABELMCK4 | 25.419 |  |  |  | WEST2001 | TAYLOR | 0.2681 | -0.11041 | 6.8148 | -2.8064 |  | 138
ABTT | ABTT | 6256 | ABTWILT4 | 12.17 |  |  |  | WEST2001 | TAYLOR | 0.26507 | -0.11019 | 3.2259 | -1.3411 |  | 138
ABRL | ABRL | 6257 | ABREBLN4 | 14.519 |  |  |  | WEST2001 | TAYLOR | 0.26388 | -0.11011 | 3.8313 | -1.5987 |  | 138
ABSO | ABSO | 6258 | ABSOUTH2 |  |  |  |  | WEST2001 | TAYLOR | 0.26085 | -0.10965 | 0 | 0 |  | 69
ABSO | ABSO | 6260 | ABSOUTH4 |  |  |  |  | WEST2001 | TAYLOR | 0.26145 | -0.10994 | 0 | 0 |  | 138
WYLE | WYLE | 6261 | ABWYLIE4 | 11.755 |  |  |  | WEST2001 | TAYLOR | 0.26253 | -0.11002 | 3.086 | -1.2932 |  | 138
ABD2 | ABD2 | 6265 | ABDYES22 | 5.059 |  |  |  | WEST2001 | TAYLOR | 0.26415 | -0.11006 | 1.3363 | -0.55681 |  | 69
ARNT | ARNT | 6266 | ABDYTP22 |  |  |  |  | WEST2001 | TAYLOR | 0.26415 | -0.11006 | 0 | 0 |  | 69
ABHT | ABHT | 6267 | ABHARTF2 | 13.205 |  |  |  | WEST2001 | TAYLOR | 0.2635 | -0.10998 | 3.4795 | -1.4523 |  | 69
ABHT | ABHT | 6268 | ABDYTP12 |  |  |  |  | WEST2001 | TAYLOR | 0.26296 | -0.10991 | 0 | 0 |  | 69
ABD1 | ABD1 | 6269 | ABDYES12 | 3.483 |  |  |  | WEST2001 | TAYLOR | 0.26296 | -0.10991 | 0.91588 | -0.38283 |  | 69
ABSH | ABSH | 6270 | ABSHLTN2 | 24.87 |  |  |  | WEST2001 | TAYLOR | 0.2632 | -0.11006 | 6.5459 | -2.7373 |  | 69
ABMM | ABMM | 6271 | ABMCMRY2 | 24.51 |  |  |  | WEST2001 | TAYLOR | 0.26234 | -0.10998 | 6.4301 | -2.6955 |  | 69
ABOV | ABOV | 6272 | ABOVER 2 | 13.556 |  |  |  | WEST2001 | TAYLOR | 0.26163 | -0.1099 | 3.5467 | -1.4898 |  | 69
ABD1 | ABD1 | 6273 | ABDYTP32 |  |  |  |  | WEST2001 | TAYLOR | 0.26296 | -0.10991 | 0 | 0 |  | 69
ABD3 | ABD3 | 6274 | ABDYES32 | 4.87 |  |  |  | WEST2001 | TAYLOR | 0.26296 | -0.10991 | 1.2806 | -0.53528 |  | 69
ABEA | ABEA | 6275 | ABEAST24 | 10.747 |  |  |  | WEST2001 | TAYLOR | 0.26257 | -0.1101 | 2.8218 | -1.1832 |  | 138
ABEA | ABEA | 6276 | ABEAST12 |  |  |  |  | WEST2001 | TAYLOR | 0.26284 | -0.11015 | 0 | 0 |  | 69
ABEA | ABEA | 6277 | ABEAST22 |  |  |  |  | WEST2001 | TAYLOR | 0.26012 | -0.1099 | 0 | 0 |  | 69
ABPLTTP2 | ABPLTTP2 | 6278 | ABPLTTP2 |  |  |  |  | WEST2001 | TALYOR | 0.26295 | -0.11013 | 0 | 0 |  | 69
ABWA | ABWA | 6281 | ABWALN 2 | 11.359 |  |  |  | WEST2001 | TAYLOR | 0.26284 | -0.11015 | 2.9856 | -1.2512 |  | 69
ABPG | ABPG | 6282 | ABILPLT2 | 14.663 | 18 |  |  | WEST2001 | TAYLOR | 0.2596 | -0.10985 | 8.4794 | -3.5881 |  | 69
ABOM | ABOM | 6283 | ABOLMLT2 |  |  |  |  | WEST2001 | TAYLOR | 0.25977 | -0.10983 | 0 | 0 |  | 69
ABWG | ABWG | 6284 | ABWTGUT2 |  |  |  |  | WEST2001 | TAYLOR | 0.2605 | -0.10971 | 0 | 0 |  | 69
ABWG | ABWG | 6285 | ABWTXGU2 | 0.027 |  |  |  | WEST2001 | TAYLOR | 0.2605 | -0.10971 | 0.0070335 | -0.0029621 |  | 69
ABOM | ABOM | 6286 | ABOILML2 | 4.726 |  |  |  | WEST2001 | TAYLOR | 0.25977 | -0.10983 | 1.2277 | -0.51904 |  | 69
ABMS | ABMS | 6290 | ABMAPLE4 | 11.404 |  |  |  | WEST2001 | TAYLOR | 0.26203 | -0.11002 | 2.9882 | -1.2547 |  | 138
AILN | AILN | 6291 | ABAILEN4 | 8.569 |  |  |  | WEST2001 | TAYLOR | 0.26308 | -0.11015 | 2.2543 | -0.94391 |  | 138
ABCC | ABCC | 6292 | ABCOCLB4 | 10.576 |  |  |  | WEST2001 | TAYLOR | 0.26207 | -0.11002 | 2.7716 | -1.1635 |  | 138
ABCR | ABCR | 6293 | ABCNYRK4 | 9.667 |  |  |  | WEST2001 | TAYLOR | 0.26182 | -0.10999 | 2.531 | -1.0632 |  | 138
SARC | SARC | 6294 | SRC1DUM |  |  |  |  | WEST2001 | TOM GREEN | 0.27086 | -0.10857 | 0 | 0 |  | 100
SARC | SARC | 6295 | SRC1TERT |  |  |  |  | WEST2001 | TOM GREEN | 0.27086 | -0.10857 | 0 | 0 |  | 13.2
WTU_DETP | WTU-DETP | 6300 | DENTONR2 | 5.222 |  |  |  | WEST2001 | CALLAHAN | 0.25114 | -0.10969 | 1.3114 | -0.57281 |  | 69
ABED | ABED | 6301 | ABELMDL2 | 2.835 |  |  |  | WEST2001 | TAYLOR | 0.25442 | -0.10975 | 0.72128 | -0.31115 |  | 69
CLYM | CLYM | 6302 | CLYDMGT2 |  |  |  |  | WEST2001 | CALLAHAN | 0.25114 | -0.10969 | 0 | 0 |  | 69
WTU_DETP | WTU-DETP | 6303 | DENTONT2 |  |  |  |  | WEST2001 | CALLAHAN | 0.25114 | -0.10969 | 0 | 0 |  | 69
CLYM | CLYM | 6304 | CLYDMAG2 | 1.737 |  |  |  | WEST2001 | CALLAHAN | 0.25114 | -0.10969 | 0.43622 | -0.19053 |  | 69
CLYD | CLYD | 6305 | CLYDE 2 | 8.718 |  |  |  | WEST2001 | CALLAHAN | 0.24549 | -0.10958 | 2.1402 | -0.95535 |  | 69
BAIR | BAIR | 6306 | BAIRD 2 | 3.105 |  |  |  | WEST2001 | CALLAHAN | 0.23805 | -0.10944 | 0.73915 | -0.33981 |  | 69
PUTN | PUTN | 6307 | PUT138 2 |  |  |  |  | WEST2001 | CALLAHAN | 0.22542 | -0.1092 | 0 | 0 |  | 69
PUTN | PUTN | 6309 | PUTNAM 4 |  |  |  |  | WEST2001 | CALLAHAN | 0.21975 | -0.10963 | 0 | 0 |  | 138
PUTT | PUTT | 6310 | PUTTAP 4 |  |  |  |  | WEST2001 | CALLAHAN | 0.21933 | -0.10966 | 0 | 0 |  | 138
CISC | CISC | 6311 | CISCO 2 | 8.398 |  |  |  | WEST2001 | EASTLAND | 0.2063 | -0.10941 | 1.7325 | -0.91883 |  | 69
PUTM | PUTM | 6312 | PUT69 2 | 3.051 |  |  |  | WEST2001 | CALLAHAN | 0.22568 | -0.10909 | 0.68855 | -0.33284 |  | 69
CHAD | CHAD | 6324 | FTCHAD | 3.522 |  |  |  | WEST2001 | COKE | 0.25442 | -0.1061 | 0.89607 | -0.3737 |  | 138
CHAD | CHAD | 6325 | FTCHADTP |  |  |  |  | WEST2001 | COKE | 0.25442 | -0.1061 | 0 | 0 |  | 138
ROBT | ROBT | 6326 | ROBRTSR2 | 4.753 |  |  |  | WEST2001 | TAYLOR | 0.25833 | -0.10879 | 1.2278 | -0.51706 |  | 69
ABCG | ABCG | 6327 | CEDARGP2 | 2.268 |  |  |  | WEST2001 | TAYLOR | 0.2589 | -0.10898 | 0.58719 | -0.24717 |  | 69
TUSC | TUSC | 6328 | TUSCOLA2 | 10.079 |  |  |  | WEST2001 | TAYLOR | 0.25466 | -0.10753 | 2.5667 | -1.0838 |  | 69
|  | 6329 | GLDBSK9 | 2.759 |  |  |  | WEST2001 | COLEMAN | 0.23776 | -0.10328 | 0.65597 | -0.28494 |  | 69
HAPV | HAPV | 6330 | HAPVAL2 | 1.574 |  |  |  | WEST2001 | TAYLOR | 0.24962 | -0.1058 | 0.3929 | -0.16653 |  | 69
CLIM | CLIM | 6331 | BRADSHW2 | 0.081 |  |  |  | WEST2001 | TAYLOR | 0.24965 | -0.10581 | 0.020221 | -0.0085705 |  | 69
HAPV | HAPV | 6332 | HAPVALT2 |  |  |  |  | WEST2001 | TAYLOR | 0.24962 | -0.1058 | 0 | 0 |  | 69
WINT | WINT | 6333 | WINTERS2 | 9.529 |  |  |  | WEST2001 | RUNNELS | 0.24423 | -0.10395 | 2.3273 | -0.99054 |  | 69
HATC | HATC | 6334 | HATCHLR2 | 2.917 |  |  |  | WEST2001 | RUNNELS | 0.23821 | -0.10188 | 0.69485 | -0.2972 |  | 69
OAKC | OAKC | 6335 | OAKCK1 4 |  |  |  |  | WEST2001 | COKE | 0.25443 | -0.10613 | 0 | 0 |  | 138
|  | 6336 | MECSNYDR | 0.652 |  |  |  | WEST2001 | SCURRY | 0.28541 | -0.11163 | 0.18609 | -0.072785 |  | 69
HUMB | HUMB | 6337 | BALEXXN2 | 0.072 |  |  |  | WEST2001 | RUNNELS | 0.2359 | -0.10146 | 0.016985 | -0.0073049 |  | 69
BALG | BALG | 6338 | BALNGR 2 | 9.19 |  |  |  | WEST2001 | RUNNELS | 0.23532 | -0.10089 | 2.1626 | -0.92722 |  | 69
BALG | BALG | 6340 | BALNGR 4 |  |  |  |  | WEST2001 | RUNNELS | 0.24505 | -0.10338 | 0 | 0 |  | 138
HUMB | HUMB | 6341 | BALEXTP2 |  |  |  |  | WEST2001 | RUNNELS | 0.2359 | -0.10146 | 0 | 0 |  | 69
NOVC | NOVC | 6342 | NOVICER2 |  |  |  |  | WEST2001 | COLEMAN | 0.23673 | -0.10227 | 0 | 0 |  | 69
ATTA | ATTA | 6343 | TALPATL2 | 2.294 |  |  |  | WEST2001 | COLEMAN | 0.23701 | -0.10255 | 0.5437 | -0.23524 |  | 69
VALE | VALE | 6344 | VALEREX2 | 0.18 |  |  |  | WEST2001 | COLEMAN | 0.23744 | -0.10296 | 0.042738 | -0.018533 |  | 69
GLSB | GLSB | 6345 | GLDBSKR2 |  |  |  |  | WEST2001 | COLEMAN | 0.23776 | -0.10328 | 0 | 0 |  | 69
COLJ | COLJ | 6346 | COLJNC 2 |  |  |  |  | WEST2001 | COLEMAN | 0.238 | -0.10352 | 0 | 0 |  | 69
ECOLEMAN | ECOLEMAN | 6347 | COLETAP4 |  |  |  |  | WEST2001 | COLEMAN | 0.24215 | -0.10366 | 0 | 0 |  | 138
ECOLEMAN | ECOLEMAN | 6348 | COLEMAN4 | 7.992 |  |  |  | WEST2001 | COLEMAN | 0.24215 | -0.10366 | 1.9353 | -0.82843 |  | 138
|  | 6349 | NOVICE9 | 3.059 |  |  |  | WEST2001 | COLEMAN | 0.23673 | -0.10227 | 0.72416 | -0.31285 |  | 69
|  | 6350 | DRESSY9 | 1.379 |  |  |  | WEST2001 | CALLAHAN | 0.23101 | -0.10698 | 0.31856 | -0.14753 |  | 69
SANA | SANA | 6353 | SANANNA2 | 3.609 |  |  |  | WEST2001 | COLEMAN | 0.23851 | -0.10401 | 0.86077 | -0.37537 |  | 69
SANA | SANA | 6355 | SANANNA4 |  |  |  |  | WEST2001 | COLEMAN | 0.24167 | -0.1037 | 0 | 0 |  | 138
DRSY | DRSY | 6356 | DRESSYR2 |  |  |  |  | WEST2001 | CALLAHAN | 0.23101 | -0.10698 | 0 | 0 |  | 69
CRPL | CRPL | 6357 | CROSSPL2 | 4.609 |  |  |  | WEST2001 | CALLAHAN | 0.23066 | -0.10712 | 1.0631 | -0.49372 |  | 69
RIST | RIST | 6358 | RISNGST2 | 3.195 |  |  |  | WEST2001 | EASTLAND | 0.23066 | -0.10712 | 0.73696 | -0.34225 |  | 69
PTRK | PTRK | 6369 | PTROCK 2 | 0.873 |  |  |  | WEST2001 | CONCHO | 0.20028 | -0.091034 | 0.17485 | -0.079473 |  | 69
EOLA | EOLA | 6370 | EOLATAP2 |  |  |  |  | WEST2001 | CONCHO | 0.19826 | -0.090465 | 0 | 0 |  | 69
EOLA | EOLA | 6371 | EOLA 2 | 3.262 |  |  |  | WEST2001 | CONCHO | 0.19826 | -0.090465 | 0.64673 | -0.2951 |  | 69
EDEN | EDEN | 6372 | EDEN 2 | 2.934 |  |  |  | WEST2001 | CONCHO | 0.15536 | -0.078391 | 0.45583 | -0.23 |  | 69
MENA | MENA | 6373 | MENARD 2 | 5.268 |  |  |  | WEST2001 | MENARD | 0.13667 | -0.072966 | 0.71997 | -0.38438 |  | 69
MENA | MENA | 6375 | MENARD 4 |  |  |  |  | WEST2001 | MENARD | 0.14445 | -0.074771 | 0 | 0 |  | 138
CRM1 | CRM1 | 6376 | CRMW1TP2 |  |  |  |  | WEST2001 | CONCHO | 0.16695 | -0.081653 | 0 | 0 |  | 69
CRM1 | CRM1 | 6377 | CRMWD1 2 | 4.878 |  |  |  | WEST2001 | CONCHO | 0.16695 | -0.081653 | 0.81438 | -0.3983 |  | 69
MELV | MELV | 6380 | MELVIN 2 | 1.19 |  |  |  | WEST2001 | MCCULLOCH | 0.13977 | -0.074124 | 0.16632 | -0.088208 |  | 69
MCLC | MCLC | 6384 | EDENRTP2 |  |  |  |  | WEST2001 | CONCHO | 0.15093 | -0.07718 | 0 | 0 |  | 69
MCLC | MCLC | 6385 | EDENREA2 | 2.55 |  |  |  | WEST2001 | CONCHO | 0.15093 | -0.07718 | 0.38488 | -0.19681 |  | 69
VRBS | VRBS | 6409 | VERIBST9 |  |  |  |  | WEST2001 | VERIBEST | 0.23896 | -0.10025 | 0 | 0 |  | 69
MILE | MILE | 6410 | MILES 2 | 1.188 |  |  |  | WEST2001 | RUNNELS | 0.23952 | -0.10114 | 0.28456 | -0.12015 |  | 69
ROWE | ROWE | 6411 | ROWENA 2 | 5.717 |  |  |  | WEST2001 | RUNNELS | 0.23755 | -0.10102 | 1.3581 | -0.57754 |  | 69
HARI | HARI | 6412 | HARRIET2 | 7.973 |  |  |  | WEST2001 | TOM GREEN | 0.23929 | -0.10077 | 1.9079 | -0.80346 |  | 69
VRBS | VRBS | 6413 | VERIBST2 | 4.81 |  |  |  | WEST2001 | TOM GREEN | 0.23896 | -0.10025 | 1.1494 | -0.4822 |  | 69
BRNT | BRNT | 6414 | BRONTE 2 | 3.629 |  |  |  | WEST2001 | COKE | 0.24528 | -0.10272 | 0.89012 | -0.37275 |  | 69
|  | 6416 | GRAPETP2 |  |  |  |  | WEST2001 | IRION | 0.24402 | -0.10147 | 0 | 0 |  | 69
|  | 6417 | STRLNG9 | 3.169 |  |  |  | WEST2001 | STERLING | 0.25933 | -0.10561 | 0.82182 | -0.33468 |  | 69
ATBR | ATBR | 6418 | BRNTATL2 | 0.639 |  |  |  | WEST2001 | COKE | 0.24393 | -0.10234 | 0.15587 | -0.065398 |  | 69
AMBR | AMBR | 6419 | BRNTAMB2 | 0.702 |  |  |  | WEST2001 | COKE | 0.24672 | -0.10311 | 0.1732 | -0.072383 |  | 69
ROBL | ROBL | 6420 | ROBLEE 2 | 4.492 |  |  |  | WEST2001 | COKE | 0.24813 | -0.1035 | 1.1146 | -0.46491 |  | 69
SPEN | SPEN | 6421 | ESPENCT2 |  |  |  |  | WEST2001 | COKE | 0.25075 | -0.10422 | 0 | 0 |  | 69
EDIT | EDIT | 6422 | EDITH 2 | 2.124 |  |  |  | WEST2001 | COKE | 0.25076 | -0.10422 | 0.53261 | -0.22136 |  | 69
CEDH | CEDH | 6423 | CDRHILL2 |  |  |  |  | WEST2001 | COKE | 0.25385 | -0.10507 | 0 | 0 |  | 69
CEDH | CEDH | 6425 | CDRHILL4 |  |  |  |  | WEST2001 | COKE | 0.25422 | -0.10573 | 0 | 0 |  | 138
SPEN | SPEN | 6426 | ESPENCE2 |  |  |  |  | WEST2001 | COKE | 0.25075 | -0.10422 | 0 | 0 |  | 69
SILR | SILR | 6427 | SILVERR2 | 0.914 |  |  |  | WEST2001 | COKE | 0.25387 | -0.10507 | 0.23203 | -0.096034 |  | 69
SILR | SILR | 6428 | SILVERR2 | 2.061 |  |  |  | WEST2001 | COKE | 0.25387 | -0.10507 | 0.52322 | -0.21655 |  | 69
SPRH | SPRH | 6429 | SPADERN2 |  |  |  |  | WEST2001 | STERLING | 0.25506 | -0.10516 | 0 | 0 |  | 69
SILV | SILV | 6430 | SILVER 2 |  |  |  |  | WEST2001 | COKE | 0.25387 | -0.10507 | 0 | 0 |  | 69
SILT | SILT | 6431 | SILVRTP2 |  |  |  |  | WEST2001 | COKE | 0.25393 | -0.10507 | 0 | 0 |  | 69
EXPE | EXPE | 6432 | PERKINS2 | 0.252 |  |  |  | WEST2001 | COKE | 0.25427 | -0.1051 | 0.064077 | -0.026485 |  | 69
SPRH | SPRH | 6433 | SPADRNT2 |  |  |  |  | WEST2001 | STERLING | 0.25506 | -0.10516 | 0 | 0 |  | 69
PANA | PANA | 6434 | PANAMRC2 |  |  |  |  | WEST2001 | STERLING | 0.25537 | -0.10518 | 0 | 0 |  | 69
STER | STER | 6435 | STRCITY2 | 2.916 |  |  |  | WEST2001 | STERLING | 0.25827 | -0.1054 | 0.75313 | -0.30733 |  | 69
STCO | STCO | 6436 | STRLGCO2 |  |  |  |  | WEST2001 | STERLING | 0.25933 | -0.10561 | 0 | 0 |  | 69
SAGT | SAGT | 6437 | CRBDTP 2 |  |  |  |  | WEST2001 | TOM GREEN | 0.23971 | -0.1003 | 0 | 0 |  | 69
CBRT | CBRT | 6438 | CBDREA 2 | 4.613 |  |  |  | WEST2001 | TOM GREEN | 0.23971 | -0.1003 | 1.1058 | -0.46268 |  | 69
AMCO | AMCO | 6439 | AMOCOTP2 |  |  |  |  | WEST2001 | TOM GREEN | 0.2507 | -0.10331 | 0 | 0 |  | 69
AMCO | AMCO | 6440 | AMOCO 2 |  |  |  |  | WEST2001 | STERLING | 0.2507 | -0.10331 | 0 | 0 |  | 69
ORNT | ORNT | 6441 | ORIENTR4 | 2.192 |  |  |  | WEST2001 | TOM GREEN | 0.25024 | -0.10381 | 0.54853 | -0.22755 |  | 138
SARC | SARC | 6442 | SAREDCK4 |  |  |  |  | WEST2001 | TOM GREEN | 0.24862 | -0.10291 | 0 | 0 |  | 138
SARC | SARC | 6444 | SAREDCK7 |  |  |  |  | WEST2001 | TOM GREEN | 0.26109 | -0.10609 | 0 | 0 |  | 345
CRM5 | CRM5 | 6445 | CRMW5TP2 |  |  |  |  | WEST2001 | STERLING | 0.25759 | -0.10521 | 0 | 0 |  | 69
CRM5 | CRM5 | 6446 | CRMWD5 2 | 3.158 |  |  |  | WEST2001 | STERLING | 0.25759 | -0.10521 | 0.81348 | -0.33225 |  | 69
PAULANN | PAULANN | 6447 | SAPLANN4 | 11.593 |  |  |  | WEST2001 | TOM GREEN | 0.24443 | -0.10168 | 2.8337 | -1.1788 |  | 138
SA_HILND | SA_HILND | 6448 | HIGHLAN4 | 13.727 |  |  |  | WEST2001 | TOM GREEN | 0.2408 | -0.10061 | 3.3054 | -1.3811 |  | 138
SACK | SACK | 6449 | SACOKE 4 | 8.587 |  |  |  | WEST2001 | TOM GREEN | 0.24206 | -0.10099 | 2.0786 | -0.86717 |  | 138
SACO | SACO | 6450 | SACONCH2 | 13.745 |  |  |  | WEST2001 | TOM GREEN | 0.23883 | -0.10005 | 3.2828 | -1.3752 |  | 69
SACO | SACO | 6452 | SACONCH4 |  |  |  |  | WEST2001 | TOM GREEN | 0.24064 | -0.10057 | 0 | 0 |  | 138
SAST | SAST | 6453 | SASOTAP4 |  |  |  |  | WEST2001 | TOM GREEN | 0.23864 | -0.099981 | 0 | 0 |  | 138
SASO | SASO | 6454 | SASOUTH4 | 11.188 |  |  |  | WEST2001 | TOM GREEN | 0.23864 | -0.099981 | 2.6699 | -1.1186 |  | 138
SASO | SASO | 6455 | SASOUTH2 | 9.154 |  |  |  | WEST2001 | TOM GREEN | 0.23843 | -0.099924 | 2.1826 | -0.9147 |  | 69
SAJS | SAJS | 6456 | SAJACKS2 | 17.057 |  |  |  | WEST2001 | TOM GREEN | 0.23855 | -0.099962 | 4.0689 | -1.705 |  | 69
SAEM | SAEM | 6457 | SAEMERS2 | 7.291 |  |  |  | WEST2001 | TOM GREEN | 0.23908 | -0.10012 | 1.7431 | -0.72998 |  | 69
CRM2 | CRM2 | 6458 | CRMWD2 | 4.519 |  |  |  | WEST2001 | TOM GREEN | 0.24714 | -0.1031 | 1.1168 | -0.46592 |  | 138
CRM3 | CRM3 | 6459 | CRMWD3 |  |  |  |  | WEST2001 | STERLING | 0.23971 | -0.1003 | 0 | 0 |  | 69
CRM4 | CRM4 | 6460 | CRMWDTP4 |  |  |  |  | WEST2001 | STERLING | 0.24828 | -0.10264 | 0 | 0 |  | 69
CRM4 | CRM4 | 6461 | CRMWD42 | 3.958 |  |  |  | WEST2001 | STERLING | 0.24828 | -0.10264 | 0.9827 | -0.40626 |  | 69
SANO | SANO | 6462 | SANORTH2 | 11.08 |  |  |  | WEST2001 | TOM GREEN | 0.23971 | -0.1003 | 2.6559 | -1.1113 |  | 69
SANO | SANO | 6464 | SANORTH4 |  |  |  |  | WEST2001 | TOM GREEN | 0.24231 | -0.10106 | 0 | 0 |  | 138
SAGC | SAGC | 6465 | GRAPECK2 | 7.516 |  |  |  | WEST2001 | TOM GREEN | 0.23971 | -0.1003 | 1.8016 | -0.75384 |  | 69
SAWT | SAWT | 6466 | SAWALTP2 |  |  |  |  | WEST2001 | TOM GREEN | 0.23951 | -0.10023 | 0 | 0 |  | 69
SAWA | SAWA | 6467 | SAWALN 2 | 13.088 |  |  |  | WEST2001 | TOM GREEN | 0.23951 | -0.10023 | 3.1347 | -1.3119 |  | 69
SACH | SACH | 6468 | SACHWST2 |  |  |  |  | WEST2001 | TOM GREEN | 0.23931 | -0.10017 | 0 | 0 |  | 69
SACH | SACH | 6470 | SACHWST4 | 23.745 |  |  |  | WEST2001 | TOM GREEN | 0.23742 | -0.099621 | 5.6376 | -2.3655 |  | 138
SAAN | SAAN | 6471 | SAAVE N2 | 13.241 |  |  |  | WEST2001 | TOM GREEN | 0.23903 | -0.10009 | 3.165 | -1.3253 |  | 69
BENF | BENF | 6473 | SABENFK4 | 8.2 |  |  |  | WEST2001 | TOM GREEN | 0.23816 | -0.099834 | 1.9529 | -0.81864 |  | 138
SAMF | SAMF | 6477 | SAMTFLD2 | 2.349 |  |  |  | WEST2001 | TOM GREEN | 0.23844 | -0.099736 | 0.5601 | -0.23428 |  | 69
SAPS | SAPS | 6478 | SAPS 2 |  |  |  |  | WEST2001 | TOM GREEN | 0.23825 | -0.09987 | 0 | 0 |  | 69
SAPS | SAPS | 6480 | SAPS1 4 |  |  |  |  | WEST2001 | TOM GREEN | 0.23568 | -0.099111 | 0 | 0 |  | 138
SASH | SASH | 6481 | SASLAND4 | 16.13 |  |  |  | WEST2001 | TOM GREEN | 0.23605 | -0.099218 | 3.8075 | -1.6004 |  | 138
SALD | SALD | 6482 | SALKDRV4 | 10.756 |  |  |  | WEST2001 | TOM GREEN | 0.24116 | -0.10072 | 2.5939 | -1.0833 |  | 138
|  | 6483 | SAPS2 4 |  |  |  |  | WEST2001 | TOM GREEN | 0.23571 | -0.099115 | 0 | 0 |  | 138
PAVE | PAVE | 6493 | PAVEPAW4 |  |  |  |  | WEST2001 | SCHLEICHER | 0.21803 | -0.093234 | 0 | 0 |  | 138
PAW2 | PAW2 | 6494 | PAVEPAW2 |  |  |  |  | WEST2001 | SCHLEICHER | 0.21871 | -0.093429 | 0 | 0 |  | 69
CRIS | CRIS | 6495 | CRISTOV2 | 2.412 |  |  |  | WEST2001 | TOM GREEN | 0.22815 | -0.096534 | 0.55029 | -0.23284 |  | 69
AROT | AROT | 6496 | ARROTT 2 | 1.427 |  |  |  | WEST2001 | SCHLEICHER | 0.22301 | -0.094843 | 0.31823 | -0.13534 |  | 69
HULD | HULD | 6497 | HULDALR2 | 1.529 |  |  |  | WEST2001 | SCHELICHER | 0.21954 | -0.0937 | 0.33567 | -0.14327 |  | 69
LVOK | LVOK | 6498 | LIVEOAK2 |  |  |  |  | WEST2001 | SCHLEICHER | 0.21368 | -0.091771 | 0 | 0 |  | 69
LVOK | LVOK | 6500 | LIVEOAK4 |  |  |  |  | WEST2001 | SCHLEICHER | 0.21389 | -0.091855 | 0 | 0 |  | 138
|  | 6503 | ELDSHBL2 |  |  |  |  | WEST2001 | SCHLEICHER | 0.2111 | -0.090918 | 0 | 0 |  | 69
ELDO | ELDO | 6505 | ELDORAD2 | 7 |  |  |  | WEST2001 | SCHLEICHER | 0.21253 | -0.091393 | 1.4877 | -0.63975 |  | 69
PAGE | PAGE | 6506 | ELDCSER2 | 0.367 |  |  |  | WEST2001 | SCHLEICHER | 0.21253 | -0.091393 | 0.078 | -0.033541 |  | 69
MIDV | MIDV | 6507 | MIDVALY2 | 0.474 |  |  |  | WEST2001 | SCHLEICHER | 0.21253 | -0.091393 | 0.10074 | -0.04332 |  | 69
FMCK | FMCK | 6508 | FTMCKAV2 | 0.567 |  |  |  | WEST2001 | SCHLEICHER | 0.21253 | -0.091393 | 0.12051 | -0.05182 |  | 69
SHBA | SHBA | 6509 | ELDSHEL2 | 0.027 |  |  |  | WEST2001 | SCHELICHER | 0.2111 | -0.090918 | 0.0056997 | -0.0024548 |  | 69
SONO | SONO | 6510 | SNRCITY2 | 2.403 |  |  |  | WEST2001 | SUTTON | 0.20102 | -0.087577 | 0.48304 | -0.21045 |  | 69
ATSO | ATSO | 6511 | SONORAT2 | 0.572 |  |  |  | WEST2001 | SUTTON | 0.20669 | -0.089164 | 0.11823 | -0.051002 |  | 69
SONR | SONR | 6513 | SONORA 2 | 1.332 |  |  |  | WEST2001 | SUTTON | 0.20058 | -0.087433 | 0.26717 | -0.11646 |  | 69
SONR | SONR | 6515 | SONORA 4 |  |  |  |  | WEST2001 | SUTTON | 0.2014 | -0.087706 | 0 | 0 |  | 138
|  | 6524 | MERTZON9 | 1.766 |  |  |  | WEST2001 | MASON | 0.23756 | -0.099028 | 0.41954 | -0.17488 |  | 69
MERR | MERR | 6526 | MERTZNR2 |  |  |  |  | WEST2001 | IRION | 0.23756 | -0.099028 | 0 | 0 |  | 69
SANW | SANW | 6527 | NSWTHYR2 | 5.277 |  |  |  | WEST2001 | TOM GREEN | 0.23526 | -0.098875 | 1.2415 | -0.52177 |  | 69
TANK | TANK | 6528 | TNKRSLY2 | 3.718 |  |  |  | WEST2001 | IRION | 0.23806 | -0.09943 | 0.88512 | -0.36968 |  | 69
MERT | MERT | 6529 | MERTZON2 | 3.08 |  |  |  | WEST2001 | IRION | 0.2376 | -0.09906 | 0.73182 | -0.3051 |  | 69
PHBA | PHBA | 6530 | BARNHAR2 |  |  |  |  | WEST2001 | IRION | 0.23669 | -0.09832 | 0 | 0 |  | 69
PHBA | PHBA | 6531 | BRNHRPH2 | 0.009 |  |  |  | WEST2001 | IRION | 0.23695 | -0.098532 | 0.0021326 | -0.00088679 |  | 69
BARN | BARN | 6532 | BARNHCV2 | 0.894 |  |  |  | WEST2001 | IRION | 0.23673 | -0.098354 | 0.21164 | -0.087928 |  | 69
BGLK | BGLK | 6533 | BIGLAKE2 | 7.286 |  |  |  | WEST2001 | REAGAN | 0.23603 | -0.097787 | 1.7197 | -0.71247 |  | 69
BGLK | BGLK | 6535 | BIGLAKE4 |  |  |  |  | WEST2001 | REAGAN | 0.23577 | -0.097733 | 0 | 0 |  | 138
BGLK | BGLK | 6536 | BIGLAK24 |  |  |  |  | WEST2001 | REAGAN | 0.23577 | -0.097727 | 0 | 0 |  | 138
TEXN | TEXN | 6538 | TEXON 2 | 3.997 |  |  |  | WEST2001 | REAGAN | 0.23993 | -0.098746 | 0.95902 | -0.39469 |  | 69
SHPO | SHPO | 6539 | SHELPOW2 |  |  |  |  | WEST2001 | REAGAN | 0.23861 | -0.09842 | 0 | 0 |  | 69
SHPO | SHPO | 6540 | SHLPOWT2 |  |  |  |  | WEST2001 | REAGAN | 0.23861 | -0.09842 | 0 | 0 |  | 69
TEXT | TEXT | 6541 | TEXONTP2 |  |  |  |  | WEST2001 | REAGAN | 0.24144 | -0.099117 | 0 | 0 |  | 69
ATLT | ATLT | 6542 | ATLBSTT2 |  |  |  |  | WEST2001 | REAGAN | 0.23993 | -0.098746 | 0 | 0 |  | 69
EXKE | EXKE | 6543 | KEMPEXT2 |  |  |  |  | WEST2001 | REAGAN | 0.23846 | -0.098385 | 0 | 0 |  | 69
HUMB | HUMB | 6544 | POWELTP2 |  |  |  |  | WEST2001 | REAGAN | 0.23861 | -0.09842 | 0 | 0 |  | 69
POWF | POWF | 6545 | POWLFLD2 | 1.728 |  |  |  | WEST2001 | CROCKETT | 0.23861 | -0.09842 | 0.41231 | -0.17007 |  | 69
PHBL | PHBL | 6546 | BGLKPHT2 |  |  |  |  | WEST2001 | REAGAN | 0.23337 | -0.09698 | 0 | 0 |  | 69
STRS | STRS | 6547 | STRSRNR2 | 1.687 |  |  |  | WEST2001 | CROCKETT | 0.23238 | -0.096677 | 0.39202 | -0.16309 |  | 69
POWT | POWT | 6548 | POWFLDT2 |  |  |  |  | WEST2001 | CROCKETT | 0.23062 | -0.096143 | 0 | 0 |  | 69
MIDW | MIDW | 6549 | MIDWYLN2 | 13.504 |  |  |  | WEST2001 | CROCKETT | 0.22732 | -0.095139 | 3.0697 | -1.2848 |  | 69
FDRAN | FDRAN | 6550 | FDRAN 2 | 0.651 |  |  |  | WEST2001 | CROCKETT | 0.21882 | -0.092604 | 0.14245 | -0.060285 |  | 69
OZNR | OZNR | 6551 | OZONARE2 | 0.651 |  |  |  | WEST2001 | CROCKETT | 0.22042 | -0.092972 | 0.14349 | -0.060525 |  | 69
OZNC | OZNC | 6552 | CROCKHT2 | 0.576 |  |  |  | WEST2001 | CROCKETT | 0.21742 | -0.092208 | 0.12524 | -0.053112 |  | 69
PHBL | PHBL | 6553 | BGLKPHL2 |  |  |  |  | WEST2001 | REAGAN | 0.23337 | -0.09698 | 0 | 0 |  | 69
EXKE | EXKE | 6554 | KEMPEXX2 | 0.054 |  |  |  | WEST2001 | REAGAN | 0.23846 | -0.098385 | 0.012877 | -0.0053128 |  | 69
ATLB | ATLB | 6555 | ATLBEST2 | 0.018 |  |  |  | WEST2001 | REAGAN | 0.23993 | -0.098746 | 0.0043188 | -0.0017774 |  | 69
YATT | YATT | 6556 | WIRAAN 2 |  |  |  |  | WEST2001 | PECOS | 0.25039 | -0.10105 | 0 | 0 |  | 69
OZNA | OZNA | 6560 | OZONA 2 | 8.56 |  |  |  | WEST2001 | CROCKETT | 0.22 | -0.092915 | 1.8832 | -0.79535 |  | 69
FDRAN | FDRAN | 6562 | FDRAN 4 |  |  |  |  | WEST2001 | CROCKETT | 0.21864 | -0.092686 | 0 | 0 |  | 138
ILLN | ILLN | 6565 | ILLNO4R2 | 1.776 |  |  |  | WEST2001 | CROCKETT | 0.22336 | -0.093374 | 0.39669 | -0.16583 |  | 69
COMSTOCK | COMSTOCK | 6566 | COMSTCK2 |  |  |  |  | WEST2001 | VAL VERDE | 0.15626 | -0.073148 | 0 | 0 |  | 69
TIPP | TIPP | 6569 | TIPPETR2 | 0.641 |  |  |  | WEST2001 | PECOS | 0.25309 | -0.10184 | 0.16223 | -0.065278 |  | 69
MART | MART | 6572 | MARYATE2 | 3.105 |  |  |  | WEST2001 | PECOS | 0.24968 | -0.10085 | 0.77525 | -0.31312 |  | 69
YATW | YATW | 6573 | YTSPMP 2 | 10.468 |  |  |  | WEST2001 | PECOS | 0.25039 | -0.10105 | 2.6211 | -1.0578 |  | 69
MART | MART | 6574 | MARATYT2 |  |  |  |  | WEST2001 | PECOS | 0.24968 | -0.10085 | 0 | 0 |  | 69
IRAN | IRAN | 6575 | IRAAN 2 | 4.879 |  |  |  | WEST2001 | PECOS | 0.24912 | -0.10068 | 1.2154 | -0.49123 |  | 69
MART | MART | 6576 | DSCVYTP2 |  |  |  |  | WEST2001 | PECOS | 0.24954 | -0.10081 | 0 | 0 |  | 69
SHEF | SHEF | 6577 | SHEFFLD2 | 4.246 |  |  |  | WEST2001 | PECOS | 0.24524 | -0.099556 | 1.0413 | -0.42271 |  | 69
FTLN | FTLN | 6578 | FTLCSTR2 |  |  |  |  | WEST2001 | PECOS | 0.24395 | -0.09918 | 0 | 0 |  | 69
FTLN | FTLN | 6579 | FTLCSTR2 |  |  |  |  | WEST2001 | PECOS | 0.25254 | -0.10158 | 0 | 0 |  | 138
AIRP | AIRP | 6580 | AIRPDTS2 | 0.054 |  |  |  | WEST2001 | CROCKETT | 0.24977 | -0.10087 | 0.013488 | -0.0054471 |  | 69
ARPT | ARPT | 6581 | AIRPDTP2 |  |  |  |  | WEST2001 | CROKETT | 0.24977 | -0.10087 | 0 | 0 |  | 69
WYTS | WYTS | 6582 | MVIEWTP2 |  |  |  |  | WEST2001 | PECOS | 0.25673 | -0.10275 | 0 | 0 |  | 138
MESAVIEW | MESAVIEW | 6583 | MESAVIEW | 14.033 |  |  |  | WEST2001 | CROCKETT | 0.25673 | -0.10275 | 3.6027 | -1.4419 |  | 138
INDN | INDN | 6584 | INDMESA2 | 1.152 |  |  |  | WEST2001 | PECOS | 0.26056 | -0.10382 | 0.30017 | -0.1196 |  | 138
MDSC | MDSC | 6585 | DSCVRY 2 | 1.026 |  |  |  | WEST2001 | PECOS | 0.24954 | -0.10081 | 0.25603 | -0.10343 |  | 69
|  | 6587 | SCROSS2 | 3.258 |  |  |  | WEST2001 | PECOS | 0.25985 | -0.10368 | 0.84658 | -0.33779 |  | 69
SHME | SHME | 6588 | SHLMESA2 | 3.429 |  |  |  | WEST2001 | UPTON | 0.25629 | -0.10276 | 0.87882 | -0.35238 |  | 69
RANK | RANK | 6589 | RANK12 2 | 2.178 |  |  |  | WEST2001 | UPTON | 0.24855 | -0.10086 | 0.54135 | -0.21968 |  | 69
SHME | SHME | 6590 | SHLMSAT2 |  |  |  |  | WEST2001 | UPTON | 0.25629 | -0.10276 | 0 | 0 |  | 69
RANK | RANK | 6591 | RANK4 2 |  |  |  |  | WEST2001 | UPTON | 0.24861 | -0.10088 | 0 | 0 |  | 69
MCAM | MCAM | 6592 | MCCAMEY2 | 6.247 |  |  |  | WEST2001 | UPTON | 0.25622 | -0.10275 | 1.6006 | -0.64186 |  | 69
MCAN | MCAN | 6593 | MCCAMYN2 |  |  |  |  | WEST2001 | UPTON | 0.25646 | -0.10281 | 0 | 0 |  | 69
SCRS | SCRS | 6594 | SCROSS 2 |  |  |  |  | WEST2001 | PECOS | 0.25985 | -0.10368 | 0 | 0 |  | 69
MCAN | MCAN | 6595 | MCCAMYN4 |  |  |  |  | WEST2001 | UPTON | 0.25766 | -0.10315 | 0 | 0 |  | 138
WTU_WHTB | WTU-WHTB | 6596 | WHTEBKR | 2.642 |  |  |  | WEST2001 | PECOS | 0.26235 | -0.10433 | 0.69312 | -0.27563 |  | 69
BOBCATH | BOBCATH | 6597 | BOBCAT 2 | 0.666 |  |  |  | WEST2001 | PECOS | 0.25972 | -0.10365 | 0.17297 | -0.069029 |  | 69
RIOP | RIOP | 6598 | RIOPEC 2 | 1.512 |  |  |  | WEST2001 | PECOS | 0.26235 | -0.10433 | 0.39667 | -0.15774 |  | 69
BOBCATH | BOBCATH | 6599 | BOBCAT T |  |  |  |  | WEST2001 | PECOS | 0.25972 | -0.10365 | 0 | 0 |  | 69
|  | 6600 | CRNAIR T |  |  |  |  | WEST2001 | CRANE | 0.2708 | -0.10651 | 0 | 0 |  | 69
RIOP | RIOP | 6601 | RIOPEC14 |  |  |  |  | WEST2001 | PECOS | 0.26248 | -0.10436 | 0 | 0 |  | 138
|  | 6602 | CRANTP1 |  |  |  |  | WEST2001 | CRANE | 0.27076 | -0.1065 | 0 | 0 |  | 69
|  | 6603 | CRANTP2 |  |  |  |  | WEST2001 | CRANE | 0.2708 | -0.10651 | 0 | 0 |  | 69
|  | 6605 | CRANAIR2 | 2.691 |  |  |  | WEST2001 | CRANE | 0.2708 | -0.10651 | 0.72872 | -0.28661 |  | 69
TNMP | TNMP | 6606 | TXNMPL 2 | 0.648 |  |  |  | WEST2001 | CRANE | 0.2708 | -0.10651 | 0.17548 | -0.069017 |  | 69
MCEL | MCEL | 6607 | MCELROY2 | 7.723 |  |  |  | WEST2001 | CRANE | 0.25646 | -0.10281 | 1.9806 | -0.79403 |  | 69
GUCA | GUCA | 6608 | CRANGU12 | 3.339 |  |  |  | WEST2001 | CRANE | 0.25646 | -0.10281 | 0.85631 | -0.34329 |  | 69
GUCT | GUCT | 6609 | TXNMTP 2 |  |  |  |  | WEST2001 | CRANE | 0.2708 | -0.10651 | 0 | 0 |  | 69
GUCB | GUCB | 6610 | CRANGU22 |  |  |  |  | WEST2001 | CRANE | 0.27076 | -0.1065 | 0 | 0 |  | 69
DUN2 | DUN2 | 6611 | DUNEFLD2 | 4.15 |  |  |  | WEST2001 | CRANE | 0.27076 | -0.1065 | 1.1237 | -0.44197 |  | 69
SPUD | SPUD | 6612 | SPUDFLT2 | 0.333 |  |  |  | WEST2001 | CRANE | 0.26581 | -0.10522 | 0.088514 | -0.035038 |  | 69
CRAN | CRAN | 6613 | WTUCRAN2 |  |  |  |  | WEST2001 | CRANE | 0.2708 | -0.10651 | 0 | 0 |  | 69
DUN2 | DUN2 | 6614 | DUNEFDT2 |  |  |  |  | WEST2001 | CRANE | 0.27076 | -0.1065 | 0 | 0 |  | 69
CRAN | CRAN | 6615 | WTUCRAN4 |  |  |  |  | WEST2001 | CRANE | 0.27362 | -0.10724 | 0 | 0 |  | 138
COMC | COMC | 6627 | COMANCK4 |  |  |  |  | WEST2001 | PECOS | 0.26528 | -0.10508 | 0 | 0 |  | 138
FTST | FTST | 6628 | FTSTKPL2 |  | 5 |  |  | WEST2001 | PECOS | 0.26748 | -0.10565 | 1.3374 | -0.52827 |  | 69
FTST | FTST | 6630 | FTSTKPL4 |  |  |  |  | WEST2001 | PECOS | 0.26834 | -0.10588 | 0 | 0 |  | 138
|  | 6632 | WDWRDTP |  |  |  |  | WEST2001 | PECOS | 0.26275 | -0.10443 | 0 | 0 |  | 138
|  | 6633 | WDWRD 4 |  |  |  |  | WEST2001 | PECOS | 0.26275 | -0.10443 | 0 | 0 |  | 138
|  | 6634 | WDWRDU1 |  |  | 15.5 | 80 | WEST2001 | PECOS | 0.26275 | -0.10443 | 21.0201 | -8.3544 |  | 34.5
|  | 6635 | TAP4 |  |  |  |  | WEST2001 | CRANE | 0.26805 | -0.1058 | 0 | 0 |  | 138
SUNV | SUNV | 6641 | SUNVALY2 | 0.672 |  |  |  | WEST2001 | PECOS | 0.26358 | -0.10465 | 0.17713 | -0.070322 |  | 69
MAST | MAST | 6642 | MASTFLD2 | 1.071 |  |  |  | WEST2001 | PECOS | 0.26452 | -0.10489 | 0.2833 | -0.11234 |  | 69
PECV | PECV | 6643 | PECOVAL2 | 0.459 |  |  |  | WEST2001 | PECOS | 0.26569 | -0.10519 | 0.12195 | -0.048283 |  | 69
FTSW | FTSW | 6645 | FTSTKSW2 | 1.96 |  |  |  | WEST2001 | REEVES | 0.26816 | -0.10583 | 0.52559 | -0.20743 |  | 69
TRAN | TRAN | 6647 | TRNPECM2 |  |  |  |  | WEST2001 | REEVES | 0.27142 | -0.10668 | 0 | 0 |  | 69
TRAN | TRAN | 6648 | TRNPECT2 |  |  |  |  | WEST2001 | REEVES | 0.27142 | -0.10668 | 0 | 0 |  | 69
VERH | VERH | 6649 | VERHALN2 | 0.702 |  |  |  | WEST2001 | REEVES | 0.27142 | -0.10668 | 0.19054 | -0.074887 |  | 69
CCRT | CCRT | 6650 | CHRYTP2 |  |  |  |  | WEST2001 | REEVES | 0.27142 | -0.10668 | 0 | 0 |  | 69
CCRK | CCRK | 6651 | CHRYCRK2 | 0.72 |  |  |  | WEST2001 | REEVES | 0.27142 | -0.10668 | 0.19542 | -0.076807 |  | 69
SGSA | SGSA | 6652 | SARAGOS2 | 2.862 |  |  |  | WEST2001 | REEVES | 0.27142 | -0.10668 | 0.7768 | -0.30531 |  | 69
BARL | BARL | 6653 | BARRILA2 |  |  |  |  | WEST2001 | PECOS | 0.27142 | -0.10668 | 0 | 0 |  | 69
BARL | BARL | 6655 | BARRILA4 |  |  |  |  | WEST2001 | PECOS | 0.27305 | -0.1071 | 0 | 0 |  | 138
MECPLNVW | MECPLNVW | 6658 | MECPLNVW | 3.054 |  |  |  | WEST2001 | SCURRY | 0.28541 | -0.11163 | 0.87164 | -0.34093 |  | 69
SNTXTAP | SNTXTAP | 6659 | SNTXTAP |  |  |  |  | WEST2001 | SCURRY | 0.28541 | -0.11163 | 0 | 0 |  | 69
SNTX1 | SNTX1 | 6660 | SYNTX 2 | 1.358 |  |  |  | WEST2001 | SCURRY | 0.28541 | -0.11163 | 0.38759 | -0.1516 |  | 69
LONGWRTH | LONGWRTH | 6661 | LONGWRT2 | 3.245 |  |  |  | WEST2001 | FISHER | 0.2722 | -0.11116 | 0.88329 | -0.36072 |  | 69
COCS | COCS | 6663 | CONRGEC2 | 0.342 |  |  |  | WEST2001 | PECOS | 0.26828 | -0.10586 | 0.091751 | -0.036205 |  | 69
ALPR | ALPR | 6665 | ALPINER2 |  |  |  |  | WEST2001 | BREWSTER | 0.27104 | -0.10658 | 0 | 0 |  | 69
ALPI | ALPI | 6666 | ALPINE 2 | 10.558 |  |  |  | WEST2001 | BREWSTER | 0.27097 | -0.10656 | 2.8609 | -1.1251 |  | 69
PAIS | PAIS | 6667 | PAISANO2 | 0.342 |  |  |  | WEST2001 | PRESIDIO | 0.2712 | -0.10662 | 0.092749 | -0.036464 |  | 69
|  | 6668 | RGECAPT2 | 2.511 |  |  |  | WEST2001 | BREWSTER | 0.27104 | -0.10658 | 0.68059 | -0.26762 |  | 69
FTDA | FTDA | 6676 | FTDAVIS2 | 2.34 |  |  |  | WEST2001 | JEFF DAVIS | 0.27158 | -0.10672 | 0.63549 | -0.24972 |  | 69
VALT | VALT | 6677 | VALTNTP2 | 4.744 | 1 |  |  | WEST2001 | JEFF DAVIS | 0.27158 | -0.10672 | 1.5599 | -0.61299 |  | 69
ALMC | ALMC | 6678 | ALAMITO2 |  |  |  |  | WEST2001 | PRESIDIO | 0.27158 | -0.10672 | 0 | 0 |  | 69
ALMC | ALMC | 6680 | ALAMITO4 |  |  |  |  | WEST2001 | PRESIDIO | 0.27216 | -0.10687 | 0 | 0 |  | 138
MARF | MARF | 6681 | MARFA 2 | 2.655 |  |  |  | WEST2001 | PRESIDIO | 0.27156 | -0.10671 | 0.72099 | -0.28332 |  | 69
CIEN | CIEN | 6682 | CIENEGA2 | 0.417 |  |  |  | WEST2001 | PRESIDIO | 0.27158 | -0.10672 | 0.11325 | -0.044501 |  | 69
SHAF | SHAF | 6683 | SHAFTER2 | 0.153 |  |  |  | WEST2001 | PRESIDIO | 0.27158 | -0.10672 | 0.041551 | -0.016328 |  | 69
PRES | PRES | 6684 | PRSIDIO2 | 2.826 |  |  |  | WEST2001 | PRESIDIO | 0.27158 | -0.10672 | 0.76748 | -0.30158 |  | 69
PRES | PRES | 6685 | PRSIDIO |  | 2 |  |  | WEST2001 | PRESIDIO | 0.27158 | -0.10672 | 0.54315 | -0.21344 |  | 12.47
BRYR | BRYR | 6689 | BRYANT2 |  |  |  |  | WEST2001 | PRESIDIO | 0.27158 | -0.10672 | 0 | 0 |  | 69
ATKN | ATKN | 6690 | ATKINSN2 |  |  |  |  | WEST2001 | PRESIDIO | 0.27158 | -0.10672 | 0 | 0 |  | 69
ESPY | ESPY | 6691 | ESPYWEL2 |  |  |  |  | WEST2001 | JEFFDAVIS | 0.27158 | -0.10672 | 0 | 0 |  | 69
POND | POND | 6692 | KENPNDR2 |  |  |  |  | WEST2001 | JEFFDAVIS | 0.27158 | -0.10672 | 0 | 0 |  | 69
PAUL | PAUL | 6750 | LKPAUL1G |  | 12 |  |  | WEST2001 | HARDEMAN | 0.25618 | -0.11297 | 3.0741 | -1.3556 |  | 13.8
PAUL | PAUL | 6751 | LKPAUL2G |  | 23 |  |  | WEST2001 | HARDEMAN | 0.25618 | -0.11297 | 5.8921 | -2.5982 |  | 13.8
OKLA | OKLA | 6752 | OKLAUN1G |  |  | 690 | 690 | WEST2001 | WILBARGER | 0.25248 | -0.11386 | 174.2078 | -78.5624 |  | 24
PAIP | PAIP | 6753 | PTCREK1G |  | 32 |  |  | WEST2001 | HASKELL | 0.26295 | -0.11181 | 8.4145 | -3.5778 |  | 13.8
PAIP | PAIP | 6754 | PTCREK2G |  | 33 |  |  | WEST2001 | HASKELL | 0.26325 | -0.1118 | 8.6873 | -3.6895 |  | 13.8
PAIP | PAIP | 6755 | PTCREK3G |  | 54 |  |  | WEST2001 | HASKELL | 0.26381 | -0.1118 | 14.2459 | -6.0372 |  | 13.8
PAIP | PAIP | 6756 | PTCREK4G |  |  | 100 | 118 | WEST2001 | HASKELL | 0.26376 | -0.11181 | 31.1237 | -13.1933 |  | 14.4
FTPP | FTPP | 6757 | PHANTM1G |  |  | 147 | 158 | WEST2001 | JONES | 0.26455 | -0.11032 | 41.7983 | -17.43 |  | 14.4
FTPP | FTPP | 6758 | PHANTM2G |  |  | 200 | 204 | WEST2001 | JONES | 0.26455 | -0.11032 | 53.9675 | -22.5046 |  | 20
OAKC | OAKC | 6759 | OAKCK 1G |  |  | 85 | 85 | WEST2001 | COKE | 0.25443 | -0.10613 | 21.6269 | -9.021 |  | 13.8
SAPS | SAPS | 6762 | SAPS 1G |  |  | 21 | 21 | WEST2001 | TOM GREEN | 0.23825 | -0.09987 | 5.0033 | -2.0973 |  | 14.4
SAPS | SAPS | 6763 | SAPS 2G |  |  | 102 | 102 | WEST2001 | TOM GREEN | 0.23568 | -0.099111 | 24.0397 | -10.1093 |  | 14.4
RIOP | RIOP | 6764 | RIOPEC4G |  | 4 |  |  | WEST2001 | PECOS | 0.26235 | -0.10433 | 1.0494 | -0.41731 |  | 13.2
RIOP | RIOP | 6765 | RIOPEC5G |  | 38 |  |  | WEST2001 | PECOS | 0.26235 | -0.10433 | 9.9692 | -3.9644 |  | 13.8
RIOP | RIOP | 6766 | RIOPEC6G |  |  | 98 | 98 | WEST2001 | PECOS | 0.26248 | -0.10436 | 25.7235 | -10.2273 |  | 14.4
SARC | SARC | 6768 | SRC2DUM |  |  |  |  | WEST2001 | TOM GREEN | 0.24745 | -0.10261 | 0 | 0 |  | 100
SARC | SARC | 6769 | SRC2TERT |  |  |  |  | WEST2001 | TOM GREEN | 0.24745 | -0.10261 | 0 | 0 |  | 13.2
|  | 6772 | ABINOPK4 | 1.215 |  |  |  | WEST2001 | JONES | 0.2693 | -0.1105 | 0.3272 | -0.13425 |  | 138
PCNBYU | PCNBYU | 6773 | PCANBYU4 | 6.4 |  |  |  | WEST2001 | TAYLOR | 0.24812 | -0.10985 | 1.588 | -0.70304 |  | 138
|  | 6780 | OK1TERT |  |  |  |  | WEST2001 | WILBARGER | 0.25238 | -0.11389 | 0 | 0 |  | 13.2
|  | 6789 | AMCWTERT |  |  |  |  | WEST2001 | JONES | 0.27039 | -0.11058 | 0 | 0 |  | 13.2
ROCK_ATL | ROCK_ATL | 8235 | PE-FINA2 |  |  |  |  | WEST2001 | EDWARDS | 0.14303 | -0.069582 | 0 | 0 |  | 69
KIMBLE | KIMBLE | 8237 | KIMCOOP2 | 1.67 |  |  |  | WEST2001 | EDWARDS | 0.14303 | -0.069582 | 0.23886 | -0.1162 |  | 69
ROCKSPRS | ROCKSPRS | 8238 | R.SPNGS2 | 1.92 |  |  |  | WEST2001 | EDWARDS | 0.14303 | -0.069582 | 0.27462 | -0.1336 |  | 69
FRIR | FRIR | 8239 | FRSRNCH2 | 0.974 |  |  |  | WEST2001 | SUTTON | 0.18232 | -0.081768 | 0.17758 | -0.079642 |  | 69
CTHR | CTHR | 8259 | CORTHAN4 | 0.96 |  |  |  | WEST2001 | SUTTON | 0.18244 | -0.081794 | 0.17514 | -0.078523 |  | 138
ROCK_ATL | ROCK_ATL | 8664 | HUMBPMP2 |  |  |  |  | WEST2001 | EDWARDS | 0.14303 | -0.069582 | 0 | 0 |  | 69
COMSTOCK | COMSTOCK | 8682 | COMSTOC2 | 0.598 |  |  |  | WEST2001 | VAL VERDE | 0.15626 | -0.073148 | 0.093444 | -0.043743 |  | 69
OECCS | OECCS | 11020 | TIE ST1 |  | 204 |  |  | WEST2001 | ECTOR | 0.28973 | -0.11132 | 59.1059 | -22.7101 |  | 18
OECCS | OECCS | 11021 | TIE CT11 |  | 172 |  |  | WEST2001 | ECTOR | 0.28973 | -0.11132 | 49.8344 | -19.1477 |  | 18
OECCS | OECCS | 11022 | TIE CT12 |  | 172 |  |  | WEST2001 | ECTOR | 0.28973 | -0.11132 | 49.8344 | -19.1477 |  | 18
OECCS | OECCS | 11023 | TIE CT21 |  | 172 |  |  | WEST2001 | ECTOR | 0.28973 | -0.11132 | 49.8344 | -19.1477 |  | 18
OECCS | OECCS | 11024 | TIE CT22 |  | 172 |  |  | WEST2001 | ECTOR | 0.28973 | -0.11132 | 49.8344 | -19.1477 |  | 18
OECCS | OECCS | 11025 | TIE ST2 |  | 204 |  |  | WEST2001 | ECTOR | 0.28973 | -0.11132 | 59.1059 | -22.7101 |  | 18
PETROLIA | PETROLIA | 37390 | PETROLIA | 4 |  |  |  | WEST2001 | CLAY | 0.22323 | -0.11567 | 0.89292 | -0.46268 |  | 69
OLNEYTN | OLNEYTN | 37830 | OLNEY | 3.1 |  |  |  | WEST2001 | YOUNG | 0.22778 | -0.11496 | 0.70611 | -0.35637 |  | 69
THURBER | THURBER | 37850 | THURBER | 7.1 |  |  |  | WEST2001 | PALO PINTO | 0.17772 | -0.10973 | 1.2618 | -0.77906 |  | 69
ELIASVLE | ELIASVLE | 37860 | ELIASVLE | 0.4 |  |  |  | WEST2001 | YOUNG | 0.22388 | -0.11435 | 0.089551 | -0.045741 |  | 69
GRAHAM | GRAHAM | 37870 | GRAHAM | 0.7 |  |  |  | WEST2001 | YOUNG | 0.22191 | -0.11473 | 0.15534 | -0.080308 |  | 69
BRYSNTN | BRYSNTN | 37890 | BRYSON | 2.8 |  |  |  | WEST2001 | JACK | 0.22191 | -0.11473 | 0.62134 | -0.32123 |  | 69
WINK | WINK | 37900 | WINK |  |  |  |  | WEST2001 | WINKLER | 0.28609 | -0.1105 | 0 | 0 |  | 138
WINK | WINK | 37920 | WINK |  |  |  |  | WEST2001 | WINKLER | 0.28597 | -0.11047 | 0 | 0 |  | 69
CALIF_TN | CALIF TN | 37940 | CALIFRNA | 2.2 |  |  |  | WEST2001 | WINKLER | 0.28594 | -0.11046 | 0.62907 | -0.24301 |  | 69
WNKLRCO6 | WNKLRCO6 | 37960 | WNKLRCO6 | 0.2 |  |  |  | WEST2001 | WINKLER | 0.28582 | -0.11042 | 0.057164 | -0.022084 |  | 69
WICKETT | WICKETT | 37980 | WICKETT | 0.8 |  |  |  | WEST2001 | WARD | 0.28572 | -0.11039 | 0.22858 | -0.088315 |  | 69
PYOTE | PYOTE | 38000 | PYOTE | 2.4 |  |  |  | WEST2001 | WARD | 0.28578 | -0.11041 | 0.68586 | -0.26498 |  | 69
WORSHAM | WORSHAM | 38020 | WORSHAM | 1.4 |  |  |  | WEST2001 | REEVES | 0.28584 | -0.11043 | 0.40018 | -0.1546 |  | 69
IH20 | IH20 | 38040 | IH20 | 3.9 |  |  |  | WEST2001 | REEVES | 0.28589 | -0.11044 | 1.115 | -0.43073 |  | 69
STAFBLVD | STAFBLVD | 38050 | STAFBLVD | 9.1 |  |  |  | WEST2001 | REEVES | 0.28589 | -0.11044 | 2.6016 | -1.005 |  | 69
FLAT_TOP | FLAT TOP | 38070 | FLAT TOP | 2.9 |  |  |  | WEST2001 | REEVES | 0.28589 | -0.11044 | 0.82908 | -0.32028 |  | 69
PECOS | PECOS | 38090 | PECOS | 9.5 |  |  |  | WEST2001 | REEVES | 0.2859 | -0.11044 | 2.716 | -1.0492 |  | 69
REEVSCO4 | REEVSCO4 | 38120 | REEVSCO4 | 2.9 |  |  |  | WEST2001 | REEVES | 0.2859 | -0.11044 | 0.82911 | -0.32029 |  | 69
TOYAH | TOYAH | 38140 | TOYAH | 0.1 |  |  |  | WEST2001 | REEVES | 0.2859 | -0.11044 | 0.02859 | -0.011044 |  | 69
COCHISE | COCHISE | 38160 | COCHISE | 2.1 |  |  |  | WEST2001 | WARD | 0.28591 | -0.11045 | 0.60042 | -0.23194 |  | 69
LNSTRTAP | LNSTRTAP | 38180 | LNSTRTAP |  |  |  |  | WEST2001 | WARD | 0.28594 | -0.11046 | 0 | 0 |  | 69
LONESTAR | LONESTAR | 38200 | LONESTAR | 2.3 |  |  |  | WEST2001 | WARD | 0.28594 | -0.11046 | 0.65767 | -0.25405 |  | 69
AAPIPELN | AAPIPELN | 38230 | AAPIPELN |  |  |  |  | WEST2001 | WINKLER | 0.28597 | -0.11047 | 0 | 0 |  | 69
KERMIT_2 | KERMIT#2 | 38250 | KERMIT#2 | 5.9 |  |  |  | WEST2001 | WINKLER | 0.28597 | -0.11047 | 1.6872 | -0.65175 |  | 69
KERMIT_1 | KERMIT#1 | 38280 | KERMIT#1 | 2.4 |  |  |  | WEST2001 | WINKLER | 0.28597 | -0.11047 | 0.68633 | -0.26512 |  | 69
KEYSTONE | KEYSTONE | 38290 | KEYSTONE | 2.6 |  |  |  | WEST2001 | WINKLER | 0.28597 | -0.11047 | 0.74353 | -0.28721 |  | 69
16TH_ST | 16TH_ST | 38310 | 16TH ST |  |  |  |  | WEST2001 | PECOS | 0.26439 | -0.10485 | 0 | 0 |  | 138
16TH_ST | 16TH_ST | 38320 | 16TH ST | 7.39 |  |  |  | WEST2001 | PECOS | 0.26621 | -0.10533 | 1.9673 | -0.77835 |  | 69
|  | 38330 | WDWRDTAP |  |  |  |  | WEST2001 | PECOS | 0.26258 | -0.10439 | 0 | 0 |  | 138
|  | 38331 | WDWRD4 |  |  |  |  | WEST2001 | PECOS | 0.26258 | -0.10439 | 0 | 0 |  | 138
|  | 38332 | WDWRDU2 |  |  | 15.5 | 80 | WEST2001 | PECOS | 0.26258 | -0.10439 | 21.0065 | -8.3508 |  | 34.5
|  | 38340 | AIRPORT | 4.99 |  |  |  | WEST2001 | PECOS | 0.26684 | -0.10549 | 1.3315 | -0.52639 |  | 69
FTSTCKTN | FTSTCKTN | 38350 | FTSTKTAP |  |  |  |  | WEST2001 | PECOS | 0.26816 | -0.10583 | 0 | 0 |  | 69
FTSTCKTN | FTSTCKTN | 38360 | FTSTCKTN | 7.27 |  |  |  | WEST2001 | PECOS | 0.26621 | -0.10533 | 1.9353 | -0.76572 |  | 69
PUCKTFLD | PUCKTFLD | 38380 | PUCKTTAP |  |  |  |  | WEST2001 | PECOS | 0.26621 | -0.10533 | 0 | 0 |  | 69
ARMDLO2 | ARMDLO2 | 38390 | ARMDLO2 |  |  |  |  | WEST2001 | PECOS | 0.26621 | -0.10533 | 0 | 0 |  | 69
SANDRSON | SANDRSON | 38400 | SANDRSON | 1.29 |  |  |  | WEST2001 | TERRELL | 0.26621 | -0.10533 | 0.34341 | -0.13587 |  | 69
|  | 38420 | SWTECTNP |  |  |  |  | WEST2001 | PECOS | 0.26235 | -0.10433 | 0 | 0 |  | 69
WTU_TNNG | WTU_TNNG | 38440 | NRTHNNAT | 5.01 |  |  |  | WEST2001 | PECOS | 0.26235 | -0.10433 | 1.3144 | -0.52267 |  | 69
PUCKTFLD | PUCKTFLD | 38460 | PUCKTFLD | 1.39 |  |  |  | WEST2001 | PECOS | 0.26235 | -0.10433 | 0.36466 | -0.14501 |  | 69
|  | 38470 | TNPGOMZ2 | 1.27 |  |  |  | WEST2001 | PECOS | 0.2674 | -0.10564 | 0.3396 | -0.13416 |  | 69
|  | 38490 | TNPBEL2 | 1.65 |  |  |  | WEST2001 | PECOS | 0.26829 | -0.10587 | 0.44269 | -0.17468 |  | 69
GTSVLTAP | GTSVLTAP | 158 | GTSVLTAP |  |  |  |  | NORTH2001 | CORYELL | 0.0019762 | -0.07265 | 0 | 0 |  | 69
|  | 164 | PATTON | 1.65 |  |  |  | NORTH2001 | MCLENNAN | -0.0004116 | -0.073203 | -0.00067914 | -0.12079 |  | 69
NAVROMLS | NAVROMLS | 186 | NAVROMLS |  |  |  |  | NORTH2001 | NAVARRO | -0.0067841 | -0.076494 | 0 | 0 |  | 69
DAWSON | DAWSON | 190 | DAWSON | 0.36 |  |  |  | NORTH2001 | NAVARRO | -0.0068592 | -0.077326 | -0.0024693 | -0.027837 |  | 69
|  | 192 | TELICO | 6.36 |  |  |  | NORTH2001 | ELLIS | -0.011276 | -0.11513 | -0.071714 | -0.73226 |  | 138
BARRY1 | BARRY1 | 193 | BARRY | 4.74 |  |  |  | NORTH2001 | NAVARRO | -0.0078885 | -0.088735 | -0.037391 | -0.4206 |  | 69
PURDON | PURDON | 194 | PURDON | 3.98 |  |  |  | NORTH2001 | NAVARRO | -0.0070295 | -0.079213 | -0.027977 | -0.31527 |  | 69
FFD | FFD | 196 | FARFIELD | 7.52 |  |  |  | NORTH2001 | FREESTONE | -0.010303 | -0.086836 | -0.077479 | -0.65301 |  | 138
EMMETT | EMMETT | 198 | EMMETT | 2.77 |  |  |  | NORTH2001 | NAVARRO | -0.0070295 | -0.079213 | -0.019472 | -0.21942 |  | 69
HIGHWY22 | HIGHWY22 | 205 | HIGHWY22 | 1.46 |  |  |  | NORTH2001 | NAVARRO | -0.010668 | -0.10863 | -0.015576 | -0.15859 |  | 138
POWELLMP | POWELLMP | 206 | POWELLMP | 1.55 |  |  |  | NORTH2001 | NAVARRO | -0.010939 | -0.10897 | -0.016956 | -0.16891 |  | 69
EUREKA | EUREKA | 208 | EUREKA | 2.64 |  |  |  | NORTH2001 | NAVARRO | -0.01063 | -0.10689 | -0.028063 | -0.28218 |  | 138
RSP | RSP | 210 | REAGRSPG | 2.49 |  |  |  | NORTH2001 | ELLIS | -0.0092482 | -0.10381 | -0.023028 | -0.25848 |  | 69
GDL | GDL | 211 | GOODLOE | 13.69 |  |  |  | NORTH2001 | NAVARRO | -0.010763 | -0.10709 | -0.14734 | -1.4661 |  | 138
WINKLER | WINKLER | 212 | WINKLER | 3.37 |  |  |  | NORTH2001 | FREESTONE | -0.010576 | -0.094215 | -0.035641 | -0.3175 |  | 138
HAN1 | HAN1 | 213 | HANEY | 2.18 |  |  |  | NORTH2001 | NAVARRO | -0.0091811 | -0.10224 | -0.020015 | -0.22288 |  | 138
ROCKETSW | ROCKETSW | 214 | ROCKETSW |  |  |  |  | NORTH2001 | ELLIS | -0.01043 | -0.1108 | 0 | 0 |  | 69
INDIA | INDIA | 215 | INDIA |  |  |  |  | NORTH2001 | ELLIS | -0.012129 | -0.11836 | 0 | 0 |  | 69
ENS | ENS | 216 | ENNIS | 2.46 |  |  |  | NORTH2001 | ELLIS | -0.011364 | -0.11681 | -0.027956 | -0.28736 |  | 138
GLNHT | GLNHT | 217 | GLENHITS | 8.69 |  |  |  | NORTH2001 | ELLIS | -0.011771 | -0.12386 | -0.10229 | -1.0763 |  | 138
ROCKETT | ROCKETT | 218 | ROCKETT | 7.1 |  |  |  | NORTH2001 | ELLIS | -0.010931 | -0.11539 | -0.077612 | -0.81927 |  | 69
CEDARHIL | CEDARHIL | 220 | CEDARHIL | 10.17 |  |  |  | NORTH2001 | ELLIS | -0.0095001 | -0.10279 | -0.096616 | -1.0454 |  | 69
TRU | TRU | 221 | FERRIS | 5.58 |  |  |  | NORTH2001 | ELLIS | -0.011624 | -0.12173 | -0.064864 | -0.67925 |  | 138
TRU | TRU | 222 | TRUMBULL |  |  |  |  | NORTH2001 | ELLIS | -0.010988 | -0.11591 | 0 | 0 |  | 69
STP11 | STP11 | 223 | ST.PAUL | 11.15 |  |  |  | NORTH2001 | ELLIS | -0.0095783 | -0.10247 | -0.1068 | -1.1426 |  | 69
ITASCA | ITASCA | 224 | ITASCA | 4.01 |  |  |  | NORTH2001 | HILL | -0.0049556 | -0.092148 | -0.019872 | -0.36951 |  | 69
FORESTON | FORESTON | 225 | FORESTON | 2.23 |  |  |  | NORTH2001 | ELLIS | -0.0073263 | -0.098587 | -0.016338 | -0.21985 |  | 69
HOL | HOL | 227 | HOLNAM | 47.42 |  |  |  | NORTH2001 | ELLIS | -0.012486 | -0.13211 | -0.5921 | -6.2649 |  | 138
PEORIA | PEORIA | 228 | PEORIA | 5.68 |  |  |  | NORTH2001 | HILL | -0.0026124 | -0.085785 | -0.014839 | -0.48726 |  | 69
LAMPSTSW | LAMPSTSW | 232 | LAMPSTSW |  |  |  |  | NORTH2001 | HILL | -0.0022544 | -0.084812 | 0 | 0 |  | 69
CHATT | CHATT | 234 | CHATT | 2.18 |  |  |  | NORTH2001 | HILL | -0.0061026 | -0.09131 | -0.013304 | -0.19906 |  | 138
LAMPOST | LAMPOST | 236 | LAMPOST | 9.72 |  |  |  | NORTH2001 | HILL | -0.003843 | -0.08148 | -0.037354 | -0.79199 |  | 138
BOSQUESW | BOSQUESW | 239 | BSQSUTH2 |  |  | 150 | 160 | NORTH2001 | BOSQUE | -0.0030892 | -0.065528 | -0.49426 | -10.4845 |  | 22
|  | 241 | WHITNEY |  |  |  |  | NORTH2001 | BOSQUE | -0.0014843 | -0.073431 | 0 | 0 |  | 138
WNS | WNS | 242 | WHITNEY |  |  |  |  | NORTH2001 | BOSQUE | -0.0008603 | -0.081516 | 0 | 0 |  | 69
WND | WND | 243 | WHITNYSW |  |  |  |  | NORTH2001 | BOSQUE | -0.00096243 | -0.081303 | 0 | 0 |  | 69
WND | WND | 244 | WHITNEY1 |  |  | 15 | 15 | NORTH2001 | BOSQUE | -0.0008603 | -0.081516 | -0.012905 | -1.2227 |  | 12
WND | WND | 245 | WHITNEY2 |  |  | 15 | 15 | NORTH2001 | BOSQUE | -0.0008603 | -0.081516 | -0.012905 | -1.2227 |  | 12
BOSQUESW | BOSQUESW | 247 | BSQSUTH1 |  |  | 150 | 160 | NORTH2001 | BOSQUE | -0.0030892 | -0.065528 | -0.49426 | -10.4845 |  | 22
MAYPEARL | MAYPEARL | 248 | MAYPEARL | 1.53 |  |  |  | NORTH2001 | ELLIS | -0.0081342 | -0.098328 | -0.012445 | -0.15044 |  | 69
BOSQUESW | BOSQUESW | 251 | BSQSUTH3 |  |  | 150 | 160 | NORTH2001 | BOSQUE | -0.0014843 | -0.073431 | -0.23749 | -11.749 |  | 22
BOSQUESW | BOSQUESW | 252 | BOSQUESW |  |  |  |  | NORTH2001 | BOSQUE | -0.0014843 | -0.073431 | 0 | 0 |  | 138
BOSQUESW | BOSQUESW | 253 | BSQSUTH4 |  |  | 90 | 120 | NORTH2001 | BOSQUE | -0.0014843 | -0.073431 | -0.17812 | -8.8117 |  | 22
HAMLTON | HAMLTON | 258 | HAMILTON | 5.72 |  |  |  | NORTH2001 | HAMILTON | 0.0064319 | -0.085096 | 0.036791 | -0.48675 |  | 69
INDIANGP | INDIANGP | 262 | INDIANGP | 1.83 |  |  |  | NORTH2001 | HAMILTON | 0.009465 | -0.093567 | 0.017321 | -0.17123 |  | 69
ENERGYSW | ENERGYSW | 265 | ENERGYSW |  |  |  |  | NORTH2001 | COMANCHE | 0.009465 | -0.093567 | 0 | 0 |  | 69
ENERGY | ENERGY | 269 | ENERGY | 1.39 |  |  |  | NORTH2001 | COMANCHE | 0.009465 | -0.093567 | 0.013156 | -0.13006 |  | 69
GUSTINE | GUSTINE | 273 | GUSTINE | 2.72 |  |  |  | NORTH2001 | COMANCHE | 0.009465 | -0.093567 | 0.025745 | -0.2545 |  | 69
HAS | HAS | 277 | HASSE | 0.71 |  |  |  | NORTH2001 | COMANCHE | 0.01189 | -0.10034 | 0.0084418 | -0.071242 |  | 69
DOWNING | DOWNING | 281 | DOWNING | 4.11 |  |  |  | NORTH2001 | COMANCHE | 0.014274 | -0.10101 | 0.058664 | -0.41517 |  | 69
ZEPHYR | ZEPHYR | 283 | ZEPHYR | 4.53 |  |  |  | NORTH2001 | BROWN | -0.00088198 | -0.099067 | -0.0039954 | -0.44877 |  | 138
RISNGSTR | RISNGSTR | 285 | RISNGSTR | 2.61 |  |  |  | NORTH2001 | COMANCHE | 0.0085557 | -0.099625 | 0.02233 | -0.26002 |  | 69
NIMROD | NIMROD | 289 | NIMROD | 2.47 |  |  |  | NORTH2001 | EASTLAND | 0.0085557 | -0.099625 | 0.021133 | -0.24607 |  | 69
COMANCHE | COMANCHE | 290 | COMANCHE | 7.17 |  |  |  | NORTH2001 | COMANCHE | 0.0014472 | -0.10573 | 0.010376 | -0.75811 |  | 138
DELEON | DELEON | 291 | DELEON | 1.37 |  |  |  | NORTH2001 | COMANCHE | 0.029591 | -0.10524 | 0.04054 | -0.14418 |  | 69
HLD | HLD | 292 | HOLDER |  |  |  |  | NORTH2001 | BROWN | 0.0010975 | -0.097812 | 0 | 0 |  | 138
HLD | HLD | 293 | HOLDER | 8.01 |  |  |  | NORTH2001 | BROWN | 0.0044522 | -0.098628 | 0.035662 | -0.79001 |  | 69
MOUNTARY | MOUNTARY | 294 | MOUNTARY | 7.81 |  |  |  | NORTH2001 | COMANCHE | 0.023053 | -0.10333 | 0.18005 | -0.80704 |  | 69
STV | STV | 295 | STPHNVL |  |  |  |  | NORTH2001 | ERATH | 0.041344 | -0.10557 | 0 | 0 |  | 138
STVLT | STVLT | 296 | STPHVLTP |  |  |  |  | NORTH2001 | ERATH | 0.041435 | -0.10557 | 0 | 0 |  | 138
CALRTNSW | CALRTNSW | 297 | CALRTNSW |  |  |  |  | NORTH2001 | ERATH | 0.028448 | -0.10476 | 0 | 0 |  | 69
CARLTON | CARLTON | 298 | CARLTON | 5.98 |  |  |  | NORTH2001 | ERATH | 0.028448 | -0.10476 | 0.17012 | -0.62646 |  | 69
STV | STV | 299 | STEPHNVL | 7.51 |  |  |  | NORTH2001 | ERATH | 0.030844 | -0.10539 | 0.23164 | -0.79149 |  | 69
|  | 300 | JOHNSVIL | 4.83 |  |  |  | NORTH2001 | ERATH | 0.028483 | -0.095592 | 0.13757 | -0.46171 |  | 138
LNG | LNG | 301 | LINGLEVL | 5.36 |  |  |  | NORTH2001 | ERATH | 0.098713 | -0.10714 | 0.5291 | -0.57428 |  | 138
SLD | SLD | 302 | SELDEN | 8.27 |  |  |  | NORTH2001 | ERATH | 0.038603 | -0.10307 | 0.31925 | -0.8524 |  | 138
NORFORK | NORFORK | 303 | NORFORK | 7.16 |  |  |  | NORTH2001 | ERATH | 0.0287 | -0.10577 | 0.20549 | -0.75734 |  | 69
WRIGHT | WRIGHT | 304 | WRIGHT | 5.49 |  |  |  | NORTH2001 | ERATH | 0.027952 | -0.10591 | 0.15346 | -0.58143 |  | 69
BNK | BNK | 306 | BUNKER |  |  |  |  | NORTH2001 | HOOD | 0.0085879 | -0.1107 | 0 | 0 |  | 138
GRBY | GRBY | 307 | GRANBURY | 4.35 |  |  |  | NORTH2001 | HOOD | 0.012213 | -0.10871 | 0.053126 | -0.47291 |  | 69
GRBY | GRBY | 308 | GRANBURY |  |  |  |  | NORTH2001 | HOOD | 0.012126 | -0.10876 | 0 | 0 |  | 69
HILLCITY | HILLCITY | 311 | HILLCITY | 1.43 |  |  |  | NORTH2001 | SOMERVELL | 0.010576 | -0.10531 | 0.015123 | -0.15059 |  | 69
GLENROSE | GLENROSE | 315 | GLENROSE | 4.6 |  |  |  | NORTH2001 | SOMERVELL | 0.0089384 | -0.1019 | 0.041117 | -0.46875 |  | 69
MERIDIAN | MERIDIAN | 319 | MERIDIAN | 3.31 |  |  |  | NORTH2001 | BOSQUE | 0.0047407 | -0.093168 | 0.015692 | -0.30839 |  | 69
|  | 322 | LIPAN |  |  |  |  | NORTH2001 | PALO PINTO | 0.048065 | -0.11358 | 0 | 0 |  | 138
CRANFLGP | CRANFLGP | 323 | CRANFLGP | 4.2 |  |  |  | NORTH2001 | BOSQUE | 0.0047407 | -0.093168 | 0.019911 | -0.39131 |  | 69
POWELL | POWELL | 327 | POWELL | 3.11 |  |  |  | NORTH2001 | BOSQUE | 0.0024986 | -0.088504 | 0.0077706 | -0.27525 |  | 69
MIL | MIL | 331 | MILLER | 5.11 |  |  |  | NORTH2001 | PALO PINTO | 0.047849 | -0.1122 | 0.24451 | -0.57334 |  | 138
MIL | MIL | 332 | MILLER1 |  |  | 70 | 88 | NORTH2001 | PALO PINTO | 0.047849 | -0.1122 | 4.2107 | -9.8736 |  | 14
MIL | MIL | 333 | MILLER2 |  |  | 120 | 138 | NORTH2001 | PALO PINTO | 0.047849 | -0.1122 | 6.6031 | -15.4836 |  | 14
MIL | MIL | 334 | MILLER3 |  |  | 165.64 | 240 | NORTH2001 | PALO PINTO | 0.047849 | -0.1122 | 11.4837 | -26.928 |  | 14
MIL | MIL | 335 | MILLER4 |  |  | 75 | 130 | NORTH2001 | PALO PINTO | 0.047849 | -0.1122 | 6.2203 | -14.586 |  | 14
MIL | MIL | 336 | MILLER5 |  |  | 104 | 130 | NORTH2001 | PALO PINTO | 0.047849 | -0.1122 | 6.2203 | -14.586 |  | 14
|  | 340 | WSTWTHFD |  |  |  |  | NORTH2001 | PARKER | 0.050727 | -0.11573 | 0 | 0 |  | 138
MSP | MSP | 343 | MORSSHEP | 11.73 |  |  |  | NORTH2001 | PALO PINTO | 0.12658 | -0.11558 | 1.4848 | -1.3557 |  | 69
MSP | MSP | 344 | MORSHEP |  |  | 12 | 12 | NORTH2001 | PALO PINTO | 0.12658 | -0.11558 | 1.519 | -1.3869 |  | 12
MSP | MSP | 345 | MORSHEP2 |  |  | 12 | 12 | NORTH2001 | PALO PINTO | 0.12658 | -0.11558 | 1.519 | -1.3869 |  | 12
PTR | PTR | 352 | PORTROYL | 17.29 |  |  |  | NORTH2001 | HOOD | 0.001589 | -0.11084 | 0.027475 | -1.9164 |  | 138
SPUNKY | SPUNKY | 356 | SPUNKY |  |  |  |  | NORTH2001 | JOHNSON | -0.007039 | -0.10944 | 0 | 0 |  | 138
SPUNKY | SPUNKY | 357 | SPUNKY |  |  |  |  | NORTH2001 | JOHNSON | -0.007039 | -0.10944 | 0 | 0 |  | 69
HOD | HOD | 363 | HOOD |  |  |  |  | NORTH2001 | HOOD | -0.0035679 | -0.11094 | 0 | 0 |  | 138
HOD | HOD | 364 | HOOD |  |  |  |  | NORTH2001 | HOOD | -0.0017225 | -0.10984 | 0 | 0 |  | 69
TEN | TEN | 366 | TENASKA |  |  | 172 | 200 | NORTH2001 | JOHNSON | -0.011159 | -0.10627 | -2.2318 | -21.2533 |  | 25
TEN | TEN | 367 | TENASKA |  |  | 86 | 116 | NORTH2001 | JOHNSON | -0.011159 | -0.10627 | -1.2944 | -12.3269 |  | 25
TEN | TEN | 370 | TENASKA | 10.4 |  |  |  | NORTH2001 | JOHNSON | -0.011159 | -0.10627 | -0.11605 | -1.1052 |  | 138
ACT | ACT | 373 | ACTON | 10.34 |  |  |  | NORTH2001 | HOOD | -0.00043775 | -0.10907 | -0.0045263 | -1.1278 |  | 69
|  | 375 | AIRLIQD | 12.13 |  |  |  | NORTH2001 | JOHNSON | -0.010047 | -0.1103 | -0.12187 | -1.338 |  | 138
FAL | FAL | 377 | FALCREEK | 12.21 |  |  |  | NORTH2001 | HOOD | -0.0088348 | -0.10786 | -0.10787 | -1.317 |  | 138
FRD | FRD | 380 | FRENDSHP | 3.66 |  |  |  | NORTH2001 | HOOD | 0.0091013 | -0.10879 | 0.033311 | -0.39817 |  | 69
GEO | GEO | 384 | GEOSCREK | 4.19 |  |  |  | NORTH2001 | SOMERVELL | -0.007039 | -0.10944 | -0.029494 | -0.45856 |  | 69
NHP | NHP | 387 | NEWHOPE | 8.93 |  |  |  | NORTH2001 | JOHNSON | -0.007039 | -0.10944 | -0.062859 | -0.97731 |  | 69
BON | BON | 391 | BONO | 5.24 |  |  |  | NORTH2001 | JOHNSON | -0.0090198 | -0.10858 | -0.047264 | -0.56897 |  | 138
CRD | CRD | 393 | CONCORD |  |  |  |  | NORTH2001 | JOHNSON | -0.018302 | -0.11064 | 0 | 0 |  | 345
CRD | CRD | 394 | CONCORD |  |  |  |  | NORTH2001 | JOHNSON | -0.01153 | -0.1075 | 0 | 0 |  | 138
JOSHUA | JOSHUA | 398 | JOSHUA | 12.66 |  |  |  | NORTH2001 | JOHNSON | -0.011158 | -0.10629 | -0.14125 | -1.3457 |  | 138
|  | 399 | CROWLEY | 8.71 |  |  |  | NORTH2001 | JOHNSON | -0.010989 | -0.10575 | -0.095718 | -0.9211 |  | 138
EGN | EGN | 405 | EGAN | 13.51 |  |  |  | NORTH2001 | JOHNSON | -0.010569 | -0.1044 | -0.14279 | -1.4104 |  | 138
BUR | BUR | 412 | BURLESON | 12.7 |  |  |  | NORTH2001 | JOHNSON | -0.010436 | -0.10396 | -0.13254 | -1.3203 |  | 138
KEN | KEN | 415 | KEENE | 4.71 |  |  |  | NORTH2001 | JOHNSON | -0.010214 | -0.10313 | -0.048109 | -0.48576 |  | 138
LILLIANS | LILLIANS | 416 | LILLIANS |  |  |  |  | NORTH2001 | JOHNSON | -0.0097353 | -0.10163 | 0 | 0 |  | 138
LIL | LIL | 419 | LILLIAN | 13.09 |  |  |  | NORTH2001 | JOHNSON | -0.0099641 | -0.10244 | -0.13043 | -1.3409 |  | 138
LIL | LIL | 420 | LILLIAN | 10.59 |  |  |  | NORTH2001 | JOHNSON | -0.009665 | -0.10213 | -0.10235 | -1.0815 |  | 69
RET | RET | 429 | RETTA | 7.17 |  |  |  | NORTH2001 | JOHNSON | -0.010214 | -0.10325 | -0.073238 | -0.7403 |  | 138
TIMBRGRN | TIMBRGRN | 430 | TIMBRGRN | 12.35 |  |  |  | NORTH2001 | JOHNSON | -0.010358 | -0.10371 | -0.12792 | -1.2808 |  | 138
CON | CON | 432 | CONLEY | 6.83 |  |  |  | NORTH2001 | JOHNSON | -0.009473 | -0.10105 | -0.064701 | -0.6902 |  | 69
LAL | LAL | 435 | LKALVRDO | 6.66 |  |  |  | NORTH2001 | JOHNSON | -0.0097154 | -0.10148 | -0.064704 | -0.67585 |  | 138
GDV | GDV | 436 | GRNDVIEW |  |  |  |  | NORTH2001 | JOHNSON | -0.0093055 | -0.10012 | 0 | 0 |  | 138
GDV | GDV | 437 | GRNDVIEW |  |  |  |  | NORTH2001 | JOHNSON | -0.0094511 | -0.10093 | 0 | 0 |  | 69
GRIFFITH | GRIFFITH | 440 | GRIFFITH | 6.95 |  |  |  | NORTH2001 | JOHNSON | -0.010983 | -0.11288 | -0.076332 | -0.78449 |  | 138
SNDFLTSW | SNDFLTSW | 443 | SNDFLTSW |  |  |  |  | NORTH2001 | JOHNSON | -0.0083974 | -0.097021 | 0 | 0 |  | 138
COV | COV | 444 | COVNGTON | 8.13 |  |  |  | NORTH2001 | JOHNSON | -0.0078203 | -0.095052 | -0.063579 | -0.77277 |  | 138
SND | SND | 447 | SANDFLAT | 8.29 |  |  |  | NORTH2001 | JOHNSON | -0.0083974 | -0.097021 | -0.069614 | -0.80431 |  | 138
NASABYSW | NASABYSW | 451 | NASABYSW |  |  |  |  | NORTH2001 | HOOD | -0.0011073 | -0.10947 | 0 | 0 |  | 69
NAS | NAS | 455 | NASAUBAY | 7.7 |  |  |  | NORTH2001 | HOOD | -0.0011073 | -0.10947 | -0.0085264 | -0.84295 |  | 69
WPL | WPL | 466 | WAPLES |  |  |  |  | NORTH2001 | HOOD | -0.00035177 | -0.10902 | 0 | 0 |  | 69
WPL | WPL | 467 | WAPLES |  |  |  |  | NORTH2001 | HOOD | -0.0074725 | -0.10805 | 0 | 0 |  | 138
FAIRVWSW | FAIRVWSW | 469 | FAIRVWSW |  |  |  |  | NORTH2001 | HOOD | -2.6515e-05 | -0.10901 | 0 | 0 |  | 69
FAIRVIEW | FAIRVIEW | 470 | FAIRVIEW | 10.61 |  |  |  | NORTH2001 | HOOD | -0.00035177 | -0.10902 | -0.0037323 | -1.1567 |  | 69
LKW | LKW | 471 | LAKEWOOD | 9.38 |  |  |  | NORTH2001 | HOOD | 0.0014207 | -0.10898 | 0.013326 | -1.0222 |  | 69
THRPSPRG | THRPSPRG | 473 | THRPSPRG | 12.68 |  |  |  | NORTH2001 | HOOD | 0.0059692 | -0.10887 | 0.075689 | -1.3804 |  | 69
FOX | FOX | 477 | FOX |  |  |  |  | NORTH2001 | PARKER | 0.048245 | -0.11473 | 0 | 0 |  | 138
FOX | FOX | 478 | FOX |  |  |  |  | NORTH2001 | PARKER | 0.041928 | -0.11454 | 0 | 0 |  | 69
SODASPRG | SODASPRG | 484 | SODASPRG | 6.12 |  |  |  | NORTH2001 | PARKER | 0.041928 | -0.11454 | 0.2566 | -0.70101 |  | 69
BRK | BRK | 487 | BROCK | 5.82 |  |  |  | NORTH2001 | PARKER | 0.038483 | -0.11444 | 0.22397 | -0.66606 |  | 69
SBROCKSW | SBROCKSW | 489 | SBROCKSW |  |  |  |  | NORTH2001 | PARKER | 0.032981 | -0.11324 | 0 | 0 |  | 69
STHBROCK | STHBROCK | 491 | STHBROCK |  |  |  |  | NORTH2001 | PARKER | 0.032981 | -0.11324 | 0 | 0 |  | 69
TINTOP | TINTOP | 494 | TINTOP | 14.2 |  |  |  | NORTH2001 | PARKER | 0.027867 | -0.11213 | 0.3957 | -1.5922 |  | 69
LIVEOAK | LIVEOAK | 495 | WRAILRD |  |  |  |  | NORTH2001 | PARKER | 0.039737 | -0.11618 | 0 | 0 |  | 69
|  | 498 | LIVEOAK |  |  |  |  | NORTH2001 | PARKER | 0.039156 | -0.11538 | 0 | 0 |  | 69
HIL | HIL | 501 | HILTOP |  |  |  |  | NORTH2001 | PARKER | 0.037767 | -0.11766 | 0 | 0 |  | 138
NTX | NTX | 502 | NTTEXAS |  |  |  |  | NORTH2001 | PARKER | 0.040318 | -0.11699 | 0 | 0 |  | 69
NTX | NTX | 503 | NTEXAS1 |  | 18 |  |  | NORTH2001 | PARKER | 0.040318 | -0.11699 | 0.72572 | -2.1058 |  | 13
NTX | NTX | 504 | NTEXAS2 |  | 18 |  |  | NORTH2001 | PARKER | 0.040318 | -0.11699 | 0.72572 | -2.1058 |  | 13
NTX | NTX | 505 | NTEXAS3 |  | 40 |  |  | NORTH2001 | PARKER | 0.040318 | -0.11699 | 1.6127 | -4.6796 |  | 13
HLK | HLK | 506 | NTTEXAS |  |  |  |  | NORTH2001 | PARKER | 0.040127 | -0.11704 | 0 | 0 |  | 69
AGNESSW | AGNESSW | 511 | AGNESSW |  |  |  |  | NORTH2001 | PARKER | 0.029315 | -0.11899 | 0 | 0 |  | 138
NWTHRFRD | NWTHRFRD | 512 | NWTHRFRD |  |  |  |  | NORTH2001 | PARKER | 0.04361 | -0.11679 | 0 | 0 |  | 138
SHADYGRV | SHADYGRV | 515 | SHADYGRV | 11.99 |  |  |  | NORTH2001 | PARKER | 0.060753 | -0.11604 | 0.72843 | -1.3913 |  | 69
WHITT | WHITT | 519 | WHITT | 3.4 |  |  |  | NORTH2001 | PARKER | 0.08316 | -0.11578 | 0.28274 | -0.39366 |  | 69
ALEDOTP | ALEDOTP | 520 | ALEDOTP |  |  |  |  | NORTH2001 | PARKER | 0.03543 | -0.11801 | 0 | 0 |  | 69
DICEY | DICEY | 526 | DICEY | 11.7 |  |  |  | NORTH2001 | PARKER | 0.03543 | -0.11801 | 0.41453 | -1.3808 |  | 69
ALEDO | ALEDO | 527 | ALEDO | 4.6 |  |  |  | NORTH2001 | PARKER | 0.03543 | -0.11801 | 0.16298 | -0.54286 |  | 69
SPRINGTW | SPRINGTW | 530 | SPRINGTW | 9.44 |  |  |  | NORTH2001 | PARKER | 0.028476 | -0.11947 | 0.26882 | -1.1278 |  | 69
FLATROCK | FLATROCK | 531 | FLATROCK | 7.11 |  |  |  | NORTH2001 | PARKER | 0.03075 | -0.11899 | 0.21863 | -0.84604 |  | 69
AGNES | AGNES | 532 | AGNES | 13.33 |  |  |  | NORTH2001 | PARKER | 0.029315 | -0.11899 | 0.39077 | -1.5862 |  | 138
FLTRCKSW | FLTRCKSW | 533 | FLTRCKSW |  |  |  |  | NORTH2001 | PARKER | 0.03075 | -0.11899 | 0 | 0 |  | 69
WFT | WFT | 534 | WETHFORD |  |  |  |  | NORTH2001 | PARKER | 0.02922 | -0.119 | 0 | 0 |  | 138
AZLESW | AZLESW | 535 | AZLESW |  |  |  |  | NORTH2001 | PARKER | 0.023673 | -0.12012 | 0 | 0 |  | 69
AZLE | AZLE | 536 | AZLE |  |  |  |  | NORTH2001 | TARRANT | 0.023673 | -0.12012 | 0 | 0 |  | 69
CNTRPT_A | CNTRPT-A | 537 | CNTRPT A | 17.5 |  |  |  | NORTH2001 | PARKER | 0.022749 | -0.12024 | 0.39811 | -2.1042 |  | 69
REN | REN | 541 | RENO |  |  |  |  | NORTH2001 | PARKER | 0.022084 | -0.12006 | 0 | 0 |  | 138
REN | REN | 542 | RENO |  |  |  |  | NORTH2001 | PARKER | 0.027947 | -0.11958 | 0 | 0 |  | 69
BRIAR | BRIAR | 545 | BRIAR | 6.07 |  |  |  | NORTH2001 | PARKER | 0.02581 | -0.11985 | 0.15667 | -0.72749 |  | 69
BOYD | BOYD | 548 | BOYD | 5.54 |  |  |  | NORTH2001 | WISE | 0.017895 | -0.12085 | 0.099141 | -0.66952 |  | 69
GRAPEVIN | GRAPEVIN | 555 | GRAPEVIN | 23.6 |  |  |  | NORTH2001 | TARRANT | -0.019726 | -0.12692 | -0.46553 | -2.9953 |  | 138
IBM_ | IBM__ | 556 | IBM | 35.34 |  |  |  | NORTH2001 | TARRANT | -0.020079 | -0.12657 | -0.70959 | -4.4728 |  | 138
|  | 561 | JOPLINSW |  |  |  |  | NORTH2001 | WISE | 0.045805 | -0.1189 | 0 | 0 |  | 69
JOPLIN | JOPLIN | 562 | JOPLIN | 2.81 |  |  |  | NORTH2001 | JACK | 0.045805 | -0.1189 | 0.12871 | -0.3341 |  | 69
KELLR | KELLR | 565 | KELLER | 35.15 |  |  |  | NORTH2001 | TARRANT | -0.020867 | -0.1254 | -0.73347 | -4.4078 |  | 138
KLRSO | KLRSO | 566 | KELERSTH | 37.38 |  |  |  | NORTH2001 | TARRANT | -0.020506 | -0.12405 | -0.76652 | -4.6368 |  | 138
AURORA | AURORA | 572 | AURORA | 4.47 |  |  |  | NORTH2001 | WISE | 0.010476 | -0.12168 | 0.046829 | -0.54393 |  | 138
NEWARK | NEWARK | 573 | NEWARK | 9.77 |  |  |  | NORTH2001 | WISE | 0.017895 | -0.12085 | 0.17484 | -1.1807 |  | 69
RHOMESW | RHOMESW | 575 | RHOMESW |  |  |  |  | NORTH2001 | PARKER | -0.0053006 | -0.12343 | 0 | 0 |  | 138
RHM | RHM | 576 | RHOME |  |  |  |  | NORTH2001 | WISE | 0.0027574 | -0.12277 | 0 | 0 |  | 138
RHM | RHM | 577 | RHOME |  |  |  |  | NORTH2001 | WISE | 0.012575 | -0.12152 | 0 | 0 |  | 69
DECATUR | DECATUR | 583 | DECATUR | 9.97 |  |  |  | NORTH2001 | WISE | 0.0014459 | -0.12417 | 0.014416 | -1.238 |  | 138
WOODIE | WOODIE | 584 | WOODIE | 2.6 |  |  |  | NORTH2001 | WISE | 0.0019755 | -0.1236 | 0.0051363 | -0.32137 |  | 138
CHISOLM | CHISOLM | 585 | CHISOLM | 14.34 |  |  |  | NORTH2001 | WISE | -0.0014968 | -0.12312 | -0.021465 | -1.7655 |  | 138
GRENWOOD | GRENWOOD | 587 | GRENWOOD | 8.25 |  |  |  | NORTH2001 | WISE | 0.00014377 | -0.12557 | 0.0011861 | -1.0359 |  | 138
WILLOW | WILLOW | 588 | WILLOW | 0.41 |  |  |  | NORTH2001 | WISE | 0.044784 | -0.11854 | 0.018361 | -0.048602 |  | 69
KEETER | KEETER | 595 | KEETER | 3.2 |  |  |  | NORTH2001 | WISE | 0.03365 | -0.11936 | 0.10768 | -0.38196 |  | 69
COTNDALE | COTNDALE | 596 | COTNDALE | 8.33 |  |  |  | NORTH2001 | WISE | 0.036759 | -0.11924 | 0.30621 | -0.99329 |  | 69
BRIDGEPR | BRIDGEPR | 600 | BRIDGEPR | 3.25 |  |  |  | NORTH2001 | WISE | 0.056923 | -0.11921 | 0.185 | -0.38744 |  | 69
EBP | EBP | 601 | EBRIDGPR | 5.59 |  |  |  | NORTH2001 | WISE | 0.001347 | -0.12428 | 0.0075299 | -0.69471 |  | 138
CHAMBERS | CHAMBERS | 604 | CHAMBERS |  |  |  |  | NORTH2001 | WISE | 0.060565 | -0.11931 | 0 | 0 |  | 69
|  | 605 | WZZRDWLS |  |  |  |  | NORTH2001 | JACK | 0.052256 | -0.12058 | 0 | 0 |  | 69
CRAFTON | CRAFTON | 608 | CRAFTON | 3.51 |  |  |  | NORTH2001 | WISE | 0.071243 | -0.11962 | 0.25006 | -0.41985 |  | 69
CARTERSW | CARTERSW | 612 | CARTERSW |  |  |  |  | NORTH2001 | MONTAGUE | 0.078801 | -0.11983 | 0 | 0 |  | 69
CARTER | CARTER | 616 | CARTER | 2.78 |  |  |  | NORTH2001 | MONTAGUE | 0.078801 | -0.11983 | 0.21907 | -0.33313 |  | 69
LONESTR | LONESTR | 618 | LONESTAR | 3.47 |  |  |  | NORTH2001 | WISE | 0.068896 | -0.12076 | 0.23907 | -0.41905 |  | 138
BOW | BOW | 620 | BOWIE |  |  |  |  | NORTH2001 | MONTAGUE | 0.072969 | -0.12168 | 0 | 0 |  | 138
BOW | BOW | 621 | BOWIE | 12.08 |  |  |  | NORTH2001 | MONTAGUE | 0.089016 | -0.12012 | 1.0753 | -1.451 |  | 69
BOW | BOW | 622 | BOWIE |  |  |  |  | NORTH2001 | MONTAGUE | 0.077992 | -0.12131 | 0 | 0 |  | 138
BRDGTAP | BRDGTAP | 626 | BRDGTAP |  |  |  |  | NORTH2001 | WISE | 0.001347 | -0.12428 | 0 | 0 |  | 138
NEWPORT | NEWPORT | 631 | NEWPORT | 1.09 |  |  |  | NORTH2001 | MONTAGUE | 0.11042 | -0.11978 | 0.12035 | -0.13056 |  | 138
JOHNSNSW | JOHNSNSW | 632 | JOHNSNSW |  |  |  |  | NORTH2001 | MONTAGUE | 0.097808 | -0.11976 | 0 | 0 |  | 69
MONTAGUE | MONTAGUE | 633 | MONTAGUE |  |  |  |  | NORTH2001 | MONTAGUE | 0.11832 | -0.11891 | 0 | 0 |  | 69
AUDBONSW | AUDBONSW | 634 | AUDBONSW |  |  |  |  | NORTH2001 | WISE | 0.00093949 | -0.12471 | 0 | 0 |  | 138
AUDUBON | AUDUBON | 635 | AUDUBON | 4.63 |  |  |  | NORTH2001 | WISE | 0.00093949 | -0.12471 | 0.0043498 | -0.57743 |  | 138
JOHNSON | JOHNSON | 636 | JOHNSON | 1.72 |  |  |  | NORTH2001 | MONTAGUE | 0.097808 | -0.11976 | 0.16823 | -0.20598 |  | 69
ROANOKE | ROANOKE | 640 | ROANOKE | 18.28 |  |  |  | NORTH2001 | DENTON | -0.018089 | -0.12448 | -0.33067 | -2.2755 |  | 138
LWSSW | LWSSW | 645 | LEWSVLSW |  |  |  |  | NORTH2001 | DENTON | -0.017107 | -0.13069 | 0 | 0 |  | 138
CPL | CPL | 648 | COPPELL |  |  |  |  | NORTH2001 | DALLAS | -0.017762 | -0.12888 | 0 | 0 |  | 138
LEBNONA | LEBNONA | 651 | LEBANON | 34.19 |  |  |  | NORTH2001 | COLLIN | -0.017239 | -0.13161 | -0.5894 | -4.4998 |  | 138
ABR | ABR | 652 | AUBREY | 25.62 |  |  |  | NORTH2001 | DENTON | -0.016179 | -0.12875 | -0.4145 | -3.2985 |  | 138
CST | CST | 655 | CUSTER | 42.03 |  |  |  | NORTH2001 | COLLIN | -0.017079 | -0.13128 | -0.71785 | -5.5177 |  | 138
MOUND | MOUND | 656 | MOUND | 30.83 |  |  |  | NORTH2001 | DENTON | -0.017563 | -0.12943 | -0.54147 | -3.9903 |  | 138
MCKMY | MCKMY | 658 | MCKAMYA | 58.46 |  |  |  | NORTH2001 | DENTON | -0.017762 | -0.12888 | -1.0383 | -7.5344 |  | 138
|  | 659 | BRIDGES | 14.34 |  |  |  | NORTH2001 | COLLIN | -0.01691 | -0.13136 | -0.24249 | -1.8836 |  | 138
LWSVL | LWSVL | 660 | LEWISVIL | 23.64 |  |  |  | NORTH2001 | DENTON | -0.0172 | -0.13043 | -0.40661 | -3.0835 |  | 138
HBR | HBR | 663 | HEBRON | 50.74 |  |  |  | NORTH2001 | DENTON | -0.016906 | -0.13174 | -0.85783 | -6.6843 |  | 138
HILND | HILND | 664 | HIGHLAND | 46.01 |  |  |  | NORTH2001 | DENTON | -0.017087 | -0.13037 | -0.78619 | -5.9981 |  | 138
CANYN | CANYN | 668 | CANYON | 45.69 |  |  |  | NORTH2001 | DENTON | -0.017055 | -0.12985 | -0.77926 | -5.9327 |  | 138
KRUMTMP | KRUM | 670 | KRUM | 8.87 |  |  |  | NORTH2001 | DENTON | -0.01269 | -0.12901 | -0.11256 | -1.1443 |  | 69
LKDALLAS | LKDALLAS | 671 | LKDALLAS | 0.6 |  |  |  | NORTH2001 | DENTON | -0.018232 | -0.12911 | -0.010939 | -0.077463 |  | 138
SANGER | SANGER | 672 | SANGER | 17.64 |  |  |  | NORTH2001 | DENTON | -0.010886 | -0.12818 | -0.19203 | -2.2611 |  | 138
NSANGER | NSANGER | 680 | NSANGER | 17.98 |  |  |  | NORTH2001 | DENTON | -0.0082346 | -0.128 | -0.14806 | -2.3015 |  | 138
FRS | FRS | 681 | FRISCO | 35.16 |  |  |  | NORTH2001 | COLLIN | -0.016937 | -0.13068 | -0.59552 | -4.5947 |  | 138
|  | 682 | DENTON |  |  |  |  | NORTH2001 | DENTON | -0.012517 | -0.12812 | 0 | 0 |  | 138
SPR | SPR | 684 | SPRING |  |  |  |  | NORTH2001 | COOKE | -0.0017314 | -0.12758 | 0 | 0 |  | 138
SPR | SPR | 685 | SPRING |  |  |  |  | NORTH2001 | COOKE | -0.0030935 | -0.12797 | 0 | 0 |  | 69
VALYVIEW | VALYVIEW | 691 | VALYVIEW | 8.02 |  |  |  | NORTH2001 | COOKE | 0.0032538 | -0.12718 | 0.026096 | -1.02 |  | 138
|  | 695 | MUENSTER | 5.5 |  |  |  | NORTH2001 | COOKE | 0.022675 | -0.12565 | 0.12471 | -0.69107 |  | 138
SALEM11 | SALEM11 | 698 | SALEM | 7.83 |  |  |  | NORTH2001 | COOKE | -0.0051923 | -0.12858 | -0.040655 | -1.0068 |  | 69
SALEMSW | SALEMSW | 699 | SALEMSW |  |  |  |  | NORTH2001 | COOKE | -0.004183 | -0.12829 | 0 | 0 |  | 69
REDMNDSW | REDMNDSW | 702 | REDMNDSW |  |  |  |  | NORTH2001 | COOKE | -0.0076486 | -0.12929 | 0 | 0 |  | 69
|  | 704 | MTNSPRGS | 5.51 |  |  |  | NORTH2001 | COOKE | -0.0060592 | -0.12883 | -0.033386 | -0.70986 |  | 69
WOODBINE | WOODBINE | 706 | WOODBINE | 4.93 |  |  |  | NORTH2001 | COOKE | -0.0076486 | -0.12929 | -0.037708 | -0.63741 |  | 69
|  | 710 | WHITSBRO | 4.19 |  |  |  | NORTH2001 | GRAYSON | -0.0087858 | -0.12962 | -0.036812 | -0.54312 |  | 69
NORTH11 | NORTH11 | 714 | NORTH | 10.48 |  |  |  | NORTH2001 | GRAYSON | -0.0087858 | -0.12962 | -0.092075 | -1.3584 |  | 69
WHITSBOR | WHITSBOR | 718 | JORDANSW |  |  |  |  | NORTH2001 | GRAYSON | -0.0087858 | -0.12962 | 0 | 0 |  | 69
|  | 722 | JORDAN |  |  |  |  | NORTH2001 | GRAYSON | -0.0090747 | -0.12971 | 0 | 0 |  | 69
SVLBNDTP | SVLBNDTP | 725 | SVLBNDTP |  |  |  |  | NORTH2001 | COOKE | -0.0076486 | -0.12929 | 0 | 0 |  | 69
GAINSVIL | GAINSVIL | 726 | GAINSVIL | 7.85 |  |  |  | NORTH2001 | COOKE | -0.0076486 | -0.12929 | -0.060042 | -1.0149 |  | 69
SVB | SVB | 727 | SIVLSBND | 2.62 |  |  |  | NORTH2001 | COOKE | -0.0076486 | -0.12929 | -0.020039 | -0.33875 |  | 69
REDRIVER | REDRIVER | 735 | REDRIVER | 6.04 |  |  |  | NORTH2001 | COOKE | -0.0076486 | -0.12929 | -0.046198 | -0.78093 |  | 69
SINCLARS | SINCLARS | 738 | SINCLARS |  |  |  |  | NORTH2001 | COOKE | -0.0076486 | -0.12929 | 0 | 0 |  | 69
SINCLAIR | SINCLAIR | 742 | SINCLAIR | 1.74 |  |  |  | NORTH2001 | COOKE | -0.0076486 | -0.12929 | -0.013309 | -0.22497 |  | 69
WALNBEND | WALNBEND | 744 | WALNBEND | 1.59 |  |  |  | NORTH2001 | COOKE | -0.0076486 | -0.12929 | -0.012161 | -0.20557 |  | 69
SJO | SJO | 746 | STJO |  |  |  |  | NORTH2001 | MONTAGUE | 0.038992 | -0.12436 | 0 | 0 |  | 138
SJO | SJO | 750 | STJO |  |  |  |  | NORTH2001 | MONTAGUE | 0.038992 | -0.12436 | 0 | 0 |  | 69
CAPSCRNR | CAPSCRNR | 754 | CAPSCRNR | 2.78 |  |  |  | NORTH2001 | MONTAGUE | 0.038992 | -0.12436 | 0.1084 | -0.34572 |  | 69
NOCONA | NOCONA | 756 | NOCONA | 3.88 |  |  |  | NORTH2001 | MONTAGUE | 0.038992 | -0.12436 | 0.15129 | -0.48252 |  | 69
ALCORN | ALCORN | 758 | ALCORN | 2.71 |  |  |  | NORTH2001 | MONTAGUE | 0.038992 | -0.12436 | 0.10567 | -0.33702 |  | 69
HARDYSW | HARDYSW | 762 | HARDYSW |  |  |  |  | NORTH2001 | MONTAGUE | 0.049575 | -0.12353 | 0 | 0 |  | 138
HARDY | HARDY | 766 | HARDY | 3.34 |  |  |  | NORTH2001 | MONTAGUE | 0.049575 | -0.12353 | 0.16558 | -0.41258 |  | 138
ORN | ORN | 785 | ORAN |  |  |  |  | NORTH2001 | PALO PINTO | 0.093066 | -0.11567 | 0 | 0 |  | 69
APOLLO | APOLLO | 800 | APOLLO D |  |  |  |  | NORTH2001 | DALLAS | -0.016099 | -0.13369 | 0 | 0 |  | 69
APOLLO | APOLLO | 802 | APOLLO C | 34.69 |  |  |  | NORTH2001 | DALLAS | -0.016862 | -0.13312 | -0.58495 | -4.6181 |  | 138
FAIRDL | FAIRDL | 803 | FAIRDL D | 25.757 |  |  |  | NORTH2001 | DALLAS | -0.015775 | -0.13393 | -0.40631 | -3.4498 |  | 69
ESYSTEM | ESYSTEM | 804 | ESYSTEM |  |  |  |  | NORTH2001 | DALLAS | -0.015668 | -0.13372 | 0 | 0 |  | 69
FAIRDL | FAIRDL | 805 | FAIRDL C |  |  |  |  | NORTH2001 | DALLAS | -0.015762 | -0.13459 | 0 | 0 |  | 138
JUPITR_D | JUPITR D | 806 | JUPITR D | 31.287 |  |  |  | NORTH2001 | DALLAS | -0.015963 | -0.1338 | -0.49945 | -4.186 |  | 69
PRAXAIR | PRAXAIR | 807 | PRAXAIR | 14.568 |  |  |  | NORTH2001 | DALLAS | -0.015631 | -0.13364 | -0.22771 | -1.9469 |  | 69
ESYSTEM | ESYSTEM | 808 | ESYSTEM |  |  |  |  | NORTH2001 | DALLAS | -0.015668 | -0.13372 | 0 | 0 |  | 13
OAKLAN_D | OAKLAN D | 809 | OAKLAN D | 21.232 |  |  |  | NORTH2001 | DALLAS | -0.015547 | -0.13347 | -0.3301 | -2.8339 |  | 69
CNTRVL_D | CNTRVL D | 810 | CNTRVL D | 35.823 |  |  |  | NORTH2001 | DALLAS | -0.015573 | -0.13365 | -0.55786 | -4.7878 |  | 69
W_JOY | W JOY | 811 | W JOY D |  |  |  |  | NORTH2001 | DALLAS | -0.015651 | -0.13449 | 0 | 0 |  | 69
SWINDALL | SWINDALL | 812 | SWINDALL |  |  |  |  | NORTH2001 | HUNT | -0.015864 | -0.13442 | 0 | 0 |  | 138
W_JOY | W JOY | 813 | W JOY C | 32.423 |  |  |  | NORTH2001 | DALLAS | -0.015634 | -0.1351 | -0.5069 | -4.3804 |  | 138
NEWMAN | NEWMAN | 814 | NEWMAN D |  |  |  |  | NORTH2001 | DALLAS | -0.015745 | -0.13397 | 0 | 0 |  | 69
NEWMAN | NEWMAN | 815 | NEWCOM E | 25.757 |  |  |  | NORTH2001 | DALLAS | -0.015745 | -0.13397 | -0.40556 | -3.4507 |  | 14
OLINGR | OLINGR | 816 | OLINGR D |  |  |  |  | NORTH2001 | COLLIN | -0.016049 | -0.13421 | 0 | 0 |  | 69
OLINGR | OLINGR | 818 | OLINGR C | 5.54 |  |  |  | NORTH2001 | COLLIN | -0.016049 | -0.13421 | -0.088912 | -0.74351 |  | 138
LYONS_C | LYONS C | 819 | LYONS C | 26.892 |  |  |  | NORTH2001 | DALLAS | -0.015537 | -0.13545 | -0.41781 | -3.6424 |  | 138
LAWLER_D | LAWLER D | 820 | LAWLER D | 22.367 |  |  |  | NORTH2001 | DALLAS | -0.015909 | -0.13383 | -0.35585 | -2.9935 |  | 69
FIRWHEEL | FIRWHEEL | 821 | FIRWHEEL |  |  |  |  | NORTH2001 | DALLAS | -0.01674 | -0.13329 | 0 | 0 |  | 138
FIRWHEEL | FIRWHEEL | 822 | FIRWHEEL | 14.003 |  |  |  | NORTH2001 | DALLAS | -0.01674 | -0.13329 | -0.23441 | -1.8664 |  | 13
WALNUT1 | WALNUT1 | 823 | WALNUT | 4.909 |  |  |  | NORTH2001 | DALLAS | -0.01577 | -0.13395 | -0.077414 | -0.65755 |  | 69
MILLER_D | MILLER D | 824 | MILLER D | 13.446 |  |  |  | NORTH2001 | DALLAS | -0.015663 | -0.13405 | -0.21061 | -1.8024 |  | 69
NAAMAN_D | NAAMAN D | 825 | NAAMAN D | 24.635 |  |  |  | NORTH2001 | DALLAS | -0.015877 | -0.13387 | -0.39112 | -3.2978 |  | 69
CASTLE_D | CASTLE D | 826 | CASTLE D | 17.852 |  |  |  | NORTH2001 | DALLAS | -0.015835 | -0.1339 | -0.28269 | -2.3903 |  | 69
BRAND_C | BRAND C | 827 | BRAND C | 41.343 |  |  |  | NORTH2001 | DALLAS | -0.015868 | -0.13447 | -0.65602 | -5.5593 |  | 138
SHILOH_C | SHILOH C | 830 | SHILOH C | 54.789 |  |  |  | NORTH2001 | DALLAS | -0.015735 | -0.13467 | -0.86209 | -7.3782 |  | 138
OATES | OATES | 831 | OATES C | 22.367 |  |  |  | NORTH2001 | DALLAS | -0.015396 | -0.13595 | -0.34435 | -3.0407 |  | 138
MCCREE | MCCREE | 832 | MCCREE D |  |  |  |  | NORTH2001 | DALLAS | -0.015517 | -0.13341 | 0 | 0 |  | 69
MCCREE | MCCREE | 834 | MCCREE C | 22.367 |  |  |  | NORTH2001 | DALLAS | -0.01568 | -0.13482 | -0.35071 | -3.0156 |  | 138
MCCREE | MCCREE | 835 | MCCREE2 |  |  |  |  | NORTH2001 | DALLAS | -0.015681 | -0.13482 | 0 | 0 |  | 138
KPSTP | KPSTP | 836 | KRAFT C | 6.664 |  |  |  | NORTH2001 | DALLAS | -0.015742 | -0.13465 | -0.10491 | -0.89727 |  | 138
NEWMAN | NEWMAN | 837 | NEWMAN5 |  | 40 |  |  | NORTH2001 | DALLAS | -0.015745 | -0.13397 | -0.62982 | -5.3588 |  | 14
NEWMAN | NEWMAN | 838 | NEWMAN3 |  | 17 |  |  | NORTH2001 | DALLAS | -0.015745 | -0.13397 | -0.26767 | -2.2775 |  | 14
NEWMAN | NEWMAN | 839 | NEWMAN4 |  | 17 |  |  | NORTH2001 | DALLAS | -0.015745 | -0.13397 | -0.26767 | -2.2775 |  | 14
NEWMAN | NEWMAN | 840 | NEWMAN1 |  | 8 |  |  | NORTH2001 | DALLAS | -0.015745 | -0.13397 | -0.12596 | -1.0718 |  | 14
NEWMAN | NEWMAN | 841 | NEWMAN2 |  | 8 |  |  | NORTH2001 | DALLAS | -0.015745 | -0.13397 | -0.12596 | -1.0718 |  | 14
OLINGR | OLINGR | 842 | OLINGR1 |  |  | 68.381 | 80 | NORTH2001 | COLLIN | -0.016049 | -0.13421 | -1.2839 | -10.7366 |  | 14
OLINGR | OLINGR | 843 | OLINGR2 |  |  | 100.285 | 110 | NORTH2001 | COLLIN | -0.016049 | -0.13421 | -1.7654 | -14.7629 |  | 14
OLINGR | OLINGR | 844 | OLINGR3 |  |  | 136.764 | 150 | NORTH2001 | COLLIN | -0.016049 | -0.13421 | -2.4074 | -20.1312 |  | 14
OLINGR | OLINGR | 845 | OLINGR4 |  | 75 |  |  | NORTH2001 | COLLIN | -0.016049 | -0.13421 | -1.2037 | -10.0656 |  | 14
|  | 850 | BTU380 | 10.7 |  |  |  | NORTH2001 | HOOD | 0.0091013 | -0.10879 | 0.097384 | -1.1641 |  | 69
|  | 851 | BTU373 | 9.5 |  |  |  | NORTH2001 | HOOD | -0.00043775 | -0.10907 | -0.0041586 | -1.0362 |  | 69
|  | 852 | BTU3752 | 5.43 |  |  |  | NORTH2001 | BOSQUE | 0.0013864 | -0.072787 | 0.007528 | -0.39523 |  | 69
|  | 853 | BTU3753 | 9.7 |  |  |  | NORTH2001 | CORYELL | 0.00153 | -0.072753 | 0.014841 | -0.70571 |  | 69
|  | 854 | BTU3755 | 2.35 |  |  |  | NORTH2001 | CORYELL | 0.00153 | -0.072753 | 0.0035956 | -0.17097 |  | 69
|  | 855 | BTU3757 | 10.11 |  |  |  | NORTH2001 | CORYELL | 0.00153 | -0.072753 | 0.015469 | -0.73554 |  | 69
BOW | BOW | 900 | BOWIE-T | 16.524 |  |  |  | NORTH2001 | MONTAGUE | 0.076882 | -0.12139 | 1.2704 | -2.0058 |  | 138
BRDGPORT | BRDGPORT | 902 | BRDGPORT | 10.977 |  |  |  | NORTH2001 | WISE | 0.001347 | -0.12428 | 0.014786 | -1.3642 |  | 138
DENTON_C | DENTON C | 908 | SPNCER D | 50 |  |  |  | NORTH2001 | DENTON | -0.019487 | -0.12807 | -0.97433 | -6.4034 |  | 69
KING_D | KING D | 909 | KING D | 29 |  |  |  | NORTH2001 | DENTON | -0.01919 | -0.12795 | -0.5565 | -3.7105 |  | 69
HICKRY_D | HICKRY D | 910 | HICKRY D | 30 |  |  |  | NORTH2001 | DENTON | -0.019278 | -0.12798 | -0.57833 | -3.8395 |  | 69
DENARCOC | DENARCOC | 911 | DENARCOC | 23 |  |  |  | NORTH2001 | DENTON | -0.019875 | -0.12825 | -0.45714 | -2.9497 |  | 138
DNN | DNN | 912 | N DENT D |  |  |  |  | NORTH2001 | DENTON | -0.019062 | -0.1279 | 0 | 0 |  | 69
LOCUST_D | LOCUST D | 914 | LOCUST D | 50 |  |  |  | NORTH2001 | DENTON | -0.019402 | -0.12803 | -0.97008 | -6.4017 |  | 69
NLSES | NLSES | 915 | N.LAKE D | 30 |  |  |  | NORTH2001 | DENTON | -0.019152 | -0.12793 | -0.57455 | -3.838 |  | 69
AIRPRT_C | AIRPRT C | 916 | JMCSTL C | 22 |  |  |  | NORTH2001 | DENTON | -0.026429 | -0.12649 | -0.58144 | -2.7828 |  | 138
POCKRUSC | POCKRUSC | 917 | POCKRUSC | 22.8 |  |  |  | NORTH2001 | DENTON | -0.021411 | -0.12798 | -0.48817 | -2.918 |  | 138
|  | 918 | TEASLY C | 14 |  |  |  | NORTH2001 | DENTON | -0.02322 | -0.12747 | -0.32507 | -1.7845 |  | 138
SPNCER | SPNCER | 920 | SPNCER1 |  |  | 11.908 | 12 | NORTH2001 | DENTON | -0.019487 | -0.12807 | -0.23384 | -1.5368 |  | 14
SPNCER | SPNCER | 921 | SPNCER2 |  |  | 11.908 | 12 | NORTH2001 | DENTON | -0.019487 | -0.12807 | -0.23384 | -1.5368 |  | 14
SPNCER | SPNCER | 922 | SPNCER3 |  |  | 26.789 | 27 | NORTH2001 | DENTON | -0.019487 | -0.12807 | -0.52614 | -3.4579 |  | 14
SPNCER | SPNCER | 923 | SPNCER4 |  |  | 60.529 | 61 | NORTH2001 | DENTON | -0.019487 | -0.12807 | -1.1887 | -7.8122 |  | 14
SPNCER | SPNCER | 924 | SPNCER5 |  |  | 65.496 | 66 | NORTH2001 | DENTON | -0.019487 | -0.12807 | -1.2861 | -8.4525 |  | 14
DIESEL | DIESEL | 936 | DIESEL D |  |  |  |  | NORTH2001 | HUNT | -0.015759 | -0.13453 | 0 | 0 |  | 69
STEAM | STEAM | 937 | STEAM D |  |  |  |  | NORTH2001 | HUNT | -0.015759 | -0.13453 | 0 | 0 |  | 69
LTV_D | LTV D | 938 | LTV D | 16.576 |  |  |  | NORTH2001 | HUNT | -0.015759 | -0.13453 | -0.26123 | -2.23 |  | 69
TERREL_D | TERREL D | 939 | TERREL D | 27.584 |  |  |  | NORTH2001 | HUNT | -0.015759 | -0.13453 | -0.43471 | -3.711 |  | 69
IND_PK_D | IND PK D | 940 | IND PK D | 13.236 |  |  |  | NORTH2001 | HUNT | -0.015759 | -0.13453 | -0.20859 | -1.7807 |  | 69
MAMIE_D | MAMIE D | 945 | MAMIE D | 3.33 |  |  |  | NORTH2001 | HUNT | -0.015759 | -0.13453 | -0.052479 | -0.448 |  | 69
DENT_RD | DENT RD | 946 | DENT RDD | 14.349 |  |  |  | NORTH2001 | HUNT | -0.015759 | -0.13453 | -0.22613 | -1.9304 |  | 69
ONEAL | ONEAL | 947 | ONEAL D | 14.349 |  |  |  | NORTH2001 | HUNT | -0.015759 | -0.13453 | -0.22613 | -1.9304 |  | 69
STEAM | STEAM | 948 | STEAM1 |  | 20 |  |  | NORTH2001 | HUNT | -0.015759 | -0.13453 | -0.31519 | -2.6907 |  | 14
STEAM | STEAM | 949 | STEAM2 |  |  | 24.024 | 26 | NORTH2001 | HUNT | -0.015759 | -0.13453 | -0.40975 | -3.4979 |  | 14
STEAM | STEAM | 950 | STEAM3 |  |  | 39.446 | 41 | NORTH2001 | HUNT | -0.015759 | -0.13453 | -0.64614 | -5.5159 |  | 14
DIESEL | DIESEL | 952 | DIESELA | 16.576 |  |  |  | NORTH2001 | HUNT | -0.015759 | -0.13453 | -0.26123 | -2.23 |  | 14
BNDVS | BNDVS | 968 | BEN DV C |  |  |  |  | NORTH2001 | DALLAS | -0.01591 | -0.13442 | 0 | 0 |  | 138
BNDVS | BNDVS | 970 | BEN DV B |  |  |  |  | NORTH2001 | DALLAS | -0.015746 | -0.13426 | 0 | 0 |  | 345
GN_S_I | GN S I | 977 | GN S I C |  |  |  |  | NORTH2001 | HUNT | -0.015759 | -0.13453 | 0 | 0 |  | 138
GN_S_I | GN S I | 979 | GN S I D |  |  |  |  | NORTH2001 | HUNT | -0.015759 | -0.13453 | 0 | 0 |  | 69
SPNCER | SPNCER | 982 | DENTON C |  |  |  |  | NORTH2001 | DENTON | -0.020154 | -0.12834 | 0 | 0 |  | 138
|  | 983 | ARCO C |  |  |  |  | NORTH2001 | DENTON | -0.019875 | -0.12825 | 0 | 0 |  | 138
DNN | DNN | 985 | N DENT C |  |  |  |  | NORTH2001 | DENTON | -0.022315 | -0.12751 | 0 | 0 |  | 138
W_DENT | W.DENT | 986 | W.DENT C |  |  |  |  | NORTH2001 | DENTON | -0.028314 | -0.12602 | 0 | 0 |  | 138
W_DENT | W.DENT | 988 | W.DENT B |  |  |  |  | NORTH2001 | DENTON | -0.034524 | -0.12436 | 0 | 0 |  | 345
PKRSW | PKRSW | 1436 | PARKER |  |  |  |  | NORTH2001 | PARKER | -0.05937 | -0.11873 | 0 | 0 |  | 345
CMNSW | CMNSW | 1440 | CMCHE SS |  |  |  |  | NORTH2001 | COMANCHE | -0.016255 | -0.1105 | 0 | 0 |  | 345
CMNSW | CMNSW | 1441 | CMCHE SS |  |  |  |  | NORTH2001 | COMANCHE | -0.0043509 | -0.10609 | 0 | 0 |  | 138
SNSSW | SNSSW | 1469 | SUNSET |  |  |  |  | NORTH2001 | WISE | 0.0875 | -0.12061 | 0 | 0 |  | 138
|  | 1470 | NEWPRT M |  |  |  |  | NORTH2001 | ARCHER | 0.11042 | -0.11978 | 0 | 0 |  | 138
BLVUE | BLVUE | 1547 | BELLEVUE | 1.377 |  |  |  | NORTH2001 | CLAY | 0.13013 | -0.11854 | 0.17919 | -0.16323 |  | 69
|  | 1548 | MONTAG M |  |  |  |  | NORTH2001 | MONTAGUE | 0.11833 | -0.11891 | 0 | 0 |  | 69
BWSRV | BWSRV | 1549 | BOWIESVC | 1.103 |  |  |  | NORTH2001 | MONTAGUE | 0.10924 | -0.11914 | 0.12049 | -0.13141 |  | 69
BOWIE | BOWIE | 1550 | BOWIE | 0.048 |  |  |  | NORTH2001 | MONTAGUE | 0.10705 | -0.11919 | 0.0051382 | -0.0057213 |  | 69
|  | 1552 | WIZRDPOD |  |  |  |  | NORTH2001 | WISE | 0.052256 | -0.12058 | 0 | 0 |  | 69
CHICW | CHICW | 1553 | CHCO W |  |  |  |  | NORTH2001 | WISE | 0.052256 | -0.12058 | 0 | 0 |  | 69
CHICC | CHICC | 1554 | CHCO CS1 | 0.3 |  |  |  | NORTH2001 | JACK | 0.052256 | -0.12058 | 0.015677 | -0.036175 |  | 69
JKSAM | JKSAM | 1555 | JACKAMCO | 1.1 |  |  |  | NORTH2001 | JACK | 0.052256 | -0.12058 | 0.057482 | -0.13264 |  | 69
JKSBR | JKSBR | 1556 | JACK | 10.875 |  |  |  | NORTH2001 | JACK | 0.093064 | -0.11567 | 1.0121 | -1.2579 |  | 69
JKREA | JKREA | 1557 | JACK TRI | 0.195 |  |  |  | NORTH2001 | JACK | 0.093064 | -0.11567 | 0.018147 | -0.022556 |  | 69
JKSSN | JKSSN | 1558 | JACK SIN | 1.493 |  |  |  | NORTH2001 | JACK | 0.093064 | -0.11567 | 0.13894 | -0.1727 |  | 69
LNSTC | LNSTC | 1561 | ALVORD | 4.116 |  |  |  | NORTH2001 | WISE | 0.068896 | -0.12076 | 0.28358 | -0.49706 |  | 138
CHITP | CHITP | 1562 | CHCO W T |  |  |  |  | NORTH2001 | WISE | 0.059738 | -0.12084 | 0 | 0 |  | 138
CHICW | CHICW | 1563 | CHCO W | 11.437 |  |  |  | NORTH2001 | WISE | 0.059738 | -0.12084 | 0.68323 | -1.3821 |  | 138
CHICG | CHICG | 1564 | CHCO GH | 11.726 |  |  |  | NORTH2001 | WISE | 0.058584 | -0.12085 | 0.68695 | -1.4171 |  | 138
BRGPR | BRGPR | 1565 | BRDGPORT | 14.715 |  |  |  | NORTH2001 | WISE | 0.053469 | -0.12089 | 0.7868 | -1.779 |  | 138
DCATR | DCATR | 1566 | DECATUR | 20.725 |  |  |  | NORTH2001 | WISE | 0.033211 | -0.12107 | 0.6883 | -2.5091 |  | 138
DCATR | DCATR | 1567 | DECATUR |  |  |  |  | NORTH2001 | WISE | 0.052256 | -0.12058 | 0 | 0 |  | 69
RHOME | RHOME | 1570 | RHOME | 11.446 |  |  |  | NORTH2001 | WISE | 0.0068471 | -0.12138 | 0.078372 | -1.3893 |  | 138
ORAN | ORAN_ | 1571 | ORAN |  |  |  |  | NORTH2001 | PALO PINTO | 0.08811 | -0.11556 | 0 | 0 |  | 138
ORAN | ORAN_ | 1572 | ORAN | 4.456 |  |  |  | NORTH2001 | PALO PINTO | 0.093064 | -0.11567 | 0.41469 | -0.51543 |  | 69
|  | 1573 | GRAFORPT |  |  |  |  | NORTH2001 | PALO PINTO | 0.093064 | -0.11567 | 0 | 0 |  | 69
|  | 1574 | PALOPNTO | 1.013 |  |  |  | NORTH2001 | PALO PINTO | 0.061051 | -0.11375 | 0.061845 | -0.11522 |  | 138
MNWLW | MNWLW | 1575 | MINWL W | 17.806 |  |  |  | NORTH2001 | PALO PINTO | 0.072031 | -0.11488 | 1.2826 | -2.0455 |  | 138
|  | 1576 | MINWLJCT |  |  |  |  | NORTH2001 | PALO PINTO | 0.069947 | -0.11479 | 0 | 0 |  | 138
MNWLL | MNWLL | 1577 | MINWL 2 | 21.437 |  |  |  | NORTH2001 | PALO PINTO | 0.064294 | -0.11506 | 1.3783 | -2.4666 |  | 138
PLPTP | PLPTP | 1578 | PALOPT M |  |  |  |  | NORTH2001 | PALO PINTO | 0.05724 | -0.1133 | 0 | 0 |  | 138
|  | 1579 | ALEDO TU | 14.373 |  |  |  | NORTH2001 | PARKER | 0.03543 | -0.11801 | 0.50924 | -1.6962 |  | 69
MNWLL | MNWLL | 1580 | MINWL 1 | 19.108 |  |  |  | NORTH2001 | PALO PINTO | 0.064266 | -0.11507 | 1.228 | -2.1987 |  | 138
GRFRD | GRFRD | 1581 | GRAFORD | 0.388 |  |  |  | NORTH2001 | PALO PINTO | 0.093064 | -0.11567 | 0.036109 | -0.04488 |  | 69
LVOAK | LVOAK | 1583 | LIVE OAK | 6.982 |  |  |  | NORTH2001 | PARKER | 0.039156 | -0.11538 | 0.27339 | -0.80556 |  | 69
WTHRW | WTHRW | 1585 | WTHFRD W |  |  |  |  | NORTH2001 | PARKER | 0.054697 | -0.11611 | 0 | 0 |  | 69
WTHRF | WTHRF | 1586 | WTHFRD | 6.227 |  |  |  | NORTH2001 | PARKER | 0.047227 | -0.11657 | 0.29408 | -0.72585 |  | 69
WTHRE | WTHRE | 1587 | WTHFRD E | 7.056 |  |  |  | NORTH2001 | PARKER | 0.04271 | -0.11684 | 0.30136 | -0.82444 |  | 69
LGVST | LGVST | 1588 | LGNVISTA | 13.75 |  |  |  | NORTH2001 | PARKER | 0.040318 | -0.11699 | 0.55437 | -1.6086 |  | 69
SPRTN | SPRTN | 1591 | SPRGTOWN | 5.712 |  |  |  | NORTH2001 | PARKER | 0.029326 | -0.11899 | 0.16751 | -0.67967 |  | 138
WTHSW | WTHSW | 1592 | WTHFRD |  |  |  |  | NORTH2001 | PARKER | 0.029326 | -0.11899 | 0 | 0 |  | 138
LIPAN | LIPAN | 1595 | LIPAN | 2.384 |  |  |  | NORTH2001 | PALO PINTO | 0.048065 | -0.11358 | 0.11459 | -0.27077 |  | 138
BLSRA | BLSRA | 1598 | BALSORA | 4.368 |  |  |  | NORTH2001 | WISE | 0.045805 | -0.1189 | 0.20008 | -0.51934 |  | 69
DLEON | DLEON | 1633 | DELEON | 6.908 |  |  |  | NORTH2001 | COMANCHE | 0.029591 | -0.10524 | 0.20442 | -0.72701 |  | 69.6
CMHTP | CMHTP | 1634 | CMYNHM T |  |  |  |  | NORTH2001 | COMANCHE | 0.029591 | -0.10524 | 0 | 0 |  | 69
CMHBL | CMHBL | 1635 | CMYNHM | 0.28 |  |  |  | NORTH2001 | COMANCHE | 0.029591 | -0.10524 | 0.0082856 | -0.029468 |  | 69
DUBLN | DUBLN | 1636 | DUBLIN | 8.367 |  |  |  | NORTH2001 | ERATH | 0.029591 | -0.10524 | 0.24759 | -0.88056 |  | 138
DUBLN | DUBLN | 1637 | DUBLIN |  |  |  |  | NORTH2001 | ERATH | 0.029591 | -0.10524 | 0 | 0 |  | 69
LNGTP | LNGTP | 1640 | LNGLVL M |  |  |  |  | NORTH2001 | ERATH | 0.098713 | -0.10714 | 0 | 0 |  | 138
STNVL | STNVL | 1641 | STPHVIL | 54.785 |  |  |  | NORTH2001 | ERATH | 0.041581 | -0.10527 | 2.278 | -5.7673 |  | 138
SELDN | SELDN | 1644 | SELDEN M |  |  |  |  | NORTH2001 | ERATH | 0.038603 | -0.10307 | 0 | 0 |  | 138
JNSVL | JNSVL | 1645 | JOHNVL M |  |  |  |  | NORTH2001 | ERATH | 0.028483 | -0.095592 | 0 | 0 |  | 138
WNTSP | WNTSP | 1646 | WALNUTSP | 1.109 |  |  |  | NORTH2001 | BOSQUE | 0.018933 | -0.088533 | 0.020997 | -0.098183 |  | 138
WNTSP | WNTSP | 1647 | WALSPTNP |  |  |  |  | NORTH2001 | BOSQUE | 0.018933 | -0.088533 | 0 | 0 |  | 69.6
|  | 1649 | HASSE M |  |  |  |  | NORTH2001 | COMANCHE | 0.010197 | -0.10519 | 0 | 0 |  | 138
CMNTP | CMNTP | 1650 | CMCHE T |  |  |  |  | NORTH2001 | COMANCHE | 0.0014472 | -0.10573 | 0 | 0 |  | 138
CMNCH | CMNCH | 1651 | CMCHE | 13.965 |  |  |  | NORTH2001 | COMANCHE | 0.0014472 | -0.10573 | 0.02021 | -1.4766 |  | 138
ZEPHR | ZEPHR | 1654 | ZEPHYR M |  |  |  |  | NORTH2001 | BROWN | -0.00088198 | -0.099067 | 0 | 0 |  | 138
BRNSW | BRNSW | 1655 | BRNWD SS |  |  |  |  | NORTH2001 | BROWN | -0.00011657 | -0.097517 | 0 | 0 |  | 138
BRNSO | BRNSO | 1656 | BRNWD S | 50.063 |  |  |  | NORTH2001 | BROWN | -0.00089028 | -0.099084 | -0.04457 | -4.9604 |  | 138
BRNWD | BRNWD | 1661 | BRNWD | 41.995 |  |  |  | NORTH2001 | BROWN | -0.0013748 | -0.10006 | -0.057734 | -4.2022 |  | 138
BRNWD | BRNWD | 1662 | BRNWD |  |  |  |  | NORTH2001 | BROWN | -0.0013748 | -0.10006 | 0 | 0 |  | 69
PRCTR | PRCTR | 1665 | PROCTOR | 1.409 |  |  |  | NORTH2001 | COMANCHE | 0.029591 | -0.10524 | 0.041694 | -0.14829 |  | 69
BLNKT | BLNKT | 1666 | BLANKET | 0.906 |  |  |  | NORTH2001 | BROWN | -0.0013748 | -0.10006 | -0.0012455 | -0.090658 |  | 69
LKBTP | LKBTP | 1669 | LBRNWD T |  |  |  |  | NORTH2001 | BROWN | -0.0013748 | -0.10006 | 0 | 0 |  | 69
LKBRN | LKBRN | 1670 | LBRNWD | 8.908 |  |  |  | NORTH2001 | BROWN | -0.0013748 | -0.10006 | -0.012246 | -0.89137 |  | 69
BANGS | BANGS | 1671 | BANGS | 4.875 |  |  |  | NORTH2001 | BROWN | -0.0013748 | -0.10006 | -0.006702 | -0.48781 |  | 69
TNSKA | TNSKA | 1675 | TNCG 1 G |  |  | 80 | 80 | NORTH2001 | LAMAR | -0.016271 | -0.13268 | -1.3017 | -10.6148 |  | 13.8
TNSKA | TNSKA | 1676 | TNCG 2 G |  |  | 80 | 80 | NORTH2001 | LAMAR | -0.016271 | -0.13268 | -1.3017 | -10.6148 |  | 13.8
TNSKA | TNSKA | 1677 | TNCG 3 G |  |  | 63 | 63 | NORTH2001 | LAMAR | -0.016271 | -0.13268 | -1.0251 | -8.3591 |  | 13.8
LPCCS | LPCCS | 1678 | LPP 1 G |  |  | 167 | 185 | NORTH2001 | LAMAR | -0.016475 | -0.1329 | -3.0479 | -24.5872 |  | 25
LPCCS | LPCCS | 1679 | LPP 2 G |  |  | 167 | 185 | NORTH2001 | LAMAR | -0.016475 | -0.1329 | -3.0479 | -24.5872 |  | 25
LPCCS | LPCCS | 1680 | LPP 3 G |  |  | 116 | 185 | NORTH2001 | LAMAR | -0.016475 | -0.1329 | -3.0479 | -24.5872 |  | 25
LPCCS | LPCCS | 1681 | LPP 4 G |  | 185 |  |  | NORTH2001 | LAMAR | -0.016475 | -0.1329 | -3.0479 | -24.5872 |  | 25
LPCCS | LPCCS | 1682 | LPP 5 G |  | 185 |  |  | NORTH2001 | LAMAR | -0.016475 | -0.1329 | -3.0479 | -24.5872 |  | 25
LPCCS | LPCCS | 1683 | LPP 6 G |  | 185 |  |  | NORTH2001 | LAMAR | -0.016475 | -0.1329 | -3.0479 | -24.5872 |  | 25
LPCCS | LPCCS | 1684 | LAMARPWR |  |  |  |  | NORTH2001 | LAMAR | -0.016475 | -0.1329 | 0 | 0 |  | 345
FMRVL | FMRVL | 1685 | FARM SW |  |  |  |  | NORTH2001 | COLLIN | -0.015969 | -0.13383 | 0 | 0 |  | 345
VLSES | VLSES | 1687 | VAL 1 G |  |  | 163 | 178 | NORTH2001 | FANNIN | -0.015988 | -0.13203 | -2.8459 | -23.5005 |  | 20
VLSES | VLSES | 1688 | VAL 2 G |  |  | 513 | 554 | NORTH2001 | FANNIN | -0.015988 | -0.13203 | -8.8573 | -73.1421 |  | 22
VLSES | VLSES | 1689 | VAL 3 G |  |  | 343 | 394 | NORTH2001 | FANNIN | -0.016789 | -0.13255 | -6.615 | -52.224 |  | 22
VLSES | VLSES | 1690 | VALLEY |  |  |  |  | NORTH2001 | FANNIN | -0.016789 | -0.13255 | 0 | 0 |  | 345
VLSES | VLSES | 1691 | VALLEY |  |  |  |  | NORTH2001 | FANNIN | -0.015988 | -0.13203 | 0 | 0 |  | 138
PRSSW | PRSSW | 1692 | PARIS SS |  |  |  |  | NORTH2001 | LAMAR | -0.016475 | -0.1329 | 0 | 0 |  | 345
PRSSW | PRSSW | 1693 | PARIS SS |  |  |  |  | NORTH2001 | LAMAR | -0.016307 | -0.13271 | 0 | 0 |  | 138
TNSKA | TNSKA | 1694 | TENASKA |  |  |  |  | NORTH2001 | LAMAR | -0.016271 | -0.13268 | 0 | 0 |  | 138
MNSES | MNSES | 1695 | MOSES |  |  |  |  | NORTH2001 | TITUS | -0.016266 | -0.13349 | 0 | 0 |  | 345
MNSES | MNSES | 1696 | MOSES-T |  |  |  |  | NORTH2001 | TITUS | -0.016271 | -0.13348 | 0 | 0 |  | 345
SSPSW | SSPSW | 1697 | SULSP SS |  |  |  |  | NORTH2001 | HOPKINS | -0.015437 | -0.13443 | 0 | 0 |  | 345
SSPSW | SSPSW | 1698 | SULSP SS | 1.609 |  |  |  | NORTH2001 | HOPKINS | -0.015216 | -0.13192 | -0.024482 | -0.21226 |  | 138
MNSES | MNSES | 1701 | MOSES1 G |  |  | 545 | 565 | NORTH2001 | TITUS | -0.016266 | -0.13349 | -9.1901 | -75.4218 |  | 18
MNSES | MNSES | 1702 | MOSES2 G |  |  | 425 | 565 | NORTH2001 | TITUS | -0.016266 | -0.13349 | -9.1901 | -75.4218 |  | 18
MNSES | MNSES | 1703 | MOSES3 G |  |  | 780 | 780 | NORTH2001 | TITUS | -0.016266 | -0.13349 | -12.6873 | -104.1221 |  | 24
SHLMT | SHLMT | 1704 | SHER LM | 6.466 |  |  |  | NORTH2001 | GRAYSON | -0.014056 | -0.13115 | -0.090889 | -0.84803 |  | 138
WBJDN | WBJDN | 1705 | WHTBOR T |  |  |  |  | NORTH2001 | GRAYSON | -0.010334 | -0.13007 | 0 | 0 |  | 138
GET38 | GET38 | 1706 | GAIN E T |  |  |  |  | NORTH2001 | COOKE | -0.0070508 | -0.12912 | 0 | 0 |  | 138
GNSVE | GNSVE | 1707 | GAIN E | 17.994 |  |  |  | NORTH2001 | COOKE | -0.0070508 | -0.12912 | -0.12687 | -2.3233 |  | 138
GNSVL | GNSVL | 1708 | GAIN | 32 |  |  |  | NORTH2001 | COOKE | -0.0059262 | -0.12879 | -0.18964 | -4.1213 |  | 138
GNSVL | GNSVL | 1709 | GAIN |  |  |  |  | NORTH2001 | COOKE | -0.0059262 | -0.12879 | 0 | 0 |  | 69
SHLMT | SHLMT | 1710 | GAIN N | 11.598 |  |  |  | NORTH2001 | GRAYSON | -0.0055045 | -0.12867 | -0.063841 | -1.4923 |  | 138
MNSTR | MNSTR | 1712 | MUENSTER | 5.125 |  |  |  | NORTH2001 | COOKE | -0.0059262 | -0.12879 | -0.030372 | -0.66006 |  | 69
MEMWT | MEMWT | 1713 | MEMC TW |  |  |  |  | NORTH2001 | GRAYSON | -0.015782 | -0.13158 | 0 | 0 |  | 138
|  | 1714 | SHRM TI2 | 12.371 |  |  |  | NORTH2001 | GRAYSON | -0.015616 | -0.13156 | -0.19319 | -1.6275 |  | 138
MEMCS | MEMCS | 1715 | MEMC 1 | 6.754 |  |  |  | NORTH2001 | GRAYSON | -0.015782 | -0.13158 | -0.10659 | -0.88866 |  | 138
SNTJO | SNTJO | 1716 | ST JO M |  |  |  |  | NORTH2001 | MONTAGUE | 0.038992 | -0.12436 | 0 | 0 |  | 69
MEMCS | MEMCS | 1717 | MEMC 2 | 6.754 |  |  |  | NORTH2001 | GRAYSON | -0.015601 | -0.13156 | -0.10537 | -0.88855 |  | 138
GET69 | GET69 | 1718 | GAINRE T |  |  |  |  | NORTH2001 | COOKE | -0.0059262 | -0.12879 | 0 | 0 |  | 69
GTP69 | GTP69 | 1719 | GAINCH T |  |  |  |  | NORTH2001 | COOKE | -0.0059262 | -0.12879 | 0 | 0 |  | 69
GNSTP | GNSTP | 1720 | GAINNS T |  |  |  |  | NORTH2001 | COOKE | -0.0059262 | -0.12879 | 0 | 0 |  | 69
GNSUP | GNSUP | 1721 | GAINNS |  |  |  |  | NORTH2001 | COOKE | -0.0059262 | -0.12879 | 0 | 0 |  | 69
CMPHZ | CMPHZ | 1722 | GAINCH | 0.357 |  |  |  | NORTH2001 | COOKE | -0.0059262 | -0.12879 | -0.0021157 | -0.045979 |  | 69
LBRPD | LBRPD | 1723 | LIBERTY |  |  |  |  | NORTH2001 | HOPKINS | -0.014919 | -0.13002 | 0 | 0 |  | 138
WBOSE | WBOSE | 1724 | SEWHTBOR | 4.971 |  |  |  | NORTH2001 | GRAYSON | -0.011009 | -0.13027 | -0.054723 | -0.64756 |  | 138
GDNTP | GDNTP | 1725 | GORDVL T |  |  |  |  | NORTH2001 | GRAYSON | -0.015457 | -0.13162 | 0 | 0 |  | 69.6
SADLR | SADLR | 1726 | SADLER | 1.46 |  |  |  | NORTH2001 | GRAYSON | -0.015457 | -0.13162 | -0.022567 | -0.19216 |  | 69.6
GDNVL | GDNVL | 1727 | GORDVL | 0.184 |  |  |  | NORTH2001 | GRAYSON | -0.015457 | -0.13162 | -0.002844 | -0.024218 |  | 69.6
WBORO | WBORO | 1728 | WHTBOR |  |  |  |  | NORTH2001 | GRAYSON | -0.015457 | -0.13162 | 0 | 0 |  | 69.6
SHNRW | SHNRW | 1732 | SHER NW | 47.987 |  |  |  | NORTH2001 | GRAYSON | -0.015479 | -0.13161 | -0.74281 | -6.3156 |  | 138
PRNTP | PRNTP | 1733 | PERRIN T |  |  |  |  | NORTH2001 | GRAYSON | -0.015543 | -0.13166 | 0 | 0 |  | 138
FNKTP | FNKTP | 1734 | FINK T |  |  |  |  | NORTH2001 | GRAYSON | -0.015543 | -0.13166 | 0 | 0 |  | 138
FINK | FINK_ | 1735 | FINK | 20.514 |  |  |  | NORTH2001 | GRAYSON | -0.015543 | -0.13166 | -0.31885 | -2.7009 |  | 138
PERIN | PERIN | 1736 | PERRIN | 7.238 |  |  |  | NORTH2001 | GRAYSON | -0.015543 | -0.13166 | -0.1125 | -0.95298 |  | 138
DNIWS | DNIWS | 1737 | DNSN W | 21.682 |  |  |  | NORTH2001 | GRAYSON | -0.015599 | -0.13171 | -0.33821 | -2.8557 |  | 138
DNDMT | DNDMT | 1739 | DNSN D T |  |  |  |  | NORTH2001 | GRAYSON | -0.015668 | -0.13176 | 0 | 0 |  | 138
SHRTI | SHRTI | 1740 | TI TAP |  |  |  |  | NORTH2001 | GRAYSON | -0.015616 | -0.13156 | 0 | 0 |  | 138
LKTXP | LKTXP | 1741 | L TEXOMA | 0.99 |  |  |  | NORTH2001 | GRAYSON | -0.015611 | -0.13172 | -0.015455 | -0.1304 |  | 138
LKTXT | LKTXT | 1742 | LTEXMA T |  |  |  |  | NORTH2001 | GRAYSON | -0.015611 | -0.13172 | 0 | 0 |  | 138
DNINR | DNINR | 1743 | DNSN N | 23.465 |  |  |  | NORTH2001 | GRAYSON | -0.015705 | -0.13179 | -0.36851 | -3.0926 |  | 138
DNISN | DNISN | 1745 | DNSN | 37.169 |  |  |  | NORTH2001 | GRAYSON | -0.015634 | -0.13174 | -0.58111 | -4.8965 |  | 138
SHMNE | SHMNE | 1746 | SHER E | 34.52 |  |  |  | NORTH2001 | GRAYSON | -0.015487 | -0.13162 | -0.53461 | -4.5434 |  | 138
CHMND | CHMND | 1747 | CHERY TU |  |  |  |  | NORTH2001 | GRAYSON | -0.015837 | -0.1319 | 0 | 0 |  | 138
SHRTI | SHRTI | 1749 | SHRM TI1 | 10.71 |  |  |  | NORTH2001 | GRAYSON | -0.015616 | -0.13156 | -0.16725 | -1.409 |  | 138
SHSTH | SHSTH | 1750 | SHER S | 30.224 |  |  |  | NORTH2001 | GRAYSON | -0.01566 | -0.13156 | -0.47331 | -3.9764 |  | 138
VAEGC | VAEGC | 1751 | EVANAL |  |  |  |  | NORTH2001 | GRAYSON | -0.016326 | -0.13163 | 0 | 0 |  | 138
|  | 1753 | MEMC TE |  |  |  |  | NORTH2001 | GRAYSON | -0.015601 | -0.13156 | 0 | 0 |  | 138
VANAL | VANAL | 1754 | VAN AL | 15.505 |  |  |  | NORTH2001 | GRAYSON | -0.016595 | -0.13165 | -0.2573 | -2.0412 |  | 138
ALHUB | ALHUB | 1757 | ALHUB TU |  |  |  |  | NORTH2001 | COLLIN | -0.016263 | -0.1312 | 0 | 0 |  | 138
PAYSW | PAYSW | 1758 | PAYNE | 34.525 |  |  |  | NORTH2001 | GRAYSON | -0.015391 | -0.13154 | -0.53139 | -4.5414 |  | 138
PAYSW | PAYSW | 1759 | PAYNE |  |  |  |  | NORTH2001 | GRAYSON | -0.015457 | -0.13162 | 0 | 0 |  | 69
BNMSW | BNMSW | 1760 | BONHM SS |  |  |  |  | NORTH2001 | GRAYSON | -0.015799 | -0.13203 | 0 | 0 |  | 138
BNMSW | BNMSW | 1761 | BONHM SS |  |  |  |  | NORTH2001 | GRAYSON | -0.015697 | -0.13191 | 0 | 0 |  | 69
BNMNW | BONHMNW | 1762 | BONHM NW | 3.933 |  |  |  | NORTH2001 | FANNIN | -0.015827 | -0.13203 | -0.062249 | -0.51926 |  | 138
BELLS | BELLS | 1763 | PINKHILM |  |  |  |  | NORTH2001 | GRAYSON | -0.015768 | -0.13185 | 0 | 0 |  | 138
BELLS | BELLS | 1764 | BELLS | 3.904 |  |  |  | NORTH2001 | GRAYSON | -0.015582 | -0.13177 | -0.060832 | -0.51442 |  | 69.6
ECTOR | ECTOR | 1765 | ECTOR |  |  |  |  | NORTH2001 | FANNIN | -0.01567 | -0.13187 | 0 | 0 |  | 69
DPREA | DPREA | 1768 | DEPORT |  |  |  |  | NORTH2001 | LAMAR | -0.016054 | -0.13253 | 0 | 0 |  | 138
PRETP | PRETP | 1769 | PARISE T |  |  |  |  | NORTH2001 | LAMAR | -0.016228 | -0.13265 | 0 | 0 |  | 138
LMRTP | LMRTP | 1770 | LAMAR T |  |  |  |  | NORTH2001 | LAMAR | -0.016237 | -0.13266 | 0 | 0 |  | 138
LMRBL | LMRBL | 1771 | LAMAR BM |  |  |  |  | NORTH2001 | LAMAR | -0.016237 | -0.13266 | 0 | 0 |  | 138
LMRBL | LMRBL | 1772 | LMRBM |  |  |  |  | NORTH2001 | LAMAR | -0.016237 | -0.13266 | 0 | 0 |  | 69
PREST | PREST | 1773 | PARIS E | 32.251 |  |  |  | NORTH2001 | LAMAR | -0.016249 | -0.13267 | -0.52406 | -4.2787 |  | 138
PRNTH | PRNTH | 1774 | PARIS N | 43.369 |  |  |  | NORTH2001 | LAMAR | -0.01627 | -0.13268 | -0.70559 | -5.7544 |  | 138
|  | 1775 | PARISN T |  |  |  |  | NORTH2001 | LAMAR | -0.016287 | -0.13267 | 0 | 0 |  | 138
KMBCL | KMBCL | 1776 | PARIS KC | 17.604 |  |  |  | NORTH2001 | LAMAR | -0.016302 | -0.1327 | -0.28698 | -2.3361 |  | 138
PARIS | PARIS | 1777 | PARIS | 37.548 |  |  |  | NORTH2001 | LAMAR | -0.016307 | -0.13271 | -0.61228 | -4.983 |  | 138
PARIS | PARIS | 1778 | PARIS | 0.376 |  |  |  | NORTH2001 | LAMAR | -0.016307 | -0.13271 | -0.0061313 | -0.049899 |  | 69
LMREA | LMREA | 1779 | LAMAR CO |  |  |  |  | NORTH2001 | LAMAR | -0.016307 | -0.13271 | 0 | 0 |  | 69
RCSES | RCSES | 1780 | RCST |  |  |  |  | NORTH2001 | RED RIVER | -0.015822 | -0.13236 | 0 | 0 |  | 138
RCSES | RCSES | 1781 | RCST |  |  |  |  | NORTH2001 | RED RIVER | -0.015822 | -0.13236 | 0 | 0 |  | 69
RCTTP | RCTTP | 1783 | RCST T |  |  |  |  | NORTH2001 | RED RIVER | -0.015822 | -0.13236 | 0 | 0 |  | 69
CLKVL | CLKVL | 1784 | CLARKVL | 14.292 |  |  |  | NORTH2001 | RED RIVER | -0.015822 | -0.13236 | -0.22613 | -1.8917 |  | 69
BAGWL | BAGWL | 1785 | BAGWELL | 0.179 |  |  |  | NORTH2001 | RED RIVER | -0.016237 | -0.13266 | -0.0029065 | -0.023746 |  | 69
PREST | PREST | 1786 | E PARISM |  |  |  |  | NORTH2001 | LAMAR | -0.016237 | -0.13266 | 0 | 0 |  | 138
RCSES | RCSES | 1787 | RCST 1 G |  |  | 92 | 114 | NORTH2001 | RED RIVER | -0.015822 | -0.13236 | -1.8037 | -15.0889 |  | 13.8
BRKTN | BRKTN | 1788 | BRKSTON | 2.232 |  |  |  | NORTH2001 | LAMAR | -0.016307 | -0.13271 | -0.036397 | -0.29621 |  | 69
HNYGR | HNYGR | 1789 | HONEY GR | 5.518 |  |  |  | NORTH2001 | FANNIN | -0.015697 | -0.13191 | -0.086614 | -0.72785 |  | 69
WINDM | WINDM | 1790 | WINDM TU |  |  |  |  | NORTH2001 | FANNIN | -0.015697 | -0.13191 | 0 | 0 |  | 69
MNMIN | MNMIN | 1791 | MOSE MIN |  |  |  |  | NORTH2001 | TITUS | -0.016271 | -0.13348 | 0 | 0 |  | 138
TALTP | TALTP | 1793 | TALCOPOD |  |  |  |  | NORTH2001 | FRANKLIN | -0.015734 | -0.1323 | 0 | 0 |  | 138
MNFTP | MNFTP | 1794 | MOSES T |  |  |  |  | NORTH2001 | TITUS | -0.015661 | -0.13224 | 0 | 0 |  | 138
MNSES | MNSES | 1795 | MOSES | 24 |  |  |  | NORTH2001 | TITUS | -0.016271 | -0.13348 | -0.39051 | -3.2036 |  | 138
SLBLF | SLBLF | 1796 | SUL BLF | 0.746 |  |  |  | NORTH2001 | HOPKINS | -0.015527 | -0.13214 | -0.011583 | -0.09858 |  | 138
SSETP | SSETP | 1797 | RKWELL T |  |  |  |  | NORTH2001 | HOPKINS | -0.01531 | -0.13199 | 0 | 0 |  | 138
SSPNE | SSPNE | 1798 | SULSP E | 24.895 |  |  |  | NORTH2001 | HOPKINS | -0.01531 | -0.13199 | -0.38114 | -3.2858 |  | 138
RWALM | RWALM | 1799 | RKWELL |  |  |  |  | NORTH2001 | HOPKINS | -0.01531 | -0.13199 | 0 | 0 |  | 138
MRTSP | MRTSP | 1800 | MRTN SPG | 12.321 |  |  |  | NORTH2001 | HOPKINS | -0.015266 | -0.13195 | -0.18809 | -1.6258 |  | 138
PRPTP | PRPTP | 1803 | PARS P T |  |  |  |  | NORTH2001 | LAMAR | -0.016307 | -0.13271 | 0 | 0 |  | 69
|  | 1804 | PARS P |  |  |  |  | NORTH2001 | LAMAR | -0.016307 | -0.13271 | 0 | 0 |  | 69
COPER | COPER | 1805 | COOPER | 7.535 |  |  |  | NORTH2001 | DELTA | -0.015458 | -0.13267 | -0.11647 | -0.99963 |  | 69
BONHM | BONHM | 1808 | BONHM | 35.185 |  |  |  | NORTH2001 | FANNIN | -0.015776 | -0.13203 | -0.55507 | -4.6456 |  | 138
WCITY | WCITY | 1809 | WOLF CTY | 5.704 |  |  |  | NORTH2001 | HUNT | -0.015604 | -0.13208 | -0.089005 | -0.75339 |  | 138
CUMBY | CUMBY | 1812 | CUMBY | 2.593 |  |  |  | NORTH2001 | HOPKINS | -0.015369 | -0.13204 | -0.039852 | -0.34239 |  | 69.6
CMBTP | CMBTP | 1813 | CUMBY T |  |  |  |  | NORTH2001 | HOPKINS | -0.015369 | -0.13204 | 0 | 0 |  | 69.6
SSPNG | SSPNG | 1814 | SULSPG | 35.123 |  |  |  | NORTH2001 | HOPKINS | -0.015248 | -0.13194 | -0.53555 | -4.6343 |  | 138
CMBTP | CMBTP | 1815 | CUMBY T | 0.753 |  |  |  | NORTH2001 | HOPKINS | -0.015369 | -0.13204 | -0.011573 | -0.099429 |  | 138
COMSW | COMSW | 1816 | COMM SS |  |  |  |  | NORTH2001 | HUNT | -0.015461 | -0.13212 | 0 | 0 |  | 138
COMSO | COMSO | 1819 | COMM S | 16.808 |  |  |  | NORTH2001 | HUNT | -0.015441 | -0.1321 | -0.25953 | -2.2204 |  | 138
COMRC | COMRC | 1820 | COMM | 18.455 |  |  |  | NORTH2001 | HUNT | -0.015461 | -0.13215 | -0.28534 | -2.4388 |  | 138
COMRC | COMRC | 1821 | COMM |  |  |  |  | NORTH2001 | HUNT | -0.015458 | -0.13267 | 0 | 0 |  | 69
CLKPT | CLKPT | 1822 | COOPLK T |  |  |  |  | NORTH2001 | HOPKINS | -0.015339 | -0.13202 | 0 | 0 |  | 138
CLKPM | CLKPM | 1823 | COOPLK | 3.3 |  |  |  | NORTH2001 | HOPKINS | -0.015339 | -0.13202 | -0.050619 | -0.43566 |  | 138
NYLDV | NYLDV | 1824 | NEYLAND | 3.542 |  |  |  | NORTH2001 | HUNT | -0.015455 | -0.13307 | -0.054742 | -0.47134 |  | 69
|  | 1825 | GREENVIL |  |  |  |  | NORTH2001 | HUNT | -0.015453 | -0.13338 | 0 | 0 |  | 69
CDMIL | CDMIL | 1826 | CADML | 4.637 |  |  |  | NORTH2001 | HUNT | -0.01545 | -0.13384 | -0.071641 | -0.62063 |  | 69
CMETP | CMETP | 1827 | CADMLX T |  |  |  |  | NORTH2001 | HUNT | -0.01545 | -0.13388 | 0 | 0 |  | 69
CMEXP | CMEXP | 1828 | CADMLX | 10.009 |  |  |  | NORTH2001 | HUNT | -0.01545 | -0.13388 | -0.15463 | -1.3401 |  | 69
RCGIN | RCGIN | 1830 | ROYSE GN |  |  |  |  | NORTH2001 | ROCKWALL | -0.015447 | -0.13423 | 0 | 0 |  | 69
BRTNT | BRTNT | 1833 | BRKSTNTP |  |  |  |  | NORTH2001 | LAMAR | -0.016259 | -0.13261 | 0 | 0 |  | 138
RNKSW | RNKSW | 1853 | ROANOKE |  |  |  |  | NORTH2001 | DENTON | -0.036713 | -0.12378 | 0 | 0 |  | 345
RNKSW | RNKSW | 1854 | ROANOKE | 26.974 |  |  |  | NORTH2001 | DENTON | -0.021856 | -0.12479 | -0.58954 | -3.3661 |  | 138
ALLNC | ALLNC | 1855 | ALLIANCE | 43.932 |  |  |  | NORTH2001 | TARRANT | -0.037911 | -0.12328 | -1.6655 | -5.4159 |  | 345
EMSES | EMSES | 1859 | EAGLE MT |  |  |  |  | NORTH2001 | TARRANT | -0.041448 | -0.12181 | 0 | 0 |  | 345
EMSES | EMSES | 1860 | EAGLE MT |  |  |  |  | NORTH2001 | TARRANT | -0.018312 | -0.12168 | 0 | 0 |  | 138
EMSES | EMSES | 1861 | EGMT1 G |  |  | 102 | 116 | NORTH2001 | TARRANT | -0.018312 | -0.12168 | -2.1242 | -14.1151 |  | 15.5
EMSES | EMSES | 1862 | EGMT2 G |  |  | 162 | 182 | NORTH2001 | TARRANT | -0.018312 | -0.12168 | -3.3328 | -22.1461 |  | 20
EMSES | EMSES | 1863 | EGMT3 G |  |  | 335 | 379 | NORTH2001 | TARRANT | -0.018312 | -0.12168 | -6.9403 | -46.1174 |  | 20
BNBSW | BNBSW | 1869 | BENB A T |  |  |  |  | NORTH2001 | TARRANT | -0.032 | -0.11726 | 0 | 0 |  | 345
BNBSW | BNBSW | 1870 | BENB B T |  |  |  |  | NORTH2001 | TARRANT | -0.0297 | -0.11717 | 0 | 0 |  | 345
BNBSW | BNBSW | 1873 | BENBRK |  |  |  |  | NORTH2001 | TARRANT | -0.030626 | -0.11714 | 0 | 0 |  | 345
BNBSW | BNBSW | 1874 | BENBRK A | 32.38 |  |  |  | NORTH2001 | TARRANT | -0.024479 | -0.11896 | -0.79264 | -3.8519 |  | 138
BNBSW | BNBSW | 1875 | BENBRK B | 24.737 |  |  |  | NORTH2001 | TARRANT | -0.022719 | -0.11941 | -0.562 | -2.9539 |  | 138
EVRSW | EVRSW | 1882 | EV WEST |  |  |  |  | NORTH2001 | TARRANT | -0.0080841 | -0.11682 | 0 | 0 |  | 345
EVRSW | EVRSW | 1883 | EVERMN A |  |  |  |  | NORTH2001 | TARRANT | -0.014642 | -0.11933 | 0 | 0 |  | 138
EVRSW | EVRSW | 1884 | EVERMN B |  |  |  |  | NORTH2001 | TARRANT | -0.014423 | -0.11978 | 0 | 0 |  | 138
|  | 1885 | EVER 1BT |  |  |  |  | NORTH2001 | TARRANT | -0.0075632 | -0.11718 | 0 | 0 |  | 345
|  | 1886 | EV EAST |  |  |  |  | NORTH2001 | TARRANT | -0.0068914 | -0.11695 | 0 | 0 |  | 345
|  | 1887 | EVER 2BT |  |  |  |  | NORTH2001 | TARRANT | -0.0076999 | -0.11686 | 0 | 0 |  | 345
DCSES | DCSES | 1888 | DEC T |  |  |  |  | NORTH2001 | HOOD | -0.021873 | -0.11518 | 0 | 0 |  | 345
DCSES | DCSES | 1889 | DEC 1 G |  |  | 764 | 818 | NORTH2001 | HOOD | -0.022012 | -0.11518 | -18.0055 | -94.2195 |  | 24
DCSES | DCSES | 1890 | DECORDVA |  |  |  |  | NORTH2001 | HOOD | -0.022012 | -0.11518 | 0 | 0 |  | 345
DCSES | DCSES | 1891 | DECORDVA |  |  |  |  | NORTH2001 | HOOD | -0.0090726 | -0.1122 | 0 | 0 |  | 138
DCSES | DCSES | 1892 | DECT A G |  |  | 75 | 75 | NORTH2001 | HOOD | -0.0090726 | -0.1122 | -0.68044 | -8.4148 |  | 13.8
DCSES | DCSES | 1893 | DECT B G |  |  | 75 | 75 | NORTH2001 | HOOD | -0.0090726 | -0.1122 | -0.68044 | -8.4148 |  | 13.8
DCSES | DCSES | 1894 | DECT C G |  |  | 71 | 71 | NORTH2001 | HOOD | -0.0090726 | -0.1122 | -0.64415 | -7.966 |  | 13.8
DCSES | DCSES | 1895 | DECT D G |  |  | 71 | 71 | NORTH2001 | HOOD | -0.0090726 | -0.1122 | -0.64415 | -7.966 |  | 13.8
CPSES | CPSES | 1898 | CMPK 1 G |  |  | 1044.08 | 1150 | NORTH2001 | SOMERVELL | -0.026622 | -0.11434 | -30.6155 | -131.4922 |  | 22
CPSES | CPSES | 1899 | CMPK 2 G |  |  | 1077.0601 | 1150 | NORTH2001 | SOMERVELL | -0.026622 | -0.11434 | -30.6155 | -131.4922 |  | 22
CPSES | CPSES | 1900 | COM PEAK | 2.16 |  |  |  | NORTH2001 | SOMERVELL | -0.026622 | -0.11434 | -0.057504 | -0.24698 |  | 345
JONSW | JONSW | 1902 | JOHN SS |  |  |  |  | NORTH2001 | JOHNSON | -0.018321 | -0.11065 | 0 | 0 |  | 345
GRIFPOD | GRIFPOD | 1905 | GRIFTH M |  |  |  |  | NORTH2001 | JOHNSON | -0.010983 | -0.11288 | 0 | 0 |  | 138
VENSW | VENSW | 1906 | VENUS S |  |  |  |  | NORTH2001 | ELLIS | -0.0087354 | -0.10947 | 0 | 0 |  | 345
VENSW | VENSW | 1907 | VENUS N |  |  |  |  | NORTH2001 | ELLIS | -0.011161 | -0.10751 | 0 | 0 |  | 345
VENSW | VENSW | 1908 | VENUS | 6.426 |  |  |  | NORTH2001 | ELLIS | -0.011343 | -0.11433 | -0.072887 | -0.73472 |  | 138
VENSW | VENSW | 1909 | VENSIND1 |  |  |  |  | NORTH2001 | ELLIS | -0.011161 | -0.10751 | 0 | 0 |  | 138
VENSW | VENSW | 1910 | VENSIND2 |  |  |  |  | NORTH2001 | ELLIS | -0.0087354 | -0.10947 | 0 | 0 |  | 138
WEBB | WEBB_ | 1911 | WEBB 1 | 70.087 |  |  |  | NORTH2001 | TARRANT | -0.012203 | -0.11431 | -0.85524 | -8.0116 |  | 345
MAYFD | MAYFD | 1912 | MAYFD NT |  |  |  |  | NORTH2001 | DALLAS | -0.013724 | -0.13131 | 0 | 0 |  | 138
MAYFD | MAYFD | 1913 | MAYFD N | 15.043 |  |  |  | NORTH2001 | DALLAS | -0.013724 | -0.13131 | -0.20646 | -1.9753 |  | 138
MAYFD | MAYFD | 1914 | MAYFD S | 31.846 |  |  |  | NORTH2001 | DALLAS | -0.012551 | -0.12782 | -0.39969 | -4.0707 |  | 138
MAYTP | MAYTP | 1915 | MAYFD ST |  |  |  |  | NORTH2001 | DALLAS | -0.012551 | -0.12782 | 0 | 0 |  | 138
|  | 1916 | LIG2 T |  |  |  |  | NORTH2001 | DALLAS | -0.013644 | -0.12372 | 0 | 0 |  | 345
SHRTP | SHRTP | 1917 | SHERRY T |  |  |  |  | NORTH2001 | TARRANT | -0.0095359 | -0.12486 | 0 | 0 |  | 345
SHRSW | SHRSW | 1918 | SHERRY |  |  |  |  | NORTH2001 | TARRANT | -0.0092057 | -0.12305 | 0 | 0 |  | 345
SHRSW | SHRSW | 1919 | SHERRY A | 23.185 |  |  |  | NORTH2001 | TARRANT | -0.013299 | -0.12616 | -0.30834 | -2.925 |  | 138
SHRSW | SHRSW | 1920 | SHERRY B | 15.348 |  |  |  | NORTH2001 | TARRANT | -0.01329 | -0.12616 | -0.20398 | -1.9362 |  | 138
LIGSW | LIGSW | 1921 | LIGGETT |  |  |  |  | NORTH2001 | DALLAS | -0.01371 | -0.12425 | 0 | 0 |  | 345
LIGSW | LIGSW | 1922 | LIGNORTH |  |  |  |  | NORTH2001 | DALLAS | -0.014802 | -0.12954 | 0 | 0 |  | 138
|  | 1923 | LIGAUTO1 |  |  |  |  | NORTH2001 | DALLAS | -0.014784 | -0.12945 | 0 | 0 |  | 138
|  | 1924 | LIGSOUTH | 25.613 |  |  |  | NORTH2001 | DALLAS | -0.015274 | -0.12877 | -0.39121 | -3.2981 |  | 138
|  | 1925 | LIGAUTO2 |  |  |  |  | NORTH2001 | DALLAS | -0.015244 | -0.12868 | 0 | 0 |  | 138
CNTRY | CNTRY | 1929 | CENTURY1 | 83.862 |  |  |  | NORTH2001 | TARRANT | -0.0093801 | -0.12401 | -0.78664 | -10.3994 |  | 345
CNTRY | CNTRY | 1930 | CENTURY3 | 66.475 |  |  |  | NORTH2001 | TARRANT | -0.0087667 | -0.12189 | -0.58277 | -8.1028 |  | 345
CRTLD | CRTLD | 1931 | COURTLND | 154.842 |  |  |  | NORTH2001 | TARRANT | -0.0090171 | -0.12284 | -1.3962 | -19.0206 |  | 345
KNEDL | KNEDL | 1932 | KENNDLE1 | 65.092 |  |  |  | NORTH2001 | TARRANT | -0.007205 | -0.11778 | -0.46899 | -7.6663 |  | 345
KNEDL | KNEDL | 1933 | KENNDLE2 |  |  |  |  | NORTH2001 | TARRANT | -0.0078648 | -0.11835 | 0 | 0 |  | 345
SYCRK | SYCRK | 1935 | SYCMR CK | 57.665 |  |  |  | NORTH2001 | TARRANT | -0.015289 | -0.11694 | -0.88166 | -6.7432 |  | 345
MDANP | MDANP | 1936 | MELP56NO |  |  |  |  | NORTH2001 | ELLIS | -0.011161 | -0.10751 | 0 | 0 |  | 345
MDANP | MDANP | 1939 | MELP S |  |  |  |  | NORTH2001 | ELLIS | -0.0087354 | -0.10947 | 0 | 0 |  | 345
MDANP | MDANP | 1940 | MELP N |  |  |  |  | NORTH2001 | ELLIS | -0.011161 | -0.10751 | 0 | 0 |  | 345
MDANP | MDANP | 1941 | MELP 1 |  |  | 250 | 280.5 | NORTH2001 | ELLIS | -0.0087354 | -0.10947 | -2.4503 | -30.7071 |  | 21
MDANP | MDANP | 1942 | MELP 2 |  |  | 250 | 280.5 | NORTH2001 | ELLIS | -0.0087354 | -0.10947 | -2.4503 | -30.7071 |  | 21
MDANP | MDANP | 1943 | MELP 3 |  |  | 250 | 280.5 | NORTH2001 | ELLIS | -0.011161 | -0.10751 | -3.1306 | -30.1562 |  | 21
MDANP | MDANP | 1944 | MELP 4 |  |  | 250 | 280.5 | NORTH2001 | ELLIS | -0.011161 | -0.10751 | -3.1306 | -30.1562 |  | 21
HLSES | HLSES | 1945 | HAND 1 G |  |  | 25 | 45 | NORTH2001 | TARRANT | -0.016148 | -0.12247 | -0.72667 | -5.5111 |  | 13
HLSES | HLSES | 1946 | HAND 2 G |  |  | 66 | 80 | NORTH2001 | TARRANT | -0.016148 | -0.12247 | -1.2919 | -9.7975 |  | 13
HLSES | HLSES | 1947 | HAND 3 G |  |  | 368 | 403 | NORTH2001 | TARRANT | -0.015575 | -0.12299 | -6.2769 | -49.5659 |  | 19
HLSES | HLSES | 1948 | HAND 4 G |  |  | 399 | 458 | NORTH2001 | TARRANT | -0.015511 | -0.12336 | -7.104 | -56.4988 |  | 26
HLSES | HLSES | 1949 | HAND 5 G |  |  | 425 | 458 | NORTH2001 | TARRANT | -0.015575 | -0.12299 | -7.1335 | -56.3305 |  | 26
HLSES | HLSES | 1950 | HANDLEYC |  |  |  |  | NORTH2001 | TARRANT | -0.015575 | -0.12299 | 0 | 0 |  | 138
HLSES | HLSES | 1951 | HANDLEYD | 45.034 |  |  |  | NORTH2001 | TARRANT | -0.015511 | -0.12336 | -0.69851 | -5.5554 |  | 138
HLSES | HLSES | 1952 | HANDLEY |  |  |  |  | NORTH2001 | TARRANT | -0.016148 | -0.12247 | 0 | 0 |  | 69
CMTSW | CMTSW | 1955 | CALMONT | 63.661 |  |  |  | NORTH2001 | TARRANT | -0.022097 | -0.11999 | -1.4067 | -7.6388 |  | 138
CMTSW | CMTSW | 1956 | CALMONT | 15.404 |  |  |  | NORTH2001 | TARRANT | -0.022097 | -0.11999 | -0.34038 | -1.8483 |  | 69
SAGNA | SAGNA | 1957 | SAGINAW |  |  |  |  | NORTH2001 | TARRANT | -0.018064 | -0.1227 | 0 | 0 |  | 138
SAGNA | SAGNA | 1958 | SAGINAW |  |  |  |  | NORTH2001 | TARRANT | -0.017283 | -0.12237 | 0 | 0 |  | 69
NMSES | NMSES | 1960 | NMAIN4G |  |  | 70 | 85 | NORTH2001 | TARRANT | -0.019477 | -0.12168 | -1.6556 | -10.3427 |  | 13.2
NMSES | NMSES | 1961 | N MAIN | 46.748 |  |  |  | NORTH2001 | TARRANT | -0.019477 | -0.12168 | -0.91052 | -5.6882 |  | 138
NMAIN | NMAIN | 1964 | N MAIN |  |  |  |  | NORTH2001 | TARRANT | -0.016887 | -0.12207 | 0 | 0 |  | 69
FHLSW | FHLSW | 1967 | FST HILL | 55.495 |  |  |  | NORTH2001 | TARRANT | -0.015277 | -0.11966 | -0.84779 | -6.6406 |  | 138
FHLSW | FHLSW | 1968 | FST HILL |  |  |  |  | NORTH2001 | TARRANT | -0.01585 | -0.12084 | 0 | 0 |  | 69
|  | 1970 | HIGHL ME |  |  |  |  | NORTH2001 | DENTON | -0.017078 | -0.13062 | 0 | 0 |  | 138
LWVJS | LWVJS | 1972 | TU JNS M |  |  |  |  | NORTH2001 | DENTON | -0.0171 | -0.13074 | 0 | 0 |  | 138
ARGYL | ARGYL | 1984 | ARGYLE |  |  |  |  | NORTH2001 | DENTON | -0.017039 | -0.12958 | 0 | 0 |  | 138
CRNTH | CRNTH | 1985 | CORINTH | 78.103 |  |  |  | NORTH2001 | DENTON | -0.018232 | -0.12911 | -1.4239 | -10.0835 |  | 138
KRMTP | KRMTP | 1986 | KRUM T |  |  |  |  | NORTH2001 | DENTON | -0.012548 | -0.12899 | 0 | 0 |  | 138
KRUM | KRUM_ | 1987 | KRUM | 11.664 |  |  |  | NORTH2001 | DENTON | -0.012548 | -0.12899 | -0.14636 | -1.5046 |  | 138
VALVW | VALVW | 1988 | VAL VIEW | 2.608 |  |  |  | NORTH2001 | COOKE | -0.0017527 | -0.12758 | -0.004571 | -0.33273 |  | 138
KRUM | KRUM_ | 1989 | KRUM |  |  |  |  | NORTH2001 | DENTON | 0.052256 | -0.12058 | 0 | 0 |  | 69
|  | 1990 | KRUM MBZ |  |  |  |  | NORTH2001 | DENTON | -0.01269 | -0.12901 | 0 | 0 |  | 138
ARCOT | ARCOT | 1993 | ARCO |  |  |  |  | NORTH2001 | DENTON | -0.019863 | -0.12825 | 0 | 0 |  | 138
KRAFT_C | KRAFT C | 1994 | KRUGRVLE | 12.785 |  |  |  | NORTH2001 | DENTON | -0.017097 | -0.12884 | -0.21859 | -1.6473 |  | 138
|  | 1996 | HIT 1T |  |  |  |  | NORTH2001 | DALLAS | -0.0159 | -0.1302 | 0 | 0 |  | 138
|  | 1997 | HIT 2T |  |  |  |  | NORTH2001 | DALLAS | -0.016032 | -0.13015 | 0 | 0 |  | 138
|  | 1998 | HIT 1 | 4.944 |  |  |  | NORTH2001 | DALLAS | -0.0159 | -0.1302 | -0.078608 | -0.6437 |  | 138
|  | 1999 | HIT 2 | 4.944 |  |  |  | NORTH2001 | DALLAS | -0.016032 | -0.13015 | -0.079262 | -0.64348 |  | 138
IRVNR | IRVNR | 2001 | IV NORTH | 121.547 |  |  |  | NORTH2001 | DALLAS | -0.015729 | -0.1296 | -1.9119 | -15.7525 |  | 138
IBLT1 | IBLT1 | 2002 | IV BLT T |  |  |  |  | NORTH2001 | DALLAS | -0.015498 | -0.12918 | 0 | 0 |  | 138
IRVBL | IRVBL | 2003 | IV BELT1 |  |  |  |  | NORTH2001 | DALLAS | -0.015498 | -0.12918 | 0 | 0 |  | 138
IRVBL | IRVBL | 2004 | IV BELT2 | 43.072 |  |  |  | NORTH2001 | DALLAS | -0.014808 | -0.13115 | -0.63781 | -5.6488 |  | 138
IRVVV | IRVVV | 2006 | IV VAL V |  |  |  |  | NORTH2001 | DALLAS | -0.015561 | -0.12861 | 0 | 0 |  | 138
|  | 2007 | IV VALV2 | 45.464 |  |  |  | NORTH2001 | DALLAS | -0.015044 | -0.12968 | -0.68395 | -5.8959 |  | 138
DFWSW | DFWSW | 2009 | DFW SW | 22.833 |  |  |  | NORTH2001 | TARRANT | -0.015872 | -0.12863 | -0.3624 | -2.9371 |  | 138
|  | 2014 | COPPEL T |  |  |  |  | NORTH2001 | DALLAS | -0.017338 | -0.12859 | 0 | 0 |  | 138
COPEL | COPEL | 2015 | COPPELL | 68.142 |  |  |  | NORTH2001 | DALLAS | -0.017749 | -0.12887 | -1.2095 | -8.7816 |  | 138
EULES | EULES | 2016 | EULESS | 106.129 |  |  |  | NORTH2001 | TARRANT | -0.016549 | -0.12806 | -1.7564 | -13.5909 |  | 138
ROANW | ROANW | 2018 | WROANOKE | 22.848 |  |  |  | NORTH2001 | DENTON | -0.021856 | -0.12479 | -0.49936 | -2.8512 |  | 138
|  | 2019 | KIMBALL1 |  |  |  |  | NORTH2001 | TARRANT | -0.021856 | -0.12479 | 0 | 0 |  | 138
SLAKE | SLAKE | 2020 | STHLAKE | 16.523 |  |  |  | NORTH2001 | TARRANT | -0.021856 | -0.12479 | -0.36113 | -2.0619 |  | 138
GRPVN | GRPVN | 2021 | GV BALL | 98.361 |  |  |  | NORTH2001 | TARRANT | -0.01642 | -0.12877 | -1.6151 | -12.6656 |  | 138
DFWNW | DFWNW | 2022 | DFW NW | 39.213 |  |  |  | NORTH2001 | TARRANT | -0.016358 | -0.12911 | -0.64144 | -5.0626 |  | 138
KIMBL | KIMBL | 2023 | KIMBALL2 | 66.849 |  |  |  | NORTH2001 | TARRANT | -0.017338 | -0.12859 | -1.159 | -8.5964 |  | 138
MCKTP | MCKTP | 2024 | MCKAMY | 61.448 |  |  |  | NORTH2001 | DENTON | -0.01742 | -0.12865 | -1.0704 | -7.9053 |  | 138
|  | 2025 | MCK T |  |  |  |  | NORTH2001 | TARRANT | -0.01742 | -0.12865 | 0 | 0 |  | 138
CLYVL | CLYVL | 2026 | COLYVILE | 66.525 |  |  |  | NORTH2001 | TARRANT | -0.018652 | -0.12676 | -1.2409 | -8.433 |  | 138
BRCRK | BRCRK | 2027 | BEAR CK1 | 49.594 |  |  |  | NORTH2001 | TARRANT | -0.019438 | -0.12628 | -0.96399 | -6.2627 |  | 138
|  | 2029 | KELSOU M |  |  |  |  | NORTH2001 | TARRANT | -0.020506 | -0.12405 | 0 | 0 |  | 138
|  | 2030 | FMPOD TU | 0.292 |  |  |  | NORTH2001 | DENTON | -0.017053 | -0.13083 | -0.0049794 | -0.038204 |  | 138
KLMTP | KLMTP | 2033 | KEL MG T |  |  |  |  | NORTH2001 | TARRANT | -0.021016 | -0.12433 | 0 | 0 |  | 138
KLRMG | KLRMG | 2034 | KEL MAG | 1.367 |  |  |  | NORTH2001 | TARRANT | -0.021016 | -0.12433 | -0.028729 | -0.16996 |  | 138
BRCRK | BRCRK | 2035 | BEAR CK3 | 26.785 |  |  |  | NORTH2001 | TARRANT | -0.020336 | -0.12395 | -0.54471 | -3.32 |  | 138
MDWPK | MDWPK | 2039 | MEAD PRK | 19.363 |  |  |  | NORTH2001 | TARRANT | -0.019119 | -0.12328 | -0.3702 | -2.3871 |  | 138
|  | 2040 | MEADPRK2 |  |  |  |  | NORTH2001 | TARRANT | -0.017473 | -0.12479 | 0 | 0 |  | 138
SMFLD | SMFLD | 2041 | SMITHFD1 | 29.227 |  |  |  | NORTH2001 | TARRANT | -0.017243 | -0.1256 | -0.50397 | -3.671 |  | 138
SMFLD | SMFLD | 2042 | SMITHFD2 | 67.88 |  |  |  | NORTH2001 | TARRANT | -0.019528 | -0.12351 | -1.3255 | -8.3835 |  | 138
WATTP | WATTP | 2043 | WATG N T |  |  |  |  | NORTH2001 | TARRANT | -0.018991 | -0.12321 | 0 | 0 |  | 138
WATTP | WATTP | 2044 | WATG S T |  |  |  |  | NORTH2001 | TARRANT | -0.017544 | -0.12454 | 0 | 0 |  | 138
WTAUG | WTAUG | 2045 | WATUGA 1 | 53.468 |  |  |  | NORTH2001 | TARRANT | -0.017544 | -0.12454 | -0.93806 | -6.6588 |  | 138
WTAUG | WTAUG | 2046 | WATUGA 2 | 31.61 |  |  |  | NORTH2001 | TARRANT | -0.018991 | -0.12321 | -0.60031 | -3.8946 |  | 138
HLTOM | HLTOM | 2047 | HALTOM 1 |  |  |  |  | NORTH2001 | TARRANT | -0.017722 | -0.12391 | 0 | 0 |  | 138
GMINI | GMINI | 2048 | GEMINI 2 | 13.728 |  |  |  | NORTH2001 | TARRANT | -0.017788 | -0.12273 | -0.2442 | -1.6848 |  | 138
GMINI | GMINI | 2049 | GEMINI 1 | 38.173 |  |  |  | NORTH2001 | TARRANT | -0.017837 | -0.12273 | -0.68088 | -4.685 |  | 138
BDFRD | BDFRD | 2050 | BEDFORD | 61.897 |  |  |  | NORTH2001 | TARRANT | -0.017338 | -0.12757 | -1.0732 | -7.8964 |  | 138
BDFWD | BDFWD | 2051 | BD WDSON | 59.567 |  |  |  | NORTH2001 | TARRANT | -0.016777 | -0.12725 | -0.99936 | -7.5801 |  | 138
IBLT2 | IBLT2 | 2053 | IVBLT 2T |  |  |  |  | NORTH2001 | DALLAS | -0.014808 | -0.13115 | 0 | 0 |  | 138
IRVNG | IRVNG | 2054 | IRVING | 65.241 |  |  |  | NORTH2001 | DALLAS | -0.014811 | -0.13211 | -0.96631 | -8.6189 |  | 138
IRVGS | IRVGS | 2055 | IV GRANT | 62.33 |  |  |  | NORTH2001 | DALLAS | -0.014937 | -0.13333 | -0.93101 | -8.3104 |  | 138
AZLE_ | AZLE_ | 2062 | AZLE | 41.281 |  |  |  | NORTH2001 | TARRANT | 0.0049318 | -0.12037 | 0.20359 | -4.9689 |  | 138
EMMCP | EMMCP | 2065 | EMCS | 2.925 |  |  |  | NORTH2001 | TARRANT | -0.0183 | -0.12173 | -0.053527 | -0.35607 |  | 138
RHTP1 | RHTP1 | 2066 | ROSEN 1T |  |  |  |  | NORTH2001 | TARRANT | -0.018133 | -0.12241 | 0 | 0 |  | 138
RHTP2 | RHTP2 | 2067 | ROSEN 2T |  |  |  |  | NORTH2001 | TARRANT | -0.018135 | -0.12241 | 0 | 0 |  | 138
RSNHT | RSNHT | 2068 | ROSEN 1 | 19.61 |  |  |  | NORTH2001 | TARRANT | -0.018133 | -0.12241 | -0.3556 | -2.4005 |  | 138
RSNHT | RSNHT | 2069 | ROSEN 2 | 24.701 |  |  |  | NORTH2001 | TARRANT | -0.018135 | -0.12241 | -0.44794 | -3.0236 |  | 138
BLMND | BLMND | 2070 | BLUE MD2 | 20.346 |  |  |  | NORTH2001 | TARRANT | -0.018093 | -0.12258 | -0.36811 | -2.4941 |  | 138
BLMND | BLMND | 2071 | BLUE MD1 | 27.724 |  |  |  | NORTH2001 | TARRANT | -0.018096 | -0.12257 | -0.50168 | -3.3981 |  | 138
FSCRK | FSCRK | 2077 | FOSIL CK | 93.608 |  |  |  | NORTH2001 | TARRANT | -0.01816 | -0.1223 | -1.6999 | -11.4487 |  | 138
SANSM | SANSM | 2085 | SANSOM 1 | 44.905 |  |  |  | NORTH2001 | TARRANT | -0.019701 | -0.12106 | -0.88467 | -5.4363 |  | 138
SANSM | SANSM | 2086 | SANSOM 2 | 29.515 |  |  |  | NORTH2001 | TARRANT | -0.019677 | -0.12107 | -0.58078 | -3.5734 |  | 138
WSTHL | WSTHL | 2087 | WHILL 13 | 30.569 |  |  |  | NORTH2001 | TARRANT | -0.021621 | -0.1202 | -0.66092 | -3.6745 |  | 138
WSTHL | WSTHL | 2088 | WHILL 24 | 28.741 |  |  |  | NORTH2001 | TARRANT | -0.021621 | -0.1202 | -0.62141 | -3.4548 |  | 138
HERTG | HERTG | 2090 | HRTG | 55.334 |  |  |  | NORTH2001 | TARRANT | -0.018605 | -0.12182 | -1.0295 | -6.7407 |  | 13
HERTG | HERTG | 2091 | HRTG1 |  |  |  |  | NORTH2001 | TARRANT | -0.019483 | -0.12167 | 0 | 0 |  | 138
HERTG | HERTG | 2092 | HRTG2 |  |  |  |  | NORTH2001 | TARRANT | -0.01941 | -0.12172 | 0 | 0 |  | 138
HERTG | HERTG | 2093 | HRTG3 |  |  |  |  | NORTH2001 | TARRANT | -0.016886 | -0.12206 | 0 | 0 |  | 69
LCKHD | LCKHD | 2094 | GEN DYN | 35.58 |  |  |  | NORTH2001 | TARRANT | -0.022097 | -0.11999 | -0.7862 | -4.2693 |  | 69
HLTOM | HLTOM | 2098 | HALTOM 2 | 59.078 |  |  |  | NORTH2001 | TARRANT | -0.017407 | -0.12278 | -1.0284 | -7.2533 |  | 138
RCHLD | RCHLD | 2099 | RICHLN 1 | 27.968 |  |  |  | NORTH2001 | TARRANT | -0.016858 | -0.12288 | -0.47148 | -3.4366 |  | 138
RCHLD | RCHLD | 2100 | RICHLN 2 | 44.086 |  |  |  | NORTH2001 | TARRANT | -0.016611 | -0.12287 | -0.7323 | -5.4168 |  | 138
SPRDL | SPRDL | 2101 | SPGDL1 | 41.483 |  |  |  | NORTH2001 | TARRANT | -0.016858 | -0.12288 | -0.69931 | -5.0973 |  | 138
SPRDL | SPRDL | 2102 | SPGDL2 |  |  |  |  | NORTH2001 | TARRANT | -0.018876 | -0.12211 | 0 | 0 |  | 138
RMTPW | RMTPW | 2103 | RANDL WT |  |  |  |  | NORTH2001 | TARRANT | -0.016548 | -0.12292 | 0 | 0 |  | 138
RMTPE | RMTPE | 2104 | RANDL ET |  |  |  |  | NORTH2001 | TARRANT | -0.016236 | -0.12291 | 0 | 0 |  | 138
RDLML | RDLML | 2105 | RANDL 1 |  |  |  |  | NORTH2001 | TARRANT | -0.016863 | -0.12269 | 0 | 0 |  | 138
RDLML | RDLML | 2106 | RANDL 2 | 51.751 |  |  |  | NORTH2001 | TARRANT | -0.016236 | -0.12291 | -0.84022 | -6.3609 |  | 138
WHTT1 | WHTT1 | 2109 | WHITE 1T |  |  |  |  | NORTH2001 | TARRANT | -0.015471 | -0.12427 | 0 | 0 |  | 138
WHTT2 | WHTT2 | 2110 | WHITE 2T |  |  |  |  | NORTH2001 | TARRANT | -0.015275 | -0.12341 | 0 | 0 |  | 138
WHITE | WHITE | 2111 | WHITE 1 | 24.135 |  |  |  | NORTH2001 | TARRANT | -0.015471 | -0.12427 | -0.37339 | -2.9992 |  | 138
WHITE | WHITE | 2112 | WHITE 2 | 14.816 |  |  |  | NORTH2001 | TARRANT | -0.015275 | -0.12341 | -0.22632 | -1.8284 |  | 138
TRNTY | TRNTY | 2113 | TRINITY1 |  |  |  |  | NORTH2001 | TARRANT | -0.015091 | -0.12367 | 0 | 0 |  | 138
TRNTY | TRNTY | 2114 | TRINITY3 | 26.531 |  |  |  | NORTH2001 | TARRANT | -0.015447 | -0.12483 | -0.40981 | -3.3118 |  | 138
HURST | HURST | 2115 | HURST N | 87.927 |  |  |  | NORTH2001 | TARRANT | -0.015385 | -0.12623 | -1.3527 | -11.0994 |  | 138
HURST | HURST | 2116 | HURST S |  |  |  |  | NORTH2001 | TARRANT | -0.014625 | -0.12431 | 0 | 0 |  | 138
DAVTP | DAVTP | 2117 | DAVIS T |  |  |  |  | NORTH2001 | TARRANT | -0.01537 | -0.12658 | 0 | 0 |  | 138
EULSO | EULSO | 2121 | EU SOUTH | 69.649 |  |  |  | NORTH2001 | TARRANT | -0.014404 | -0.12462 | -1.0032 | -8.6798 |  | 138
PIPLN | PIPLN | 2123 | PIPELINE | 4.762 |  |  |  | NORTH2001 | TARRANT | -0.015333 | -0.12741 | -0.073017 | -0.60674 |  | 138
INAIR | INAIR | 2124 | INT AIR1 | 54.62 |  |  |  | NORTH2001 | TARRANT | -0.014408 | -0.12866 | -0.78694 | -7.0272 |  | 138
INAIR | INAIR | 2125 | INT AIR2 | 18.264 |  |  |  | NORTH2001 | TARRANT | -0.015309 | -0.12796 | -0.27961 | -2.3371 |  | 138
WATSN | WATSN | 2128 | WATSON | 42.222 |  |  |  | NORTH2001 | TARRANT | -0.014006 | -0.12776 | -0.59138 | -5.3942 |  | 138
BRHT1 | BRHT1 | 2133 | BRKHOL1T |  |  |  |  | NORTH2001 | TARRANT | -0.013824 | -0.12735 | 0 | 0 |  | 138
BRHT2 | BRHT2 | 2134 | BRKHOL2T |  |  |  |  | NORTH2001 | TARRANT | -0.01366 | -0.12566 | 0 | 0 |  | 138
BRHLW | BRHLW | 2135 | BRKHOL 1 | 28.646 |  |  |  | NORTH2001 | TARRANT | -0.013824 | -0.12735 | -0.39601 | -3.6481 |  | 138
BRHLW | BRHLW | 2136 | BRKHOL 2 | 36.131 |  |  |  | NORTH2001 | TARRANT | -0.01366 | -0.12566 | -0.49354 | -4.5401 |  | 138
GSTHW | GSTHW | 2137 | GSW 1 | 34.205 |  |  |  | NORTH2001 | TARRANT | -0.013648 | -0.12696 | -0.46682 | -4.3425 |  | 138
GSTHW | GSTHW | 2138 | GSW 2 | 53.666 |  |  |  | NORTH2001 | TARRANT | -0.013541 | -0.12582 | -0.72667 | -6.7523 |  | 138
GNMTR | GNMTR | 2139 | GEN MOT1 | 34.33 |  |  |  | NORTH2001 | TARRANT | -0.013473 | -0.12592 | -0.46252 | -4.3227 |  | 138
GNMTR | GNMTR | 2140 | GEN MOT2 |  |  |  |  | NORTH2001 | TARRANT | -0.013547 | -0.12673 | 0 | 0 |  | 138
AMFTP | AMFTP | 2146 | AM MFG T |  |  |  |  | NORTH2001 | TARRANT | -0.018401 | -0.12245 | 0 | 0 |  | 138
AMMFG | AMMFG | 2147 | AM MFG | 18.382 |  |  |  | NORTH2001 | TARRANT | -0.018401 | -0.12245 | -0.33825 | -2.251 |  | 138
SPDTP | SPDTP | 2148 | SPGDL 2T |  |  |  |  | NORTH2001 | TARRANT | -0.018876 | -0.12211 | 0 | 0 |  | 138
CURIE | CURIE | 2150 | CURRIE | 21.737 |  |  |  | NORTH2001 | TARRANT | -0.019889 | -0.12141 | -0.43234 | -2.6391 |  | 138
BLKST | BLKST | 2151 | BLACKSTN | 64.003 |  |  |  | NORTH2001 | TARRANT | -0.020602 | -0.12095 | -1.3186 | -7.7414 |  | 138
CRSWL | CRSWL | 2152 | CARSWELL | 10.695 |  |  |  | NORTH2001 | TARRANT | -0.021099 | -0.12063 | -0.22565 | -1.2902 |  | 138
DENAV | DENAV | 2157 | DENTN AV | 37.551 |  |  |  | NORTH2001 | TARRANT | -0.017137 | -0.12231 | -0.64351 | -4.593 |  | 69
DUVAL | DUVAL | 2158 | DUVAL | 53.296 |  |  |  | NORTH2001 | TARRANT | -0.016315 | -0.12179 | -0.86952 | -6.491 |  | 69
BRAVT | BRAVT | 2159 | BRYAN T |  |  |  |  | NORTH2001 | TARRANT | -0.016104 | -0.12136 | 0 | 0 |  | 69
BRNAV | BRNAV | 2160 | BRYAN AV | 55.848 |  |  |  | NORTH2001 | TARRANT | -0.016042 | -0.12123 | -0.89592 | -6.7705 |  | 69
MCDON | MCDON | 2161 | MCDONUGH | 0.904 |  |  |  | NORTH2001 | TARRANT | -0.015962 | -0.12107 | -0.01443 | -0.10945 |  | 69
HMPHL | HMPHL | 2164 | HEMPHILL | 74.609 |  |  |  | NORTH2001 | TARRANT | -0.017697 | -0.12209 | -1.3203 | -9.1089 |  | 138
EPDC | EPDC_ | 2166 | EPDC | 44.412 |  |  |  | NORTH2001 | TARRANT | -0.017651 | -0.12233 | -0.78391 | -5.433 |  | 13.2
AYERS | AYERS | 2167 | AYERS | 22.115 |  |  |  | NORTH2001 | TARRANT | -0.016353 | -0.12266 | -0.36165 | -2.7126 |  | 138
EPDC_ | EPDC_ | 2168 | EPDCADUD |  |  |  |  | NORTH2001 | TARRANT | -0.017696 | -0.12209 | 0 | 0 |  | 138
EPDC_ | EPDC_ | 2169 | EPDCSMUD |  |  |  |  | NORTH2001 | TARRANT | -0.015797 | -0.12322 | 0 | 0 |  | 138
EPDC_ | EPDC_ | 2170 | EPDCFRUD |  |  |  |  | NORTH2001 | TARRANT | -0.019461 | -0.12168 | 0 | 0 |  | 138
MSTLT | MSTLT | 2172 | MIST 12 | 27.608 |  |  |  | NORTH2001 | TARRANT | -0.024479 | -0.11896 | -0.67583 | -3.2843 |  | 138
MSTLT | MSTLT | 2173 | MIST 34 | 33.628 |  |  |  | NORTH2001 | TARRANT | -0.018302 | -0.12177 | -0.61547 | -4.0947 |  | 138
HORNE | HORNE | 2174 | HORNE 13 | 45.418 |  |  |  | NORTH2001 | TARRANT | -0.019958 | -0.12088 | -0.90645 | -5.4903 |  | 138
HORNE | HORNE | 2175 | HORNE 24 | 32.807 |  |  |  | NORTH2001 | TARRANT | -0.024479 | -0.11896 | -0.80309 | -3.9027 |  | 138
FARON | FARON | 2176 | FARON 1 | 22.481 |  |  |  | NORTH2001 | TARRANT | -0.024479 | -0.11896 | -0.55032 | -2.6744 |  | 138
FARON | FARON | 2177 | FARON 2 | 32.154 |  |  |  | NORTH2001 | TARRANT | -0.019958 | -0.12088 | -0.64173 | -3.8869 |  | 138
EPDC_ | EPDC_ | 2178 | EPDC1 |  |  |  |  | NORTH2001 | TARRANT | -0.017696 | -0.12209 | 0 | 0 |  | 138
EPDC_ | EPDC_ | 2179 | EPDC2 |  |  |  |  | NORTH2001 | TARRANT | -0.015808 | -0.12322 | 0 | 0 |  | 138
EPDC_ | EPDC_ | 2180 | EPDC3 |  |  |  |  | NORTH2001 | TARRANT | -0.019448 | -0.12169 | 0 | 0 |  | 138
BRIRV | BRIRV | 2182 | BRYT IV1 | 24.461 |  |  |  | NORTH2001 | TARRANT | -0.021396 | -0.1192 | -0.52336 | -2.9156 |  | 138
BRIRV | BRIRV | 2183 | BRYT IV2 | 17.723 |  |  |  | NORTH2001 | TARRANT | -0.020412 | -0.11939 | -0.36175 | -2.1159 |  | 138
WDGTP | WDGTP | 2184 | WDGWD NT |  |  |  |  | NORTH2001 | TARRANT | -0.020353 | -0.11928 | 0 | 0 |  | 138
WDGTP | WDGTP | 2185 | WDGWD ST |  |  |  |  | NORTH2001 | TARRANT | -0.019631 | -0.11938 | 0 | 0 |  | 138
WDGSW | WDGSW | 2186 | WDGWD 1 | 36.273 |  |  |  | NORTH2001 | TARRANT | -0.019631 | -0.11938 | -0.71208 | -4.3303 |  | 138
WDGWD | WDGWD | 2187 | WDGWD 23 | 51.855 |  |  |  | NORTH2001 | TARRANT | -0.020353 | -0.11928 | -1.0554 | -6.185 |  | 138
PFFRD | PFFRD | 2188 | PAFFRD 1 | 24.541 |  |  |  | NORTH2001 | TARRANT | -0.020353 | -0.11928 | -0.49947 | -2.9271 |  | 138
PFFRD | PFFRD | 2189 | PAFFRD 2 | 37.926 |  |  |  | NORTH2001 | TARRANT | -0.019631 | -0.11938 | -0.74453 | -4.5276 |  | 138
EDGCF | EDGCF | 2190 | EDGCLF13 | 52.603 |  |  |  | NORTH2001 | TARRANT | -0.017782 | -0.11936 | -0.93537 | -6.2788 |  | 138
EDGCF | EDGCF | 2191 | EDGCLF 2 | 24.777 |  |  |  | NORTH2001 | TARRANT | -0.017881 | -0.11946 | -0.44303 | -2.9599 |  | 138
ROGRS | ROGRS | 2192 | ROGERS 1 | 28.17 |  |  |  | NORTH2001 | TARRANT | -0.016713 | -0.11935 | -0.47079 | -3.3621 |  | 138
ROGRS | ROGRS | 2193 | ROGERS 2 | 21.647 |  |  |  | NORTH2001 | TARRANT | -0.016452 | -0.11957 | -0.35613 | -2.5884 |  | 138
PRFTW | PRFTW | 2196 | PRIMRSE1 | 40.389 |  |  |  | NORTH2001 | TARRANT | -0.020353 | -0.11928 | -0.82202 | -4.8174 |  | 138
PRFTW | PRFTW | 2197 | PRIMRSE3 |  |  |  |  | NORTH2001 | TARRANT | -0.019631 | -0.11938 | 0 | 0 |  | 138
CRSSN | CRSSN | 2204 | CRESSON | 2.974 |  |  |  | NORTH2001 | PARKER | -0.01585 | -0.12084 | -0.047139 | -0.35937 |  | 69
CRWLY | CRWLY | 2205 | CROWLEY | 3.345 |  |  |  | NORTH2001 | TARRANT | -0.01585 | -0.12084 | -0.053019 | -0.4042 |  | 69
MNFLD | MNFLD | 2208 | MANSFLD | 46.395 |  |  |  | NORTH2001 | TARRANT | -0.013608 | -0.11714 | -0.63136 | -5.4349 |  | 138
BRLSN | BRLSN | 2209 | BURLSON | 69.202 |  |  |  | NORTH2001 | TARRANT | -0.012367 | -0.11452 | -0.85583 | -7.9247 |  | 138
JSHUA | JSHUA | 2210 | JOSHUA | 11.82 |  |  |  | NORTH2001 | JOHNSON | -0.011224 | -0.11209 | -0.13266 | -1.325 |  | 138
RLHT1 | RLHT1 | 2211 | ROLLHL1T |  |  |  |  | NORTH2001 | TARRANT | -0.015148 | -0.11968 | 0 | 0 |  | 138
RLHT2 | RLHT2 | 2212 | ROLLHL2T |  |  |  |  | NORTH2001 | TARRANT | -0.015277 | -0.11966 | 0 | 0 |  | 138
TXSTL | TXSTL | 2213 | TX STL | 7.837 |  |  |  | NORTH2001 | TARRANT | -0.015277 | -0.11966 | -0.11972 | -0.93779 |  | 138
ROLHL | ROLHL | 2214 | ROLL HL1 | 4.718 |  |  |  | NORTH2001 | TARRANT | -0.015148 | -0.11968 | -0.071468 | -0.56465 |  | 138
ROLHL | ROLHL | 2215 | ROLL HL2 |  |  |  |  | NORTH2001 | TARRANT | -0.015277 | -0.11966 | 0 | 0 |  | 138
BWTAT | BWTAT | 2219 | BW/TAT T |  |  |  |  | NORTH2001 | TARRANT | -0.01547 | -0.1227 | 0 | 0 |  | 138
TATTW | TATTW | 2220 | TATE W T |  |  |  |  | NORTH2001 | TARRANT | -0.015229 | -0.12205 | 0 | 0 |  | 138
TATTE | TATTE | 2221 | TATE E T |  |  |  |  | NORTH2001 | TARRANT | -0.015205 | -0.12196 | 0 | 0 |  | 138
TATSP | TATSP | 2222 | TAT SPG1 | 58.943 |  |  |  | NORTH2001 | TARRANT | -0.015229 | -0.12205 | -0.89764 | -7.1942 |  | 138
TATSP | TATSP | 2223 | TAT SPG3 | 26.898 |  |  |  | NORTH2001 | TARRANT | -0.015205 | -0.12196 | -0.40898 | -3.2805 |  | 138
OAKT1 | OAKT1 | 2224 | OAK H 1T |  |  |  |  | NORTH2001 | TARRANT | -0.014946 | -0.12074 | 0 | 0 |  | 138
OAKT2 | OAKT2 | 2225 | OAK H 2T |  |  |  |  | NORTH2001 | TARRANT | -0.014828 | -0.12091 | 0 | 0 |  | 138
OAKHL | OAKHL | 2226 | OAK HIL1 | 30.771 |  |  |  | NORTH2001 | TARRANT | -0.014946 | -0.12074 | -0.45991 | -3.7153 |  | 138
OAKHL | OAKHL | 2227 | OAK HIL2 | 33.718 |  |  |  | NORTH2001 | TARRANT | -0.014828 | -0.12091 | -0.49997 | -4.0769 |  | 138
BWNT2 | BWNT2 | 2232 | BOWEN 2T |  |  |  |  | NORTH2001 | TARRANT | -0.01547 | -0.1227 | 0 | 0 |  | 138
BOWEN | BOWEN | 2233 | BOWEN 2 | 38.524 |  |  |  | NORTH2001 | TARRANT | -0.01547 | -0.1227 | -0.59598 | -4.7269 |  | 138
VGCRK | VGCRK | 2234 | VILGCRK | 22.172 |  |  |  | NORTH2001 | TARRANT | -0.01547 | -0.1227 | -0.34301 | -2.7205 |  | 138
DAVIS | DAVIS | 2239 | DAVIS 1 | 31.726 |  |  |  | NORTH2001 | TARRANT | -0.01547 | -0.1227 | -0.49081 | -3.8928 |  | 138
DAVIS | DAVIS | 2240 | DAVIS 2 | 40.778 |  |  |  | NORTH2001 | TARRANT | -0.01537 | -0.12658 | -0.62674 | -5.1619 |  | 138
ENWSW | ENWSW | 2241 | ENNIS W |  |  |  |  | NORTH2001 | ELLIS | -0.011482 | -0.11911 | 0 | 0 |  | 138
LKWOD | LKWOD | 2245 | LAKEWD 1 | 13.429 |  |  |  | NORTH2001 | TARRANT | -0.015052 | -0.12372 | -0.20213 | -1.6614 |  | 138
LKWOD | LKWOD | 2246 | LAKEWD 2 | 13.893 |  |  |  | NORTH2001 | TARRANT | -0.015 | -0.124 | -0.20839 | -1.7228 |  | 138
PNTGO | PNTGO | 2247 | PANTEGO | 29.864 |  |  |  | NORTH2001 | TARRANT | -0.014597 | -0.12435 | -0.43593 | -3.7137 |  | 138
BOWEN | BOWEN | 2248 | BOWEN 1 | 30.455 |  |  |  | NORTH2001 | TARRANT | -0.014487 | -0.12451 | -0.4412 | -3.7918 |  | 138
BOWEN | BOWEN | 2250 | BOWEN 1T |  |  |  |  | NORTH2001 | TARRANT | -0.014487 | -0.12451 | 0 | 0 |  | 138
ARLNG | ARLNG | 2251 | ARLTON 1 | 48.618 |  |  |  | NORTH2001 | TARRANT | -0.013971 | -0.12522 | -0.67924 | -6.0881 |  | 138
ARLNG | ARLNG | 2252 | ARLTON 2 | 27.928 |  |  |  | NORTH2001 | TARRANT | -0.013946 | -0.12533 | -0.38947 | -3.5002 |  | 138
PRKRW | PRKRW | 2257 | PK ROW 1 | 26.066 |  |  |  | NORTH2001 | TARRANT | -0.013265 | -0.12696 | -0.34576 | -3.3092 |  | 138
PRKRW | PRKRW | 2258 | PK ROW 2 | 34.364 |  |  |  | NORTH2001 | TARRANT | -0.013255 | -0.12687 | -0.45548 | -4.3597 |  | 138
LTV | LTV__ | 2259 | LTV | 19.302 |  |  |  | NORTH2001 | DALLAS | -0.01321 | -0.12776 | -0.25498 | -2.466 |  | 138
PLYAM | PLYAM | 2260 | POLY AM | 16.958 |  |  |  | NORTH2001 | DALLAS | -0.013228 | -0.12782 | -0.22431 | -2.1676 |  | 138
GRDPR | GRDPR | 2262 | GRD PRIE | 64.643 |  |  |  | NORTH2001 | DALLAS | -0.013148 | -0.12902 | -0.84991 | -8.3399 |  | 138
SHDYG | SHDYG | 2270 | SHDY GRV | 61.168 |  |  |  | NORTH2001 | TARRANT | -0.01447 | -0.13008 | -0.88511 | -7.957 |  | 138
IHFT1 | IHFT1 | 2271 | IV HUN T |  |  |  |  | NORTH2001 | DALLAS | -0.014563 | -0.12993 | 0 | 0 |  | 138
IRVHF | IRVHF | 2273 | IV HUNTF |  |  |  |  | NORTH2001 | DALLAS | -0.014563 | -0.12993 | 0 | 0 |  | 138
DALWT | DALWT | 2274 | DALWORTH | 75.565 |  |  |  | NORTH2001 | DALLAS | -0.014113 | -0.13067 | -1.0665 | -9.8741 |  | 138
IRVHF | IRVHF | 2276 | IV HNT 2 | 17.177 |  |  |  | NORTH2001 | DALLAS | -0.014459 | -0.1357 | -0.24837 | -2.3309 |  | 138
DCDAM | DCDAM | 2277 | DECRD SB | 15.144 |  |  |  | NORTH2001 | HOOD | -0.0061764 | -0.11154 | -0.093535 | -1.6891 |  | 138
CPSES | CPSES | 2278 | CPK STUP | 4.23 |  |  |  | NORTH2001 | SOMERVELL | 0.007907 | -0.10988 | 0.033447 | -0.46478 |  | 138
CLBSW | CLBSW | 2279 | CLEB SS |  |  |  |  | NORTH2001 | JOHNSON | -0.010219 | -0.10997 | 0 | 0 |  | 138
CLBNR | CLBNR | 2280 | CLEB N | 48.62 |  |  |  | NORTH2001 | JOHNSON | -0.010062 | -0.11027 | -0.48922 | -5.3616 |  | 138
GODLY | GODLY | 2281 | GODLEY | 4.021 |  |  |  | NORTH2001 | JOHNSON | -0.0099265 | -0.11054 | -0.039914 | -0.44447 |  | 138
|  | 2282 | SQW CK M |  |  |  |  | NORTH2001 | SOMERVELL | 0.007907 | -0.10988 | 0 | 0 |  | 138
|  | 2283 | AIRLQD M |  |  |  |  | NORTH2001 | JOHNSON | -0.010047 | -0.1103 | 0 | 0 |  | 138
CLBRN | CLBRN | 2290 | CLEBURNE | 40.738 |  |  |  | NORTH2001 | JOHNSON | -0.010158 | -0.1097 | -0.4138 | -4.4688 |  | 138
CLBSW | CLBSW | 2291 | CLEB W | 19.352 |  |  |  | NORTH2001 | JOHNSON | -0.0094311 | -0.1065 | -0.18251 | -2.0611 |  | 138
KEENE | KEENE | 2294 | KEENE | 13.913 |  |  |  | NORTH2001 | JOHNSON | -0.01032 | -0.11033 | -0.14358 | -1.535 |  | 138
ALVDO | ALVDO | 2297 | ALVARADO | 11.342 |  |  |  | NORTH2001 | JOHNSON | -0.010623 | -0.11142 | -0.12049 | -1.2637 |  | 138
ALVDO | ALVDO | 2298 | ALVARADO |  |  |  |  | NORTH2001 | JOHNSON | -0.0089975 | -0.10287 | 0 | 0 |  | 69.4
CSTLT | CSTLT | 2300 | CHAPST T |  |  |  |  | NORTH2001 | ELLIS | -0.01147 | -0.11576 | 0 | 0 |  | 138
CHPST | CHPST | 2301 | CHAPSTF1 | 60.493 |  |  |  | NORTH2001 | ELLIS | -0.0087354 | -0.10947 | -0.52843 | -6.6223 |  | 138
CHPST | CHPST | 2302 | CHAPSTF2 | 79.397 |  |  |  | NORTH2001 | ELLIS | -0.011161 | -0.10751 | -0.88614 | -8.5359 |  | 138
CHPST | CHPST | 2304 | CHAPSTML | 54.646 |  |  |  | NORTH2001 | ELLIS | -0.01147 | -0.11576 | -0.62681 | -6.3259 |  | 138
APDTP | APDTP | 2305 | AIRPRD T |  |  |  |  | NORTH2001 | ELLIS | -0.011377 | -0.11536 | 0 | 0 |  | 138
ARPRD | ARPRD | 2306 | AIRPRD | 12.683 |  |  |  | NORTH2001 | ELLIS | -0.011377 | -0.11536 | -0.14429 | -1.4631 |  | 138
MDTXI | MDTXI | 2307 | MIDL TXI | 22.207 |  |  |  | NORTH2001 | ELLIS | -0.011387 | -0.11564 | -0.25286 | -2.5681 |  | 138
MDTHS | MDTHS | 2308 | MIDL S | 9.362 |  |  |  | NORTH2001 | ELLIS | -0.011418 | -0.11658 | -0.1069 | -1.0915 |  | 138
WXHNW | WXHNW | 2309 | WAX NW | 0.576 |  |  |  | NORTH2001 | ELLIS | -0.011491 | -0.11874 | -0.0066186 | -0.068397 |  | 138
MDANP | MDANP | 2310 | MIDL2TXI |  |  |  |  | NORTH2001 | ELLIS | -0.011568 | -0.11686 | 0 | 0 |  | 138
MDNTP | MDNTP | 2311 | MIDL N T |  |  |  |  | NORTH2001 | ELLIS | -0.011828 | -0.11976 | 0 | 0 |  | 138
TRLWD | TRLWD | 2312 | TRAILWD | 60.36 |  |  |  | NORTH2001 | DALLAS | -0.012741 | -0.12995 | -0.76904 | -7.8437 |  | 138
MDTHN | MDTHN | 2313 | MIDL N | 33.702 |  |  |  | NORTH2001 | ELLIS | -0.011828 | -0.11976 | -0.39864 | -4.0361 |  | 138
MDHOL | MDHOL | 2314 | MIDL BOX |  |  |  |  | NORTH2001 | ELLIS | -0.012486 | -0.13211 | 0 | 0 |  | 138
|  | 2316 | MG IND T |  |  |  |  | NORTH2001 | ELLIS | -0.011547 | -0.12042 | 0 | 0 |  | 138
STERT | STERT | 2317 | STERRET | 17.302 |  |  |  | NORTH2001 | ELLIS | -0.011547 | -0.12042 | -0.19978 | -2.0835 |  | 138
STERT | STERT | 2318 | STERRET |  |  |  |  | NORTH2001 | ELLIS | -0.010664 | -0.11735 | 0 | 0 |  | 69.6
WXPM1 | WXPM1 | 2319 | WAX PMP | 5.34 |  |  |  | NORTH2001 | ELLIS | -0.011545 | -0.12038 | -0.06165 | -0.64282 |  | 138
WXNTH | WXNTH | 2320 | WAX N | 36.514 |  |  |  | NORTH2001 | ELLIS | -0.01154 | -0.12027 | -0.42135 | -4.3915 |  | 138
WXHCH | WXHCH | 2321 | WAXAHCHE | 38.026 |  |  |  | NORTH2001 | ELLIS | -0.011522 | -0.11992 | -0.43815 | -4.56 |  | 138
|  | 2322 | BARDWELL |  |  |  |  | NORTH2001 | ELLIS | -0.0092482 | -0.10381 | 0 | 0 |  | 69
MGIND | MGIND | 2323 | MG IND | 10.461 |  |  |  | NORTH2001 | ELLIS | -0.011547 | -0.12042 | -0.12079 | -1.2597 |  | 138
ENSSO | ENSSO | 2324 | ENNIS S | 29.272 |  |  |  | NORTH2001 | ELLIS | -0.011466 | -0.11878 | -0.33564 | -3.477 |  | 138
ENNIS | ENNIS | 2325 | ENNIS | 30.556 |  |  |  | NORTH2001 | ELLIS | -0.011461 | -0.11867 | -0.35019 | -3.626 |  | 138
|  | 2327 | TRUMBULL |  |  |  |  | NORTH2001 | ELLIS | -0.011625 | -0.12173 | 0 | 0 |  | 138
RDOAK | RDOAK | 2328 | RED OAK | 30.361 |  |  |  | NORTH2001 | ELLIS | -0.011762 | -0.12377 | -0.35712 | -3.7578 |  | 138
ENSSW | ENSSW | 2329 | ENNIS SS |  |  |  |  | NORTH2001 | ELLIS | -0.011446 | -0.11837 | 0 | 0 |  | 138
CRISP | CRISP | 2330 | CRISP | 3.742 |  |  |  | NORTH2001 | ELLIS | -0.011421 | -0.1179 | -0.042738 | -0.44116 |  | 138
ENPTP | ENPTP | 2331 | ENIS PMP |  |  |  |  | NORTH2001 | ELLIS | -0.011364 | -0.11681 | 0 | 0 |  | 138
TELTP | TELTP | 2332 | TELICO M |  |  |  |  | NORTH2001 | ELLIS | -0.011276 | -0.11513 | 0 | 0 |  | 138
WXHCH | WXHCH | 2335 | WAXAHCHE |  |  |  |  | NORTH2001 | ELLIS | -0.0095529 | -0.10996 | 0 | 0 |  | 69.6
FRSTN | FRSTN | 2336 | FORESTON | 2.626 |  |  |  | NORTH2001 | ELLIS | -0.0088877 | -0.1054 | -0.023339 | -0.27678 |  | 69.6
ITALY | ITALY | 2337 | ITALY | 5.178 |  |  |  | NORTH2001 | ELLIS | -0.0084613 | -0.10248 | -0.043812 | -0.53063 |  | 69.6
MEXTP | MEXTP | 2338 | MILEXN T |  |  |  |  | NORTH2001 | ELLIS | -0.0080694 | -0.099792 | 0 | 0 |  | 69.6
MLFEX | MLFEX | 2339 | MIL EXXN | 1.1 |  |  |  | NORTH2001 | ELLIS | -0.0080694 | -0.099792 | -0.0088763 | -0.10977 |  | 69.6
FERIS | FERIS | 2342 | FERRIS | 10.561 |  |  |  | NORTH2001 | ELLIS | -0.011509 | -0.1268 | -0.12155 | -1.3391 |  | 69.6
WXOCF | WXOCF | 2343 | WAX OCF | 34.202 |  |  |  | NORTH2001 | ELLIS | -0.0106 | -0.11713 | -0.36253 | -4.0061 |  | 69.6
PALMR | PALMR | 2344 | PALMER | 4.535 |  |  |  | NORTH2001 | ELLIS | -0.011402 | -0.12393 | -0.051708 | -0.56202 |  | 69.6
ENNIS | ENNIS | 2345 | ENNIS |  |  |  |  | NORTH2001 | ELLIS | -0.01128 | -0.12068 | 0 | 0 |  | 69.6
ALMA | ALMA_ | 2346 | ALMA | 2.678 |  |  |  | NORTH2001 | ELLIS | -0.011162 | -0.11753 | -0.029893 | -0.31475 |  | 69.6
RICE | RICE_ | 2347 | RICE TPL | 2.215 |  |  |  | NORTH2001 | NAVARRO | -0.011097 | -0.11578 | -0.024579 | -0.25644 |  | 69.6
RICE | RICE_ | 2348 | RICE REA |  |  |  |  | NORTH2001 | NAVARRO | -0.011039 | -0.11423 | 0 | 0 |  | 69.6
|  | 2351 | INDIA | 2.1 |  |  |  | NORTH2001 | ELLIS | -0.012129 | -0.11836 | -0.025471 | -0.24855 |  | 69
RENSW | RENSW | 2352 | RNRTPL W |  |  |  |  | NORTH2001 | COLLIN | -0.017248 | -0.13277 | 0 | 0 |  | 138
RENSW | RENSW | 2353 | RNRTPL E | 29.635 |  |  |  | NORTH2001 | COLLIN | -0.017248 | -0.13278 | -0.51113 | -3.9348 |  | 138
RENSW | RENSW | 2354 | RENERTPL |  |  |  |  | NORTH2001 | COLLIN | -0.017256 | -0.13277 | 0 | 0 |  | 138
RENSW | RENSW | 2355 | RENERTPL |  |  |  |  | NORTH2001 | COLLIN | -0.018139 | -0.13216 | 0 | 0 |  | 345
RENSW | RENSW | 2356 | RNRDPL N |  |  |  |  | NORTH2001 | COLLIN | -0.016209 | -0.13581 | 0 | 0 |  | 138
RENSW | RENSW | 2357 | RNRDPL S |  |  |  |  | NORTH2001 | COLLIN | -0.016215 | -0.13581 | 0 | 0 |  | 138
RENSW | RENSW | 2358 | RENERDPL |  |  |  |  | NORTH2001 | COLLIN | -0.01622 | -0.1358 | 0 | 0 |  | 138
RENSW | RENSW | 2359 | RENERDPL |  |  |  |  | NORTH2001 | COLLIN | -0.018242 | -0.13208 | 0 | 0 |  | 345
CRLNW | CRLNW | 2360 | CLT NW T |  |  |  |  | NORTH2001 | DALLAS | -0.016926 | -0.13207 | 0 | 0 |  | 138
CRLNW | CRLNW | 2361 | CLT NW |  |  |  |  | NORTH2001 | DALLAS | -0.02032 | -0.12987 | 0 | 0 |  | 345
CRLNW | CRLNW | 2362 | CLT NW E |  |  |  |  | NORTH2001 | DALLAS | -0.016903 | -0.13205 | 0 | 0 |  | 138
CRLNW | CRLNW | 2363 | CLT NW W |  |  |  |  | NORTH2001 | DALLAS | -0.016889 | -0.13213 | 0 | 0 |  | 138
|  | 2367 | N LAKE T |  |  |  |  | NORTH2001 | DALLAS | -0.016376 | -0.13284 | 0 | 0 |  | 138
|  | 2369 | WHTOAKS | 34.893 |  |  |  | NORTH2001 | COLLIN | -0.017188 | -0.13151 | -0.59975 | -4.5886 |  | 138
CNSES | CNSES | 2370 | COLLIN | 25.969 |  |  |  | NORTH2001 | COLLIN | -0.016915 | -0.13094 | -0.43926 | -3.4004 |  | 138
CNSES | CNSES | 2371 | COLL1 G |  |  | 147 | 156 | NORTH2001 | COLLIN | -0.016915 | -0.13094 | -2.6387 | -20.4266 |  | 18
ANASW | ANASW | 2373 | ANNA SS |  |  |  |  | NORTH2001 | COLLIN | -0.018165 | -0.13141 | 0 | 0 |  | 345
ANASW | ANASW | 2374 | ANNA SS |  |  |  |  | NORTH2001 | COLLIN | -0.017282 | -0.13171 | 0 | 0 |  | 138
HEBRN | HEBRN | 2376 | HEBRN SS |  |  |  |  | NORTH2001 | DENTON | -0.016906 | -0.13174 | 0 | 0 |  | 138
NLSES | NLSES | 2381 | NLK 1 G |  |  | 162 | 175 | NORTH2001 | DALLAS | -0.016376 | -0.13284 | -2.8658 | -23.2462 |  | 13.8
NLSES | NLSES | 2382 | NLK 2 G |  |  | 162 | 181 | NORTH2001 | DALLAS | -0.016376 | -0.13284 | -2.9641 | -24.0432 |  | 18
NLSES | NLSES | 2383 | NLK 3 G |  |  | 323 | 368 | NORTH2001 | DALLAS | -0.016376 | -0.13284 | -6.0265 | -48.8834 |  | 20
|  | 2385 | N LAKE S |  |  |  |  | NORTH2001 | DALLAS | -0.016379 | -0.13285 | 0 | 0 |  | 138
N_LAKE_D | N.LAKE D | 2386 | N LAKE N |  |  |  |  | NORTH2001 | DALLAS | -0.016381 | -0.1328 | 0 | 0 |  | 138
HKBRY | HKBRY | 2387 | HACKBRY | 64.452 |  |  |  | NORTH2001 | DALLAS | -0.018048 | -0.1295 | -1.1632 | -8.3465 |  | 345
HKBRY | HKBRY | 2388 | HACKBRY | 106.318 |  |  |  | NORTH2001 | DALLAS | -0.016133 | -0.13034 | -1.7152 | -13.8572 |  | 138
VLYRN | VLYRN | 2389 | IV VR |  |  |  |  | NORTH2001 | DALLAS | -0.01745 | -0.12937 | 0 | 0 |  | 345
|  | 2390 | IV VR1 | 59.574 |  |  |  | NORTH2001 | DALLAS | -0.016139 | -0.13347 | -0.96145 | -7.9514 |  | 138
|  | 2393 | IV VR2 | 57.997 |  |  |  | NORTH2001 | DALLAS | -0.016257 | -0.13157 | -0.94286 | -7.6305 |  | 138
WLVEE | WLVEE | 2396 | W LEVP2 |  |  |  |  | NORTH2001 | DALLAS | -0.011901 | -0.16695 | 0 | 0 |  | 345
WLVEE | WLVEE | 2397 | W LEVP1 |  |  |  |  | NORTH2001 | DALLAS | -0.012214 | -0.1633 | 0 | 0 |  | 345
WLVEE | WLVEE | 2398 | W LEVEE |  |  |  |  | NORTH2001 | DALLAS | -0.01247 | -0.16031 | 0 | 0 |  | 345
WLVEE | WLVEE | 2399 | WLEVEE E |  |  |  |  | NORTH2001 | DALLAS | -0.013671 | -0.1464 | 0 | 0 |  | 138
WLVEE | WLVEE | 2400 | WLEVEE W |  |  |  |  | NORTH2001 | DALLAS | -0.013639 | -0.14663 | 0 | 0 |  | 138
LHSES | LHSES | 2401 | L HUB W |  |  |  |  | NORTH2001 | DALLAS | -0.014531 | -0.13962 | 0 | 0 |  | 138
LHSES | LHSES | 2402 | L HUB E |  |  |  |  | NORTH2001 | DALLAS | -0.014531 | -0.13962 | 0 | 0 |  | 138
LHSES | LHSES | 2403 | L HUB T |  |  |  |  | NORTH2001 | DALLAS | -0.014531 | -0.13962 | 0 | 0 |  | 138
|  | 2404 | NORWDTIE |  |  |  |  | NORTH2001 | DALLAS | -0.014779 | -0.13517 | 0 | 0 |  | 138
|  | 2405 | NORWDPLW |  |  |  |  | NORTH2001 | DALLAS | -0.014774 | -0.13524 | 0 | 0 |  | 138
NORSW | NORSW | 2406 | NORWD |  |  |  |  | NORTH2001 | DALLAS | -0.014177 | -0.12863 | 0 | 0 |  | 345
IRVND | IRVND | 2407 | NORWDPLE |  |  |  |  | NORTH2001 | DALLAS | -0.014777 | -0.13518 | 0 | 0 |  | 138
IRVND | IRVND | 2408 | NORWOD 1 | 56.49 |  |  |  | NORTH2001 | DALLAS | -0.014821 | -0.13489 | -0.83726 | -7.6199 |  | 138
IRVND | IRVND | 2409 | NORWOD 2 |  |  |  |  | NORTH2001 | DALLAS | -0.014828 | -0.13488 | 0 | 0 |  | 138
NORSW | NORSW | 2410 | NORWOODT |  |  |  |  | NORTH2001 | DALLAS | -0.014126 | -0.1287 | 0 | 0 |  | 345
MCSES | MCSES | 2411 | MT CRK W |  |  |  |  | NORTH2001 | DALLAS | -0.013536 | -0.13724 | 0 | 0 |  | 138
MCSES | MCSES | 2412 | MT CRK E |  |  |  |  | NORTH2001 | DALLAS | -0.013538 | -0.13723 | 0 | 0 |  | 138
MCSES | MCSES | 2413 | MTCK 6 G |  |  | 105 | 117 | NORTH2001 | DALLAS | -0.013537 | -0.13723 | -1.5839 | -16.0561 |  | 13.8
MCSES | MCSES | 2414 | MTCK 7 G |  |  | 105 | 127 | NORTH2001 | DALLAS | -0.013537 | -0.13723 | -1.7192 | -17.4284 |  | 15
MCSES | MCSES | 2415 | MT CRK T |  |  |  |  | NORTH2001 | DALLAS | -0.013537 | -0.13723 | 0 | 0 |  | 138
MCSES | MCSES | 2416 | MT CREEK |  |  |  |  | NORTH2001 | DALLAS | -0.013431 | -0.13502 | 0 | 0 |  | 69.6
MCSES | MCSES | 2417 | MTCK 8 G |  |  | 531 | 565 | NORTH2001 | DALLAS | -0.013537 | -0.13723 | -7.6486 | -77.5357 |  | 22.8
MCSES | MCSES | 2418 | MTCK 2 G |  |  | 29 | 33 | NORTH2001 | DALLAS | -0.013431 | -0.13502 | -0.44323 | -4.4556 |  | 13.8
MCSES | MCSES | 2419 | MTCK 3 G |  |  | 63 | 70 | NORTH2001 | DALLAS | -0.013431 | -0.13502 | -0.94018 | -9.4512 |  | 13.8
CDHSW | CDHSW | 2420 | C HILL |  |  |  |  | NORTH2001 | DALLAS | -0.011087 | -0.13162 | 0 | 0 |  | 345
CDHSW | CDHSW | 2421 | C HILL S |  |  |  |  | NORTH2001 | DALLAS | -0.012973 | -0.13253 | 0 | 0 |  | 138
CDHSW | CDHSW | 2422 | C HILL N |  |  |  |  | NORTH2001 | DALLAS | -0.012979 | -0.13254 | 0 | 0 |  | 138
DESSW | DESSW | 2424 | DESOTO |  |  |  |  | NORTH2001 | DALLAS | -0.011846 | -0.12502 | 0 | 0 |  | 138
|  | 2425 | DES PKVL | 34.827 |  |  |  | NORTH2001 | DALLAS | -0.012031 | -0.12779 | -0.41899 | -4.4507 |  | 138
GLNHT | GLNHT | 2426 | GL HGHTM |  |  |  |  | NORTH2001 | ELLIS | -0.011771 | -0.12386 | 0 | 0 |  | 138
WTRML | WTRML | 2427 | WATMILLW |  |  |  |  | NORTH2001 | DALLAS | -0.011542 | -0.16874 | 0 | 0 |  | 345
WTRML | WTRML | 2428 | WATMILLE |  |  |  |  | NORTH2001 | DALLAS | -0.011566 | -0.17087 | 0 | 0 |  | 345
WTRML | WTRML | 2429 | WATMLL E |  |  |  |  | NORTH2001 | DALLAS | -0.012632 | -0.14853 | 0 | 0 |  | 138
WTRML | WTRML | 2430 | WATMLL W |  |  |  |  | NORTH2001 | DALLAS | -0.012623 | -0.14878 | 0 | 0 |  | 138
TRCNR | TRCNR | 2432 | TRICORN |  |  |  |  | NORTH2001 | DALLAS | -0.012341 | -0.14779 | 0 | 0 |  | 345
SGVSW | SGVSW | 2433 | SGVL SS |  |  |  |  | NORTH2001 | DALLAS | -0.013362 | -0.1427 | 0 | 0 |  | 345
SGVSW | SGVSW | 2434 | SGVL SS |  |  |  |  | NORTH2001 | DALLAS | -0.013581 | -0.14042 | 0 | 0 |  | 138
|  | 2435 | WATMLLDB |  |  |  |  | NORTH2001 | DALLAS | -0.011548 | -0.16955 | 0 | 0 |  | 345
FORSW | FORSW | 2437 | FORNEY |  |  |  |  | NORTH2001 | DALLAS | -0.01419 | -0.13875 | 0 | 0 |  | 345
FORSW | FORSW | 2438 | FORNEY | 33.986 |  |  |  | NORTH2001 | KAUFMAN | -0.014395 | -0.13898 | -0.48922 | -4.7233 |  | 138
PDSES | PDSES | 2440 | PARKD T |  |  |  |  | NORTH2001 | DALLAS | -0.014331 | -0.14129 | 0 | 0 |  | 138
PRCSW | PRCSW | 2441 | PR CREEK |  |  |  |  | NORTH2001 | DALLAS | -0.014507 | -0.13975 | 0 | 0 |  | 138
PDSES | PDSES | 2442 | PARKD B1 |  |  |  |  | NORTH2001 | DALLAS | -0.014332 | -0.14128 | 0 | 0 |  | 138
PDSES | PDSES | 2443 | PARKD B3 |  |  |  |  | NORTH2001 | DALLAS | -0.014333 | -0.14128 | 0 | 0 |  | 138
PDSES | PDSES | 2444 | PARKDALE |  |  |  |  | NORTH2001 | DALLAS | -0.014331 | -0.14129 | 0 | 0 |  | 69
PDSES | PDSES | 2445 | PARKD B2 |  |  |  |  | NORTH2001 | DALLAS | -0.01433 | -0.14129 | 0 | 0 |  | 138
PDSES | PDSES | 2446 | PARK 1 G |  |  | 72 | 87 | NORTH2001 | DALLAS | -0.014331 | -0.14129 | -1.2468 | -12.2919 |  | 13.8
PDSES | PDSES | 2447 | PARK 2 G |  |  | 91 | 115 | NORTH2001 | DALLAS | -0.014331 | -0.14129 | -1.6481 | -16.2479 |  | 13.8
PDSES | PDSES | 2448 | PARK 3 G |  |  | 114 | 125 | NORTH2001 | DALLAS | -0.014331 | -0.14129 | -1.7914 | -17.6608 |  | 15
LHSES | LHSES | 2451 | LKHB 1 G |  |  | 344 | 397 | NORTH2001 | DALLAS | -0.014531 | -0.13962 | -5.7687 | -55.428 |  | 24
LHSES | LHSES | 2452 | LKHB 2 G |  |  | 488 | 528 | NORTH2001 | DALLAS | -0.014531 | -0.13962 | -7.6722 | -73.7178 |  | 22
CNRSW | CNRSW | 2453 | CNVIL |  |  |  |  | NORTH2001 | DALLAS | -0.014349 | -0.13884 | 0 | 0 |  | 345
CNRSW | CNRSW | 2454 | CNVIL |  |  |  |  | NORTH2001 | DALLAS | -0.014695 | -0.13904 | 0 | 0 |  | 138
KRGRV | KRGRV | 2456 | KRKLD E |  |  |  |  | NORTH2001 | DALLAS | -0.015052 | -0.13871 | 0 | 0 |  | 138
KRKPK | KRKPK | 2457 | KRKLD W |  |  |  |  | NORTH2001 | DALLAS | -0.015051 | -0.13871 | 0 | 0 |  | 138
KRKPK | KRKPK | 2458 | KIRKTIE1 |  |  |  |  | NORTH2001 | DALLAS | -0.015048 | -0.13872 | 0 | 0 |  | 138
KRKPK | KRKPK | 2459 | KIRKTIE2 |  |  |  |  | NORTH2001 | DALLAS | -0.015048 | -0.13872 | 0 | 0 |  | 138
RYSSW | RYSSW | 2460 | ROYSE T |  |  |  |  | NORTH2001 | ROCKWALL | -0.015449 | -0.13486 | 0 | 0 |  | 138
RYSSW | RYSSW | 2461 | ROYSE |  |  |  |  | NORTH2001 | ROCKWALL | -0.015702 | -0.13422 | 0 | 0 |  | 345
RYSSW | RYSSW | 2462 | ROYSE | 18.71 |  |  |  | NORTH2001 | ROCKWALL | -0.015443 | -0.13485 | -0.28894 | -2.5231 |  | 138
RYSSW | RYSSW | 2463 | ROYSE |  |  |  |  | NORTH2001 | ROCKWALL | -0.015447 | -0.13433 | 0 | 0 |  | 69
RYSSW | RYSSW | 2471 | ROYSE A |  |  |  |  | NORTH2001 | ROCKWALL | -0.015451 | -0.13488 | 0 | 0 |  | 138
RYSSW | RYSSW | 2472 | ROYSE B |  |  |  |  | NORTH2001 | ROCKWALL | -0.015443 | -0.13486 | 0 | 0 |  | 138
|  | 2474 | ROYSE T |  |  |  |  | NORTH2001 | ROCKWALL | -0.015684 | -0.13428 | 0 | 0 |  | 345
WLVEE | WLVEE | 2479 | WLEVEE T |  |  |  |  | NORTH2001 | DALLAS | -0.013603 | -0.14705 | 0 | 0 |  | 138
WLVEE | WLVEE | 2480 | WLEVEE2T |  |  |  |  | NORTH2001 | DALLAS | -0.013637 | -0.14673 | 0 | 0 |  | 138
ELVSW | ELVSW | 2481 | E LEVEEW |  |  |  |  | NORTH2001 | DALLAS | -0.013703 | -0.14565 | 0 | 0 |  | 138
ELVSW | ELVSW | 2482 | E LEVEEE |  |  |  |  | NORTH2001 | DALLAS | -0.013724 | -0.14568 | 0 | 0 |  | 138
CDCSW | CDCSW | 2484 | CREST B1 |  |  |  |  | NORTH2001 | DALLAS | -0.013638 | -0.14461 | 0 | 0 |  | 138
CDCSW | CDCSW | 2486 | C CREST | 29.985 |  |  |  | NORTH2001 | DALLAS | -0.013638 | -0.14356 | -0.40894 | -4.3046 |  | 69.6
DENDR | DENDR | 2487 | DEN DR E |  |  |  |  | NORTH2001 | DALLAS | -0.015058 | -0.13525 | 0 | 0 |  | 138
DENDR | DENDR | 2488 | DEN DR W |  |  |  |  | NORTH2001 | DALLAS | -0.015064 | -0.13527 | 0 | 0 |  | 138
DENDR | DENDR | 2489 | DEN DR 1 | 8.751 |  |  |  | NORTH2001 | DALLAS | -0.015058 | -0.13525 | -0.13177 | -1.1836 |  | 69.6
DENDR | DENDR | 2490 | DEN DR 2 | 18.015 |  |  |  | NORTH2001 | DALLAS | -0.015064 | -0.13527 | -0.27138 | -2.437 |  | 69
FCRSW | FCRSW | 2491 | FSHCRK |  |  |  |  | NORTH2001 | DALLAS | -0.013161 | -0.12938 | 0 | 0 |  | 138
FCRSW | FCRSW | 2492 | FSHCRK |  |  |  |  | NORTH2001 | DALLAS | -0.013307 | -0.13242 | 0 | 0 |  | 69.6
CDCSW | CDCSW | 2493 | C CRST W |  |  |  |  | NORTH2001 | DALLAS | -0.013638 | -0.14356 | 0 | 0 |  | 138
CDCSW | CDCSW | 2494 | C CRST E |  |  |  |  | NORTH2001 | DALLAS | -0.013639 | -0.14355 | 0 | 0 |  | 138
CDCSW | CDCSW | 2495 | C CRST T |  |  |  |  | NORTH2001 | DALLAS | -0.013638 | -0.14356 | 0 | 0 |  | 138
DLSES | DLSES | 2496 | DLS LL1 |  |  |  |  | NORTH2001 | DALLAS | -0.013752 | -0.14569 | 0 | 0 |  | 13.8
DLSES | DLSES | 2498 | DLS LL2 |  |  |  |  | NORTH2001 | DALLAS | -0.013751 | -0.14571 | 0 | 0 |  | 13.8
DLSES | DLSES | 2499 | DLS H3 |  |  |  |  | NORTH2001 | DALLAS | -0.013797 | -0.14563 | 0 | 0 |  | 138
DLSES | DLSES | 2500 | DLS LL3 | 40.782 |  |  |  | NORTH2001 | DALLAS | -0.013763 | -0.14568 | -0.56127 | -5.941 |  | 13.8
DLSES | DLSES | 2501 | DLS H4 |  |  |  |  | NORTH2001 | DALLAS | -0.013769 | -0.14582 | 0 | 0 |  | 138
DLSES | DLSES | 2502 | DLS LL4 | 56.92 |  |  |  | NORTH2001 | DALLAS | -0.013756 | -0.14574 | -0.78298 | -8.2953 |  | 13.8
DLSES | DLSES | 2503 | DLS RT1 |  |  |  |  | NORTH2001 | DALLAS | -0.013751 | -0.14571 | 0 | 0 |  | 13.8
DLSES | DLSES | 2504 | DLS RT2 |  |  |  |  | NORTH2001 | DALLAS | -0.013752 | -0.14569 | 0 | 0 |  | 13.8
DLSES | DLSES | 2505 | DLS RT3 |  |  |  |  | NORTH2001 | DALLAS | -0.013751 | -0.14571 | 0 | 0 |  | 13.8
DLSES | DLSES | 2506 | DLS RT4 |  |  |  |  | NORTH2001 | DALLAS | -0.013752 | -0.14569 | 0 | 0 |  | 13.8
DLSES | DLSES | 2507 | DLS H1 |  |  |  |  | NORTH2001 | DALLAS | -0.013704 | -0.14565 | 0 | 0 |  | 138
DLSES | DLSES | 2508 | DLS H2 |  |  |  |  | NORTH2001 | DALLAS | -0.013725 | -0.14568 | 0 | 0 |  | 138
ALNSW | ALNSW | 2509 | ALLENSSW | 29.288 |  |  |  | NORTH2001 | COLLIN | -0.017566 | -0.13229 | -0.51448 | -3.8745 |  | 138
ALNSW | ALNSW | 2510 | ALLENSSE | 33.331 |  |  |  | NORTH2001 | COLLIN | -0.017571 | -0.13229 | -0.58567 | -4.4093 |  | 138
ALNSW | ALNSW | 2511 | ALLEN1SS |  |  |  |  | NORTH2001 | COLLIN | -0.017568 | -0.13229 | 0 | 0 |  | 138
ALNSW | ALNSW | 2512 | ALLEN2SS |  |  |  |  | NORTH2001 | COLLIN | -0.017592 | -0.13227 | 0 | 0 |  | 138
ALNSW | ALNSW | 2513 | ALLEN1SS |  |  |  |  | NORTH2001 | COLLIN | -0.017528 | -0.13265 | 0 | 0 |  | 345
ALNSW | ALNSW | 2514 | ALLEN2SS |  |  |  |  | NORTH2001 | COLLIN | -0.019075 | -0.13097 | 0 | 0 |  | 345
LEBNONA | LEBNONA | 2515 | LEBANON |  |  |  |  | NORTH2001 | COLLIN | -0.017239 | -0.13161 | 0 | 0 |  | 138
MCDMT | MCDMT | 2516 | MCDERM | 52.309 |  |  |  | NORTH2001 | COLLIN | -0.017291 | -0.13172 | -0.90445 | -6.89 |  | 138
|  | 2517 | BRIDGESM |  |  |  |  | NORTH2001 | DENTON | -0.01691 | -0.13136 | 0 | 0 |  | 138
COLNY | COLNY | 2518 | COLONY | 75.283 |  |  |  | NORTH2001 | DENTON | -0.016908 | -0.13156 | -1.2729 | -9.9039 |  | 138
CRLFR | CRLFR | 2519 | CLT FK | 71.008 |  |  |  | NORTH2001 | DENTON | -0.016904 | -0.13198 | -1.2003 | -9.3718 |  | 138
PTENN | PTENN | 2522 | PL TEN | 64.149 |  |  |  | NORTH2001 | COLLIN | -0.019517 | -0.13058 | -1.252 | -8.3766 |  | 345
PTENN | PTENN | 2523 | PL TEN | 45.145 |  |  |  | NORTH2001 | COLLIN | -0.017398 | -0.13255 | -0.78543 | -5.9839 |  | 138
PCOIT | PCOIT | 2524 | PL COIT | 129.316 |  |  |  | NORTH2001 | COLLIN | -0.017317 | -0.13267 | -2.2393 | -17.1564 |  | 138
PCUST | PCUST | 2525 | PL CUST1 | 65.59 |  |  |  | NORTH2001 | COLLIN | -0.017497 | -0.13215 | -1.1476 | -8.6674 |  | 138
|  | 2526 | PL CUST2 | 64.844 |  |  |  | NORTH2001 | COLLIN | -0.017514 | -0.13237 | -1.1357 | -8.5837 |  | 138
ANATP | ANATP | 2528 | ANNASS1T |  |  |  |  | NORTH2001 | COLLIN | -0.016794 | -0.13167 | 0 | 0 |  | 138
MKNNY | MKNNY | 2529 | MCKIN 1 | 33.611 |  |  |  | NORTH2001 | COLLIN | -0.017378 | -0.13191 | -0.58408 | -4.4335 |  | 138
MKNSW | MKNSW | 2530 | MCKINSW1 | 58.917 |  |  |  | NORTH2001 | COLLIN | -0.017439 | -0.13203 | -1.0274 | -7.7789 |  | 138
ALLEN | ALLEN | 2531 | ALLEN 1 | 73.288 |  |  |  | NORTH2001 | COLLIN | -0.017527 | -0.13221 | -1.2845 | -9.6893 |  | 138
MKNTI | MKNTI | 2532 | MCKIN TI | 6.108 |  |  |  | NORTH2001 | COLLIN | -0.017408 | -0.13197 | -0.10633 | -0.80606 |  | 138
ALNTH | ALNTH | 2533 | ALLEN N1 | 24.202 |  |  |  | NORTH2001 | COLLIN | -0.017495 | -0.13214 | -0.42342 | -3.1982 |  | 138
CRLUD | CRLUD | 2535 | CLT UPF | 9.985 |  |  |  | NORTH2001 | DALLAS | -0.016514 | -0.13263 | -0.1649 | -1.3243 |  | 138
CRLUD | CRLUD | 2536 | CLT UPF2 | 33.511 |  |  |  | NORTH2001 | DALLAS | -0.016525 | -0.13256 | -0.55378 | -4.4424 |  | 138
CRLTN | CRLTN | 2537 | CLT | 128.293 |  |  |  | NORTH2001 | DALLAS | -0.016323 | -0.13284 | -2.0942 | -17.0425 |  | 138
MNTRY | MNTRY | 2538 | MONETY1 | 8.947 |  |  |  | NORTH2001 | DALLAS | -0.016465 | -0.1327 | -0.14732 | -1.1872 |  | 138
MNTRY | MNTRY | 2539 | MONETY2 | 8.947 |  |  |  | NORTH2001 | DALLAS | -0.016476 | -0.13263 | -0.14741 | -1.1867 |  | 138
CRNRD | CRNRD | 2540 | CROWN 1 | 29.15 |  |  |  | NORTH2001 | DALLAS | -0.015998 | -0.13332 | -0.46633 | -3.8863 |  | 138
CRNRD | CRNRD | 2541 | CROWN 2 | 15.949 |  |  |  | NORTH2001 | DALLAS | -0.016005 | -0.13327 | -0.25527 | -2.1256 |  | 138
HNSTP | HNSTP | 2542 | HENSTL T |  |  |  |  | NORTH2001 | DALLAS | -0.015932 | -0.13341 | 0 | 0 |  | 138
HNSLS | HNSLS | 2543 | HENSTL | 4.798 |  |  |  | NORTH2001 | DALLAS | -0.015932 | -0.13341 | -0.076444 | -0.64009 |  | 138
|  | 2546 | MCKIN 2 | 40.229 |  |  |  | NORTH2001 | COLLIN | -0.017386 | -0.13192 | -0.69941 | -5.307 |  | 138
|  | 2547 | MCKINSW2 | 24.027 |  |  |  | NORTH2001 | COLLIN | -0.017428 | -0.132 | -0.41875 | -3.1717 |  | 138
ALNTH | ALNTH | 2548 | ALLEN N2 | 32.566 |  |  |  | NORTH2001 | COLLIN | -0.01749 | -0.13213 | -0.5696 | -4.3029 |  | 138
ALLEN | ALLEN | 2549 | ALLEN 2 | 28.637 |  |  |  | NORTH2001 | COLLIN | -0.017527 | -0.1322 | -0.50191 | -3.7858 |  | 138
LSCOL | LSCOL | 2550 | LASCOL 1 | 41.372 |  |  |  | NORTH2001 | DALLAS | -0.015427 | -0.13408 | -0.63823 | -5.5472 |  | 138
LSCOL | LSCOL | 2551 | LASCOL 2 | 20.382 |  |  |  | NORTH2001 | DALLAS | -0.015431 | -0.13406 | -0.31451 | -2.7324 |  | 138
IRVNE | IRVNE | 2552 | IV NE | 49.139 |  |  |  | NORTH2001 | DALLAS | -0.015278 | -0.13428 | -0.75076 | -6.5984 |  | 138
CRLJL | CRLJL | 2555 | CLT JOSY | 62.072 |  |  |  | NORTH2001 | DALLAS | -0.016685 | -0.13296 | -1.0357 | -8.2528 |  | 138
CRLTR | CRLTR | 2558 | CLT TAR1 | 61.925 |  |  |  | NORTH2001 | DALLAS | -0.016609 | -0.13343 | -1.0285 | -8.2624 |  | 138
CRLTR | CRLTR | 2559 | CLT TAR2 | 34.189 |  |  |  | NORTH2001 | DALLAS | -0.016586 | -0.13345 | -0.56706 | -4.5625 |  | 138
HRSMD | HRSMD | 2562 | CLT RM 1 | 82.955 |  |  |  | NORTH2001 | DENTON | -0.016826 | -0.1332 | -1.3958 | -11.05 |  | 138
NPKWY | NPKWY | 2564 | N PRK 1 | 66.332 |  |  |  | NORTH2001 | COLLIN | -0.016879 | -0.13315 | -1.1196 | -8.8321 |  | 138
NPKWY | NPKWY | 2565 | N PRK 2 | 69.97 |  |  |  | NORTH2001 | COLLIN | -0.016957 | -0.13307 | -1.1865 | -9.311 |  | 138
ADISN | ADISN | 2569 | ADD | 64.791 |  |  |  | NORTH2001 | DALLAS | -0.016563 | -0.13345 | -1.0731 | -8.6464 |  | 138
|  | 2576 | ADD TAP1 |  |  |  |  | NORTH2001 | DALLAS | -0.016563 | -0.13345 | 0 | 0 |  | 138
|  | 2577 | ADD TAP2 |  |  |  |  | NORTH2001 | DALLAS | -0.016569 | -0.13347 | 0 | 0 |  | 138
|  | 2578 | CLT E E |  |  |  |  | NORTH2001 | DALLAS | -0.016556 | -0.13348 | 0 | 0 |  | 138
EFPNR | EFPNR | 2580 | ELMFK N1 | 4.518 |  |  |  | NORTH2001 | DALLAS | -0.016473 | -0.13316 | -0.074426 | -0.6016 |  | 138
EFPNR | EFPNR | 2581 | ELMFK N2 | 4.518 |  |  |  | NORTH2001 | DALLAS | -0.016483 | -0.13322 | -0.074469 | -0.60189 |  | 138
FRMBG | FRMBG | 2582 | FB GILLS | 129.731 |  |  |  | NORTH2001 | DALLAS | -0.016476 | -0.13402 | -2.1374 | -17.3861 |  | 138
FRMBR | FRMBR | 2583 | FB | 84.799 |  |  |  | NORTH2001 | DALLAS | -0.016115 | -0.13487 | -1.3665 | -11.4367 |  | 138
EFTP1 | EFTP1 | 2586 | ELMFK 1T |  |  |  |  | NORTH2001 | DALLAS | -0.016473 | -0.13316 | 0 | 0 |  | 138
EFTP1 | EFTP1 | 2587 | ELMFK 2T |  |  |  |  | NORTH2001 | DALLAS | -0.016483 | -0.13322 | 0 | 0 |  | 138
EFPMP | EFPMP | 2588 | ELMFK 1 | 4.693 |  |  |  | NORTH2001 | DALLAS | -0.016473 | -0.13316 | -0.077309 | -0.6249 |  | 138
EFPMP | EFPMP | 2589 | ELMFK 2 | 4.686 |  |  |  | NORTH2001 | DALLAS | -0.016483 | -0.13322 | -0.077238 | -0.62427 |  | 138
NLPTP | NLPTP | 2590 | NL PMP T |  |  |  |  | NORTH2001 | DALLAS | -0.016424 | -0.13296 | 0 | 0 |  | 138
NLRVP | NLRVP | 2591 | NL PMP |  |  |  |  | NORTH2001 | DALLAS | -0.016424 | -0.13296 | 0 | 0 |  | 138
|  | 2595 | AIR LQ T |  |  |  |  | NORTH2001 | DALLAS | -0.015356 | -0.13795 | 0 | 0 |  | 138
ALPHA | ALPHA | 2596 | ALPHA 1 | 66.268 |  |  |  | NORTH2001 | DALLAS | -0.015659 | -0.1363 | -1.0377 | -9.0324 |  | 138
ALPHA | ALPHA | 2597 | ALPHA 2 | 47.84 |  |  |  | NORTH2001 | DALLAS | -0.015539 | -0.13697 | -0.7434 | -6.5525 |  | 138
ARLQE | ARLQE | 2606 | AIR LIQD | 10.174 |  |  |  | NORTH2001 | DALLAS | -0.015356 | -0.13795 | -0.15623 | -1.4035 |  | 138
WLNTP | WLNTP | 2607 | WALNT 1T |  |  |  |  | NORTH2001 | DALLAS | -0.015356 | -0.13795 | 0 | 0 |  | 138
WALNT | WALNT | 2608 | WALNT 1 | 13.774 |  |  |  | NORTH2001 | DALLAS | -0.015356 | -0.13795 | -0.21151 | -1.9001 |  | 138
RWDHV | RWDHV | 2609 | WALNT 2T |  |  |  |  | NORTH2001 | DALLAS | -0.016866 | -0.13316 | 0 | 0 |  | 138
WALNT | WALNT | 2610 | WALNT 2 | 16.161 |  |  |  | NORTH2001 | DALLAS | -0.016866 | -0.13316 | -0.27258 | -2.1519 |  | 138
PRSTN | PRSTN | 2611 | KNL TR2T |  |  |  |  | NORTH2001 | DALLAS | -0.016328 | -0.13501 | 0 | 0 |  | 138
PRSTN | PRSTN | 2612 | KNL TR1T |  |  |  |  | NORTH2001 | DALLAS | -0.015867 | -0.13641 | 0 | 0 |  | 138
KNLTR | KNLTR | 2613 | KNL TR2 | 22.41 |  |  |  | NORTH2001 | DALLAS | -0.016375 | -0.13469 | -0.36697 | -3.0185 |  | 138
KNLTR | KNLTR | 2614 | KNL TR1 | 26.71 |  |  |  | NORTH2001 | DALLAS | -0.015729 | -0.13664 | -0.42013 | -3.6497 |  | 138
PRSTN | PRSTN | 2615 | PRSTN N1 | 28.127 |  |  |  | NORTH2001 | DALLAS | -0.016328 | -0.13501 | -0.45925 | -3.7975 |  | 138
PRSTN | PRSTN | 2616 | PRSTN N2 | 33.773 |  |  |  | NORTH2001 | DALLAS | -0.015867 | -0.13641 | -0.53589 | -4.6068 |  | 138
MDWCK | MDWCK | 2617 | MEDWCK 1 | 32.762 |  |  |  | NORTH2001 | DALLAS | -0.016328 | -0.13501 | -0.53493 | -4.4233 |  | 138
MDWCK | MDWCK | 2618 | MEDWCK 2 | 19.669 |  |  |  | NORTH2001 | DALLAS | -0.015867 | -0.13641 | -0.3121 | -2.683 |  | 138
FRNKF | FRNKF | 2623 | FRNKFD 1 | 27.011 |  |  |  | NORTH2001 | COLLIN | -0.016084 | -0.13614 | -0.43445 | -3.6772 |  | 138
FRNKF | FRNKF | 2624 | FRNKFD 2 | 25.313 |  |  |  | NORTH2001 | COLLIN | -0.016079 | -0.13614 | -0.407 | -3.446 |  | 138
BLTLN | BLTLN | 2627 | BLTLIN 1 | 31.165 |  |  |  | NORTH2001 | DALLAS | -0.015638 | -0.13725 | -0.48736 | -4.2773 |  | 138
BLTLN | BLTLN | 2628 | BLTLIN 2 | 18.496 |  |  |  | NORTH2001 | DALLAS | -0.015635 | -0.13725 | -0.28919 | -2.5386 |  | 138
DALTI | DALTI | 2633 | TI DPL 1 | 56.437 |  |  |  | NORTH2001 | DALLAS | -0.015379 | -0.13789 | -0.86797 | -7.7822 |  | 138
DALTI | DALTI | 2634 | TI DPL 2 | 54.05 |  |  |  | NORTH2001 | DALLAS | -0.015378 | -0.1379 | -0.83118 | -7.4533 |  | 138
SCHRD | SCHRD | 2636 | SCHDR 1 | 20.13 |  |  |  | NORTH2001 | DALLAS | -0.015323 | -0.13803 | -0.30844 | -2.7786 |  | 138
SCHRD | SCHRD | 2637 | SCHDR 2 | 16.271 |  |  |  | NORTH2001 | DALLAS | -0.015311 | -0.13806 | -0.24912 | -2.2464 |  | 138
COTRD | COTRD | 2638 | COIT 2 | 17.984 |  |  |  | NORTH2001 | DALLAS | -0.015255 | -0.1382 | -0.27435 | -2.4854 |  | 138
COTRD | COTRD | 2639 | COIT 1 | 17.724 |  |  |  | NORTH2001 | DALLAS | -0.015241 | -0.13824 | -0.27014 | -2.4501 |  | 138
JCTTP | JCTTP | 2640 | JUDD T |  |  |  |  | NORTH2001 | DALLAS | -0.015202 | -0.13834 | 0 | 0 |  | 138
JUDCT | JUDCT | 2642 | JUDD 1 | 17.056 |  |  |  | NORTH2001 | DALLAS | -0.015202 | -0.13834 | -0.25929 | -2.3594 |  | 138
CNEXP | CNEXP | 2647 | CENEXP 1 | 26.965 |  |  |  | NORTH2001 | DALLAS | -0.015105 | -0.13845 | -0.40731 | -3.7333 |  | 138
CNEXP | CNEXP | 2648 | CENEXP 2 | 27.196 |  |  |  | NORTH2001 | DALLAS | -0.015105 | -0.13845 | -0.4108 | -3.7653 |  | 138
EDGTM | EDGTM | 2651 | BANDRA1T |  |  |  |  | NORTH2001 | DALLAS | -0.015238 | -0.1378 | 0 | 0 |  | 138
EDGTM | EDGTM | 2652 | BANDRA2T |  |  |  |  | NORTH2001 | DALLAS | -0.01524 | -0.13779 | 0 | 0 |  | 138
BNDRA | BNDRA | 2653 | BANDRA1 | 20.212 |  |  |  | NORTH2001 | DALLAS | -0.015238 | -0.1378 | -0.30798 | -2.7852 |  | 138
BNDRA | BNDRA | 2654 | BANDRA2 | 32.197 |  |  |  | NORTH2001 | DALLAS | -0.01524 | -0.13779 | -0.49067 | -4.4365 |  | 138
NHNSW | NHNSW | 2657 | NOHAVN W |  |  |  |  | NORTH2001 | DALLAS | -0.015338 | -0.13731 | 0 | 0 |  | 138
NHNSW | NHNSW | 2658 | NOHAVN E | 63.335 |  |  |  | NORTH2001 | DALLAS | -0.015334 | -0.13732 | -0.97121 | -8.6973 |  | 138
NHNSW | NHNSW | 2659 | NOHAVN T |  |  |  |  | NORTH2001 | DALLAS | -0.015337 | -0.13731 | 0 | 0 |  | 138
WELRD | WELRD | 2660 | WELCH 1 | 25.128 |  |  |  | NORTH2001 | DALLAS | -0.015359 | -0.13683 | -0.38594 | -3.4383 |  | 138
WELRD | WELRD | 2661 | WELCH 2 | 27.713 |  |  |  | NORTH2001 | DALLAS | -0.015351 | -0.13687 | -0.42543 | -3.7932 |  | 138
MSHLN | MSHLN | 2662 | MARSH 1 | 19.781 |  |  |  | NORTH2001 | DALLAS | -0.015371 | -0.13636 | -0.30404 | -2.6973 |  | 138
MSHLN | MSHLN | 2663 | MARSH 2 | 23.479 |  |  |  | NORTH2001 | DALLAS | -0.015381 | -0.13632 | -0.36113 | -3.2007 |  | 138
PARCO | PARCO | 2671 | PL ARCO | 3.508 |  |  |  | NORTH2001 | COLLIN | -0.017274 | -0.13271 | -0.060598 | -0.46555 |  | 138
|  | 2672 | TWN STAR | 1.832 |  |  |  | NORTH2001 | COLLIN | -0.017292 | -0.13267 | -0.031679 | -0.24305 |  | 138
PWEST | PWEST | 2673 | PL W | 95.804 |  |  |  | NORTH2001 | COLLIN | -0.017292 | -0.13267 | -1.6566 | -12.7103 |  | 138
PLANO | PLANO | 2674 | PL | 34.562 |  |  |  | NORTH2001 | COLLIN | -0.017384 | -0.13254 | -0.60083 | -4.5809 |  | 138
PALRD | PALRD | 2677 | PL ALMA | 69.219 |  |  |  | NORTH2001 | COLLIN | -0.017394 | -0.13253 | -1.204 | -9.1736 |  | 138
PPARK | PPARK | 2678 | PL PARK | 57.833 |  |  |  | NORTH2001 | COLLIN | -0.017485 | -0.1324 | -1.0112 | -7.6571 |  | 138
RCHRD | RCHRD | 2683 | RICH | 62.278 |  |  |  | NORTH2001 | DALLAS | -0.017229 | -0.13274 | -1.073 | -8.2666 |  | 138
RSPVY | RSPVY | 2684 | RICH SV | 30.899 |  |  |  | NORTH2001 | DALLAS | -0.017229 | -0.13274 | -0.53236 | -4.1014 |  | 138
RCHAT | RCHAT | 2685 | RICHCL T |  |  |  |  | NORTH2001 | DALLAS | -0.017229 | -0.13274 | 0 | 0 |  | 138
|  | 2686 | RICHCOL | 67.671 |  |  |  | NORTH2001 | DALLAS | -0.017136 | -0.13284 | -1.1596 | -8.9892 |  | 138
RSPCK | RSPCK | 2689 | RICH SC | 67.143 |  |  |  | NORTH2001 | DALLAS | -0.017158 | -0.13281 | -1.1521 | -8.9174 |  | 138
REAST | REAST | 2690 | RICH E | 62.202 |  |  |  | NORTH2001 | DALLAS | -0.017075 | -0.1329 | -1.0621 | -8.2668 |  | 138
PSHIL | PSHIL | 2691 | PL SHIL | 68.072 |  |  |  | NORTH2001 | COLLIN | -0.017335 | -0.13258 | -1.18 | -9.0251 |  | 138
LAVON | LAVON | 2693 | WYLIE M |  |  |  |  | NORTH2001 | COLLIN | -0.015657 | -0.13466 | 0 | 0 |  | 138
LAVON | LAVON | 2694 | LAVON | 71.081 |  |  |  | NORTH2001 | COLLIN | -0.015688 | -0.13463 | -1.1151 | -9.5694 |  | 138
WYLPM | WYLPM | 2695 | LV NTMWD | 14.089 |  |  |  | NORTH2001 | COLLIN | -0.015692 | -0.13462 | -0.22109 | -1.8967 |  | 138
MURPH | MURPH | 2696 | MURPHY | 43.963 |  |  |  | NORTH2001 | DALLAS | -0.015816 | -0.13451 | -0.69532 | -5.9134 |  | 138
|  | 2697 | NW WYL M |  |  |  |  | NORTH2001 | COLLIN | -0.015781 | -0.13454 | 0 | 0 |  | 138
RWDHV | RWDHV | 2698 | RICH WD | 53.538 |  |  |  | NORTH2001 | DALLAS | -0.016949 | -0.13306 | -0.90741 | -7.1236 |  | 138
FSTVW | FSTVW | 2699 | FORSTV 1 | 27.088 |  |  |  | NORTH2001 | DALLAS | -0.016823 | -0.13321 | -0.4557 | -3.6084 |  | 138
GRLWS | GRLWS | 2700 | GARL W | 7.109 |  |  |  | NORTH2001 | DALLAS | -0.016639 | -0.13343 | -0.11828 | -0.94858 |  | 138
GRLND | GRLND | 2701 | GARL | 27.748 |  |  |  | NORTH2001 | DALLAS | -0.016531 | -0.13357 | -0.45869 | -3.7062 |  | 138
RWALL | RWALL | 2702 | RKWL | 61.747 |  |  |  | NORTH2001 | ROCKWALL | -0.015885 | -0.13435 | -0.98086 | -8.2959 |  | 138
PRCTN | PRCTN | 2707 | PRINCPOD |  |  |  |  | NORTH2001 | COLLIN | -0.015443 | -0.13486 | 0 | 0 |  | 138
|  | 2708 | CLIMAX M |  |  |  |  | NORTH2001 | COLLIN | -0.016794 | -0.13167 | 0 | 0 |  | 138
RWALS | RWALS | 2711 | RKWL S | 35.289 |  |  |  | NORTH2001 | ROCKWALL | -0.014867 | -0.13715 | -0.52464 | -4.8398 |  | 138
BLKLD | BLKLD | 2713 | BLACKLND |  |  |  |  | NORTH2001 | ROCKWALL | -0.015204 | -0.13451 | 0 | 0 |  | 138
TRNTP | TRNTP | 2715 | TERRL NT |  |  |  |  | NORTH2001 | KAUFMAN | -0.01465 | -0.13371 | 0 | 0 |  | 138
|  | 2716 | TER ARCO |  |  |  |  | NORTH2001 | KAUFMAN | -0.01465 | -0.13371 | 0 | 0 |  | 138
|  | 2717 | TERARC T |  |  |  |  | NORTH2001 | KAUFMAN | -0.01465 | -0.13371 | 0 | 0 |  | 138
TRNTH | TRNTH | 2718 | TERRL N | 16.929 |  |  |  | NORTH2001 | KAUFMAN | -0.014354 | -0.13329 | -0.243 | -2.2564 |  | 138
ARCTP | ARCTP | 2719 | TERAIR T |  |  |  |  | NORTH2001 | KAUFMAN | -0.013842 | -0.13255 | 0 | 0 |  | 138
AIRCO | AIRCO | 2720 | TERAIRCO | 6.281 |  |  |  | NORTH2001 | KAUFMAN | -0.013842 | -0.13255 | -0.08694 | -0.83254 |  | 138
TRLSW | TRLSW | 2721 | TERRL SS | 19.22 |  |  |  | NORTH2001 | KAUFMAN | -0.014104 | -0.13293 | -0.27107 | -2.5548 |  | 138
TRLSW | TRLSW | 2722 | TERRL SS |  |  |  |  | NORTH2001 | KAUFMAN | -0.014104 | -0.13293 | 0 | 0 |  | 69.6
RHILL | RHILL | 2723 | ROSEHILL |  |  |  |  | NORTH2001 | KAUFMAN | -0.013842 | -0.13255 | 0 | 0 |  | 138
KFMNW | KFMNW | 2724 | KAUFMAN | 11.117 |  |  |  | NORTH2001 | KAUFMAN | -0.013527 | -0.1321 | -0.15038 | -1.4685 |  | 138
OKGTP | OKGTP | 2725 | OAKGROVE |  |  |  |  | NORTH2001 | KAUFMAN | -0.013227 | -0.1291 | 0 | 0 |  | 138
KMPSO | KMPSO | 2726 | KEMP S | 4.614 |  |  |  | NORTH2001 | KAUFMAN | -0.012527 | -0.12212 | -0.057802 | -0.56344 |  | 138
CRNDL | CRNDL | 2727 | CRANDL | 7.689 |  |  |  | NORTH2001 | KAUFMAN | -0.013557 | -0.13676 | -0.10424 | -1.0515 |  | 138
KFMSO | KFMSO | 2728 | KAUF S | 6.981 |  |  |  | NORTH2001 | KAUFMAN | -0.013296 | -0.12979 | -0.092818 | -0.90604 |  | 138
QNLTP | QNLTP | 2729 | MUNSON |  |  |  |  | NORTH2001 | ROCKWALL | -0.014104 | -0.13293 | 0 | 0 |  | 69.6
QNLAN | QNLAN | 2730 | QUINLAN | 7.831 |  |  |  | NORTH2001 | HUNT | -0.014104 | -0.13293 | -0.11044 | -1.0409 |  | 69.6
TERSO | TERSO | 2731 | TERRL S | 8.768 |  |  |  | NORTH2001 | KAUFMAN | -0.014008 | -0.13279 | -0.12282 | -1.1643 |  | 138
RWATP | RWATP | 2733 | RKWLAL T |  |  |  |  | NORTH2001 | ROCKWALL | -0.015425 | -0.13525 | 0 | 0 |  | 138
RWATP | RWATP | 2734 | RKWLAL | 0.664 |  |  |  | NORTH2001 | ROCKWALL | -0.015425 | -0.13525 | -0.010242 | -0.089807 |  | 138
DALRK | DALRK | 2735 | GRL DAL | 67.161 |  |  |  | NORTH2001 | DALLAS | -0.015415 | -0.13547 | -1.0353 | -9.0986 |  | 138
ROWLT | ROWLT | 2736 | ROWLETT | 55.547 |  |  |  | NORTH2001 | DALLAS | -0.015408 | -0.13563 | -0.85586 | -7.5339 |  | 138
|  | 2738 | OATES M |  |  |  |  | NORTH2001 | DALLAS | -0.015393 | -0.13596 | 0 | 0 |  | 138
BOBTP | BOBTP | 2739 | GRL BT T |  |  |  |  | NORTH2001 | DALLAS | -0.015397 | -0.13587 | 0 | 0 |  | 138
BBTWN | BBTWN | 2740 | GRL BT | 25.704 |  |  |  | NORTH2001 | DALLAS | -0.015397 | -0.13587 | -0.39576 | -3.4924 |  | 138
MESNT | MESNT | 2742 | MSQT N T |  |  |  |  | NORTH2001 | DALLAS | -0.015164 | -0.13694 | 0 | 0 |  | 138
SCYEN | SCYEN | 2743 | SCYENE1T |  |  |  |  | NORTH2001 | DALLAS | -0.014425 | -0.14046 | 0 | 0 |  | 138
SCYTP | SCYTP | 2744 | SCYENE2T |  |  |  |  | NORTH2001 | DALLAS | -0.014333 | -0.14128 | 0 | 0 |  | 138
SCYEN | SCYEN | 2745 | SCYENE1 | 10.081 |  |  |  | NORTH2001 | DALLAS | -0.014425 | -0.14046 | -0.14542 | -1.416 |  | 138
SCYEN | SCYEN | 2746 | SCYENE2 | 12.364 |  |  |  | NORTH2001 | DALLAS | -0.014333 | -0.14128 | -0.17722 | -1.7468 |  | 138
THRET | THRET | 2747 | THRN E1T |  |  |  |  | NORTH2001 | DALLAS | -0.014821 | -0.1384 | 0 | 0 |  | 138
JMPMP | JMPMP | 2748 | J MILLER | 6.065 |  |  |  | NORTH2001 | DALLAS | -0.014333 | -0.14128 | -0.086931 | -0.85687 |  | 138
THRNE | THRNE | 2750 | THRN E1 | 18.211 |  |  |  | NORTH2001 | DALLAS | -0.014821 | -0.1384 | -0.26991 | -2.5205 |  | 138
THRNE | THRNE | 2751 | THRN E2 | 20.901 |  |  |  | NORTH2001 | DALLAS | -0.014333 | -0.14128 | -0.29958 | -2.9529 |  | 138
MESFR | MESFR | 2752 | MSQT FR | 38.125 |  |  |  | NORTH2001 | DALLAS | -0.014599 | -0.13935 | -0.5566 | -5.3128 |  | 138
MESQW | MESQW | 2754 | MSQT W | 64.704 |  |  |  | NORTH2001 | DALLAS | -0.014382 | -0.13961 | -0.93058 | -9.0336 |  | 138
MESQE | MESQE | 2756 | MSQT E |  |  |  |  | NORTH2001 | DALLAS | -0.01426 | -0.13948 | 0 | 0 |  | 138
MESWE | MESWE | 2759 | MSQT WE | 6.572 |  |  |  | NORTH2001 | DALLAS | -0.014449 | -0.13969 | -0.094959 | -0.91802 |  | 138
PRCRK | PRCRK | 2762 | PR CRK 2 | 18.089 |  |  |  | NORTH2001 | DALLAS | -0.014503 | -0.13978 | -0.26234 | -2.5285 |  | 138
PRCRK | PRCRK | 2763 | PR CRK 1 | 14.278 |  |  |  | NORTH2001 | DALLAS | -0.014503 | -0.13978 | -0.20707 | -1.9958 |  | 138
MESTE | MESTE | 2765 | MSQT TE | 95.806 |  |  |  | NORTH2001 | DALLAS | -0.01426 | -0.13948 | -1.3662 | -13.3631 |  | 138
MESQN | MESQN | 2766 | MSQT N | 61.7 |  |  |  | NORTH2001 | DALLAS | -0.01426 | -0.13948 | -0.87987 | -8.6059 |  | 138
EFTPS | EFTPE | 2769 | E SIDE1T |  |  |  |  | NORTH2001 | DALLAS | -0.014288 | -0.13938 | 0 | 0 |  | 138
EFTPN | ESFLT | 2770 | E SIDE1 | 5.72 |  |  |  | NORTH2001 | DALLAS | -0.014288 | -0.13938 | -0.081728 | -0.79723 |  | 138
EFTPW | EFTPW | 2771 | E SIDE2T |  |  |  |  | NORTH2001 | DALLAS | -0.014209 | -0.13955 | 0 | 0 |  | 138
ESFLT | ESFLT | 2772 | E SIDE2 | 2.86 |  |  |  | NORTH2001 | DALLAS | -0.014209 | -0.13955 | -0.040638 | -0.39912 |  | 138
MESQT | MESQT | 2775 | MSQT | 61.131 |  |  |  | NORTH2001 | DALLAS | -0.014184 | -0.13959 | -0.86706 | -8.5331 |  | 138
BSPTP | BSPTP | 2776 | BCHSPG T |  |  |  |  | NORTH2001 | DALLAS | -0.014102 | -0.1397 | 0 | 0 |  | 138
BSPRG | BSPRG | 2777 | BCHSPG | 37.289 |  |  |  | NORTH2001 | DALLAS | -0.014102 | -0.1397 | -0.52586 | -5.2093 |  | 138
LWSNR | LWSNR | 2779 | LAWSON | 32.889 |  |  |  | NORTH2001 | DALLAS | -0.013915 | -0.13996 | -0.45765 | -4.6031 |  | 138
MSLSW | MSLSW | 2782 | MORSON E | 22.512 |  |  |  | NORTH2001 | DALLAS | -0.015408 | -0.13535 | -0.34688 | -3.0469 |  | 138
MSLSW | MSLSW | 2783 | MORSON W | 21.689 |  |  |  | NORTH2001 | DALLAS | -0.015425 | -0.13532 | -0.33455 | -2.9349 |  | 138
LMBLN | LMBLN | 2784 | LOMBRY 1 | 27.06 |  |  |  | NORTH2001 | DALLAS | -0.015277 | -0.13531 | -0.41338 | -3.6615 |  | 138
LMBLN | LMBLN | 2785 | LOMBRY 2 | 15.873 |  |  |  | NORTH2001 | DALLAS | -0.015291 | -0.1353 | -0.24272 | -2.1476 |  | 138
LMTP1 | LMTP1 | 2786 | L MNT 1T |  |  |  |  | NORTH2001 | DALLAS | -0.01515 | -0.13528 | 0 | 0 |  | 138
LMTP2 | LMTP2 | 2787 | L MNT 2T |  |  |  |  | NORTH2001 | DALLAS | -0.015163 | -0.13529 | 0 | 0 |  | 138
LKMNT | LKMNT | 2788 | L MNT 1 | 27.332 |  |  |  | NORTH2001 | DALLAS | -0.01515 | -0.13528 | -0.41407 | -3.6974 |  | 138
LKMNT | LKMNT | 2789 | L MNT 2 | 25.4 |  |  |  | NORTH2001 | DALLAS | -0.015163 | -0.13529 | -0.38514 | -3.4363 |  | 138
MAPLE | MAPLE | 2792 | MAPLE 2 | 25.742 |  |  |  | NORTH2001 | DALLAS | -0.015058 | -0.13525 | -0.38761 | -3.4816 |  | 69.6
CLLVL | CLLVL | 2793 | COLVLE 2 | 9.301 |  |  |  | NORTH2001 | DALLAS | -0.015058 | -0.13525 | -0.14005 | -1.258 |  | 69.6
ECTP1 | ECTP1 | 2796 | EP CNT1T |  |  |  |  | NORTH2001 | DALLAS | -0.015021 | -0.13524 | 0 | 0 |  | 138
ECTP2 | ECTP2 | 2797 | EP CNT2T |  |  |  |  | NORTH2001 | DALLAS | -0.014939 | -0.13526 | 0 | 0 |  | 138
EMPCT | EMPCT | 2798 | EP CNT1 | 17.453 |  |  |  | NORTH2001 | DALLAS | -0.015021 | -0.13524 | -0.26215 | -2.3604 |  | 138
EMPCT | EMPCT | 2799 | EP CNT2 | 18.406 |  |  |  | NORTH2001 | DALLAS | -0.014939 | -0.13526 | -0.27496 | -2.4896 |  | 138
RGLRW | RGLRW | 2800 | REG RW 1 | 12.997 |  |  |  | NORTH2001 | DALLAS | -0.014947 | -0.13522 | -0.19426 | -1.7575 |  | 138
RGLRW | RGLRW | 2801 | REG RW 2 | 29.835 |  |  |  | NORTH2001 | DALLAS | -0.014952 | -0.13526 | -0.4461 | -4.0355 |  | 138
TRIRA | TRIRA | 2804 | TRA 1 | 17.91 |  |  |  | NORTH2001 | DALLAS | -0.014092 | -0.13631 | -0.2524 | -2.4413 |  | 138
IHFT2 | IHFT2 | 2805 | IVHNT 2T |  |  |  |  | NORTH2001 | DALLAS | -0.014459 | -0.1357 | 0 | 0 |  | 138
CHROW | CHROW | 2811 | CHNLR 1 | 21.585 |  |  |  | NORTH2001 | DALLAS | -0.014526 | -0.13771 | -0.31354 | -2.9725 |  | 138
CHROW | CHROW | 2812 | CHNLR 2 | 24.323 |  |  |  | NORTH2001 | DALLAS | -0.014777 | -0.13518 | -0.35943 | -3.2879 |  | 138
RECCR | RECCR | 2813 | REC CR 1 | 23.783 |  |  |  | NORTH2001 | DALLAS | -0.014291 | -0.14004 | -0.33989 | -3.3307 |  | 138
RECCR | RECCR | 2814 | REC CR 2 | 24.57 |  |  |  | NORTH2001 | DALLAS | -0.014307 | -0.13989 | -0.35152 | -3.437 |  | 138
AMLIA | AMLIA | 2815 | AMELIA 1 | 21.498 |  |  |  | NORTH2001 | DALLAS | -0.014087 | -0.14208 | -0.30283 | -3.0544 |  | 138
AMLIA | AMLIA | 2816 | AMELIA 2 | 14.525 |  |  |  | NORTH2001 | DALLAS | -0.014777 | -0.13518 | -0.21464 | -1.9634 |  | 138
MAPLE | MAPLE | 2817 | MAPLE 1 | 22.606 |  |  |  | NORTH2001 | DALLAS | -0.014777 | -0.13518 | -0.33405 | -3.0558 |  | 138
CLLVL | CLLVL | 2818 | COLVLE 1 | 8.981 |  |  |  | NORTH2001 | DALLAS | -0.014777 | -0.13518 | -0.13271 | -1.214 |  | 138
REGST | REGST | 2819 | REAGAN 1 | 18.593 |  |  |  | NORTH2001 | DALLAS | -0.013925 | -0.14369 | -0.2589 | -2.6717 |  | 138
REGST | REGST | 2820 | REAGAN 2 | 14.482 |  |  |  | NORTH2001 | DALLAS | -0.013724 | -0.14568 | -0.19876 | -2.1098 |  | 138
LOMAL | LOMAL | 2828 | LOMO A 2 | 55.787 |  |  |  | NORTH2001 | DALLAS | -0.013724 | -0.14568 | -0.76564 | -8.1273 |  | 138
LOMAL | LOMAL | 2829 | LOMO A 1 | 52.041 |  |  |  | NORTH2001 | DALLAS | -0.014479 | -0.14145 | -0.75352 | -7.3612 |  | 138
DLSWT | DLSWT | 2832 | W DAL 2T |  |  |  |  | NORTH2001 | DALLAS | -0.013613 | -0.1411 | 0 | 0 |  | 138
DALLW | DALLW | 2833 | W DAL 2 | 14.332 |  |  |  | NORTH2001 | DALLAS | -0.013613 | -0.1411 | -0.1951 | -2.0222 |  | 138
TRIRA | TRIRA | 2836 | TRA 2 | 7.391 |  |  |  | NORTH2001 | DALLAS | -0.013584 | -0.13965 | -0.1004 | -1.0321 |  | 138
CALTP | CALTP | 2837 | CALUMT2T |  |  |  |  | NORTH2001 | DALLAS | -0.013553 | -0.1381 | 0 | 0 |  | 138
CLMET | CLMET | 2838 | CALUMT2 | 11.355 |  |  |  | NORTH2001 | DALLAS | -0.013553 | -0.1381 | -0.1539 | -1.5681 |  | 138
DEALY | DEALY | 2842 | DEALEY1 | 28.655 |  |  |  | NORTH2001 | DALLAS | -0.013639 | -0.14567 | -0.39082 | -4.1741 |  | 138
DALLW | DALLW | 2845 | W DAL 1 | 13.425 |  |  |  | NORTH2001 | DALLAS | -0.013538 | -0.13723 | -0.18175 | -1.8423 |  | 138
DVSTP | DVSTP | 2849 | DAV ST1T |  |  |  |  | NORTH2001 | DALLAS | -0.013538 | -0.13723 | 0 | 0 |  | 138
DAVST | DAVST | 2850 | DAV ST 1 | 32.659 |  |  |  | NORTH2001 | DALLAS | -0.013538 | -0.13723 | -0.44215 | -4.4817 |  | 138
LFARG | LFARG | 2851 | T P C |  |  |  |  | NORTH2001 | DALLAS | -0.013538 | -0.13723 | 0 | 0 |  | 138
CLMET | CLMET | 2852 | CALUMT1 | 13.588 |  |  |  | NORTH2001 | DALLAS | -0.013538 | -0.13723 | -0.18396 | -1.8646 |  | 138
DGNST | DGNST | 2857 | DRAGON 2 | 19.038 |  |  |  | NORTH2001 | DALLAS | -0.013766 | -0.14581 | -0.26208 | -2.776 |  | 138
DGNST | DGNST | 2858 | DRAGON 1 | 19.866 |  |  |  | NORTH2001 | DALLAS | -0.013738 | -0.14602 | -0.27291 | -2.9008 |  | 138
FLYNN | FLYNN | 2859 | FLYNN N |  |  |  |  | NORTH2001 | DALLAS | -0.013797 | -0.14563 | 0 | 0 |  | 138
FLYNN | FLYNN | 2860 | FLYNN S |  |  |  |  | NORTH2001 | DALLAS | -0.013769 | -0.14582 | 0 | 0 |  | 138
NNTWK | NNTWK | 2861 | N NET 1 |  |  |  |  | NORTH2001 | DALLAS | -0.014307 | -0.14148 | 0 | 0 |  | 138
NNTWK | NNTWK | 2862 | N NET 2 |  |  |  |  | NORTH2001 | DALLAS | -0.013798 | -0.14561 | 0 | 0 |  | 138
NNTWK | NNTWK | 2863 | N NET 3 |  |  |  |  | NORTH2001 | DALLAS | -0.013771 | -0.14581 | 0 | 0 |  | 138
FRMNT | FRMNT | 2864 | FAIRMNT1 | 39.539 |  |  |  | NORTH2001 | DALLAS | -0.013896 | -0.14505 | -0.54942 | -5.735 |  | 138
FRMNT | FRMNT | 2865 | FAIRMNT2 | 40.107 |  |  |  | NORTH2001 | DALLAS | -0.013919 | -0.14488 | -0.55825 | -5.8106 |  | 138
NNTWK | NNTWK | 2866 | N NET13 | 60.939 |  |  |  | NORTH2001 | DALLAS | -0.013959 | -0.1443 | -0.85065 | -8.7933 |  | 13.8
ARMST | ARMST | 2868 | ARMSTG 1 | 34.801 |  |  |  | NORTH2001 | DALLAS | -0.014177 | -0.14332 | -0.49339 | -4.9876 |  | 138
ARMST | ARMST | 2869 | ARMSTG 2 | 54.762 |  |  |  | NORTH2001 | DALLAS | -0.014193 | -0.1432 | -0.77725 | -7.842 |  | 138
WNTWK | WNTWK | 2873 | W NET13 | 60.422 |  |  |  | NORTH2001 | DALLAS | -0.013717 | -0.14497 | -0.82883 | -8.7594 |  | 13.8
WNTWK | WNTWK | 2874 | W NET 1 |  |  |  |  | NORTH2001 | DALLAS | -0.013704 | -0.14564 | 0 | 0 |  | 138
WNTWK | WNTWK | 2875 | W NET 2 |  |  |  |  | NORTH2001 | DALLAS | -0.013723 | -0.14493 | 0 | 0 |  | 138
WNTWK | WNTWK | 2876 | W NET 3 |  |  |  |  | NORTH2001 | DALLAS | -0.013725 | -0.14434 | 0 | 0 |  | 138
GAVSW | GAVSW | 2882 | GRNVL W | 34.813 |  |  |  | NORTH2001 | DALLAS | -0.014473 | -0.14151 | -0.50385 | -4.9263 |  | 138
GAVSW | GAVSW | 2883 | GRNVL E | 42.527 |  |  |  | NORTH2001 | DALLAS | -0.014479 | -0.14145 | -0.61577 | -6.0155 |  | 138
BKWST | BKWST | 2884 | BLKWEL 1 | 17.939 |  |  |  | NORTH2001 | DALLAS | -0.014813 | -0.13986 | -0.26574 | -2.509 |  | 138
BKWST | BKWST | 2885 | BLKWEL 2 | 24.028 |  |  |  | NORTH2001 | DALLAS | -0.014815 | -0.13984 | -0.35598 | -3.3601 |  | 138
JNKNS | JNKNS | 2886 | JENKNS 1 | 18.789 |  |  |  | NORTH2001 | DALLAS | -0.014927 | -0.13932 | -0.28046 | -2.6176 |  | 138
JNKNS | JNKNS | 2887 | JENKNS 2 | 24.985 |  |  |  | NORTH2001 | DALLAS | -0.014927 | -0.13931 | -0.37296 | -3.4806 |  | 138
MTLDA | MTLDA | 2890 | MATILDA1 | 27.15 |  |  |  | NORTH2001 | DALLAS | -0.014473 | -0.14151 | -0.39294 | -3.8419 |  | 138
MTLDA | MTLDA | 2891 | MATILDA2 | 27.405 |  |  |  | NORTH2001 | DALLAS | -0.014479 | -0.14145 | -0.39681 | -3.8765 |  | 138
ABRRD | ABRRD | 2894 | ABRAMS 1 | 20.451 |  |  |  | NORTH2001 | DALLAS | -0.014459 | -0.14143 | -0.2957 | -2.8924 |  | 138
ABRRD | ABRRD | 2895 | ABRAMS 2 | 23.428 |  |  |  | NORTH2001 | DALLAS | -0.014452 | -0.14147 | -0.33858 | -3.3144 |  | 138
LWRDR | LWRDR | 2896 | LAWTHR 1 | 10.495 |  |  |  | NORTH2001 | DALLAS | -0.014408 | -0.14137 | -0.15121 | -1.4837 |  | 138
LWRDR | LWRDR | 2897 | LAWTHR 2 | 11.36 |  |  |  | NORTH2001 | DALLAS | -0.014405 | -0.1414 | -0.16364 | -1.6063 |  | 138
HSKTP | HSKTP | 2898 | HSKEL 1T |  |  |  |  | NORTH2001 | DALLAS | -0.014344 | -0.14131 | 0 | 0 |  | 138
HSKAV | HSKAV | 2899 | HSKEL 1 | 33.212 |  |  |  | NORTH2001 | DALLAS | -0.014344 | -0.14131 | -0.47639 | -4.693 |  | 138
HSKAV | HSKAV | 2900 | HSKEL 2 | 24.326 |  |  |  | NORTH2001 | DALLAS | -0.01433 | -0.14129 | -0.3486 | -3.437 |  | 138
ENTUG | ENTUG | 2902 | E NET13 | 54.526 |  |  |  | NORTH2001 | DALLAS | -0.014325 | -0.14134 | -0.78107 | -7.7068 |  | 13.8
ENTUG | ENTUG | 2903 | E NET 1 | 24.473 |  |  |  | NORTH2001 | DALLAS | -0.01431 | -0.14146 | -0.35021 | -3.4618 |  | 138
ENTUG | ENTUG | 2904 | E NET 2 | 22.193 |  |  |  | NORTH2001 | DALLAS | -0.014333 | -0.14128 | -0.31809 | -3.1355 |  | 138
ENTUG | ENTUG | 2905 | E NET 3 |  |  |  |  | NORTH2001 | DALLAS | -0.014332 | -0.14129 | 0 | 0 |  | 138
NNETT | NNETT | 2906 | N NET 1T |  |  |  |  | NORTH2001 | DALLAS | -0.014308 | -0.14147 | 0 | 0 |  | 138
BRYAN | BRYAN | 2907 | BRYN ST1 | 26.666 |  |  |  | NORTH2001 | DALLAS | -0.014308 | -0.14147 | -0.38155 | -3.7724 |  | 138
BRYAN | BRYAN | 2908 | BRYN ST2 | 16.511 |  |  |  | NORTH2001 | DALLAS | -0.014333 | -0.14128 | -0.23665 | -2.3327 |  | 138
WHTRK | WHTRK | 2913 | WHROCK1 | 30.159 |  |  |  | NORTH2001 | DALLAS | -0.014377 | -0.14091 | -0.43359 | -4.2498 |  | 138
WHTRK | WHTRK | 2914 | WHROCK2 | 28.986 |  |  |  | NORTH2001 | DALLAS | -0.014374 | -0.14092 | -0.41666 | -4.0847 |  | 138
EZACH | EZACH | 2915 | E ZACH1 | 20.378 |  |  |  | NORTH2001 | DALLAS | -0.014403 | -0.14069 | -0.2935 | -2.867 |  | 138
EZACH | EZACH | 2916 | E ZACH2 | 27.243 |  |  |  | NORTH2001 | DALLAS | -0.014401 | -0.1407 | -0.39233 | -3.8331 |  | 138
CNTRD | CNTRD | 2917 | CNVIL 1 | 9.522 |  |  |  | NORTH2001 | DALLAS | -0.014688 | -0.13906 | -0.13986 | -1.3241 |  | 138
CNTRD | CNTRD | 2918 | CNVIL 2 | 11.178 |  |  |  | NORTH2001 | DALLAS | -0.014688 | -0.13906 | -0.16418 | -1.5544 |  | 138
GRLRD | GRLRD | 2919 | GARLDPL1 | 14.3 |  |  |  | NORTH2001 | DALLAS | -0.014755 | -0.13898 | -0.211 | -1.9874 |  | 138
GRLRD | GRLRD | 2920 | GARLDPL2 | 16.505 |  |  |  | NORTH2001 | DALLAS | -0.014755 | -0.13898 | -0.24353 | -2.2939 |  | 138
PROAD | PROAD | 2921 | PLANO 1 | 16.526 |  |  |  | NORTH2001 | DALLAS | -0.014864 | -0.13888 | -0.24564 | -2.2952 |  | 138
PROAD | PROAD | 2922 | PLANO 2 | 34.427 |  |  |  | NORTH2001 | DALLAS | -0.014863 | -0.13888 | -0.51171 | -4.7813 |  | 138
AUDTM | AUDTM | 2923 | L HLDS1T |  |  |  |  | NORTH2001 | DALLAS | -0.014907 | -0.13884 | 0 | 0 |  | 138
AUDTM | AUDTM | 2924 | L HLDS2T |  |  |  |  | NORTH2001 | DALLAS | -0.014907 | -0.13884 | 0 | 0 |  | 138
LKHLD | LKHLD | 2925 | L HLDS1 | 32.823 |  |  |  | NORTH2001 | DALLAS | -0.014907 | -0.13884 | -0.4893 | -4.5573 |  | 138
LKHLD | LKHLD | 2926 | L HLDS2 | 28.651 |  |  |  | NORTH2001 | DALLAS | -0.014907 | -0.13884 | -0.4271 | -3.978 |  | 138
FROKS | FROKS | 2927 | FAIROK 1 | 28.683 |  |  |  | NORTH2001 | DALLAS | -0.014962 | -0.13879 | -0.42915 | -3.981 |  | 138
FROKS | FROKS | 2928 | FAIROK 2 | 30.179 |  |  |  | NORTH2001 | DALLAS | -0.014962 | -0.13879 | -0.45153 | -4.1886 |  | 138
FVWTP | FVWTP | 2929 | FORSTV2T |  |  |  |  | NORTH2001 | DALLAS | -0.014943 | -0.13881 | 0 | 0 |  | 138
FSTVW | FSTVW | 2930 | FORSTV 2 | 30.67 |  |  |  | NORTH2001 | DALLAS | -0.014943 | -0.13881 | -0.45831 | -4.2573 |  | 138
JUDCT | JUDCT | 2931 | JUDD 2 | 28.405 |  |  |  | NORTH2001 | DALLAS | -0.014943 | -0.13881 | -0.42446 | -3.9429 |  | 138
DKCTP | DKCTP | 2934 | DUCKCK T |  |  |  |  | NORTH2001 | DALLAS | -0.014469 | -0.13933 | 0 | 0 |  | 138
DKCRK | DKCRK | 2935 | DUCK CK | 1.553 |  |  |  | NORTH2001 | DALLAS | -0.014469 | -0.13933 | -0.022471 | -0.21638 |  | 138
LHPMP | LHPMP | 2936 | LHUB PMP | 2.517 |  |  |  | NORTH2001 | DALLAS | -0.014469 | -0.13933 | -0.036419 | -0.35069 |  | 138
SATP1 | SATP1 | 2939 | ST AUG1T |  |  |  |  | NORTH2001 | DALLAS | -0.014507 | -0.13975 | 0 | 0 |  | 138
STAUG | STAUG | 2944 | ST AUG1 | 15.809 |  |  |  | NORTH2001 | DALLAS | -0.014507 | -0.13975 | -0.22934 | -2.2093 |  | 138
LKJNP | LKJNP | 2945 | LKJUNE 1 | 3.6 |  |  |  | NORTH2001 | DALLAS | -0.014507 | -0.13975 | -0.052226 | -0.50309 |  | 138
SATP2 | SATP2 | 2951 | ST AUG2T |  |  |  |  | NORTH2001 | DALLAS | -0.014082 | -0.1421 | 0 | 0 |  | 138
PGTP2 | PGTP2 | 2952 | PL GRV2T |  |  |  |  | NORTH2001 | DALLAS | -0.014082 | -0.1421 | 0 | 0 |  | 138
PLGRV | PLGRV | 2953 | PL GRV2 | 17.316 |  |  |  | NORTH2001 | DALLAS | -0.014082 | -0.1421 | -0.24385 | -2.4606 |  | 138
MRTP1 | MRTP1 | 2954 | MURDCK1T |  |  |  |  | NORTH2001 | DALLAS | -0.014082 | -0.1421 | 0 | 0 |  | 138
MRDCK | MRDCK | 2955 | MURDCK1 | 12.428 |  |  |  | NORTH2001 | DALLAS | -0.014082 | -0.1421 | -0.17501 | -1.766 |  | 138
STAUG | STAUG | 2956 | ST AUG2 | 31.746 |  |  |  | NORTH2001 | DALLAS | -0.014082 | -0.1421 | -0.44705 | -4.5112 |  | 138
LKJNP | LKJNP | 2957 | LKJUNE 2 | 3.6 |  |  |  | NORTH2001 | DALLAS | -0.014082 | -0.1421 | -0.050696 | -0.51157 |  | 138
PGTP1 | PGTP1 | 2960 | PL GRV1T |  |  |  |  | NORTH2001 | DALLAS | -0.013366 | -0.14571 | 0 | 0 |  | 138
PLGRV | PLGRV | 2961 | PL GRV1 | 14.897 |  |  |  | NORTH2001 | DALLAS | -0.013366 | -0.14571 | -0.19911 | -2.1707 |  | 138
MRTP2 | MRTP2 | 2962 | MURDCK2T |  |  |  |  | NORTH2001 | DALLAS | -0.01308 | -0.14681 | 0 | 0 |  | 138
MRDCK | MRDCK | 2963 | MURDCK2 | 13.237 |  |  |  | NORTH2001 | DALLAS | -0.01308 | -0.14681 | -0.17314 | -1.9433 |  | 138
HUTCH | HUTCH | 2964 | HUTCH | 27.02 |  |  |  | NORTH2001 | DALLAS | -0.01295 | -0.14731 | -0.3499 | -3.9803 |  | 138
SFTPE | SFTPE | 2965 | SSWWT 1T |  |  |  |  | NORTH2001 | DALLAS | -0.012862 | -0.14765 | 0 | 0 |  | 138
SFILT | SFILT | 2966 | SSWWT 1 | 4.256 |  |  |  | NORTH2001 | DALLAS | -0.012862 | -0.14765 | -0.054739 | -0.62839 |  | 138
OKLTP | OKLTP | 2969 | OAKLND1T |  |  |  |  | NORTH2001 | DALLAS | -0.014134 | -0.14228 | 0 | 0 |  | 138
OKLND | OKLND | 2970 | OAKLND1 | 14.563 |  |  |  | NORTH2001 | DALLAS | -0.014134 | -0.14228 | -0.20583 | -2.072 |  | 138
OKLND | OKLND | 2971 | OAKLND2 | 13.965 |  |  |  | NORTH2001 | DALLAS | -0.014332 | -0.14128 | -0.20014 | -1.973 |  | 138
STHRL | STHRL | 2972 | SUTHLD 1 | 10.04 |  |  |  | NORTH2001 | DALLAS | -0.013601 | -0.14481 | -0.13656 | -1.4539 |  | 138
STHRL | STHRL | 2973 | SUTHLD 2 | 7.416 |  |  |  | NORTH2001 | DALLAS | -0.013904 | -0.14343 | -0.10311 | -1.0637 |  | 138
|  | 2974 | INDUST W |  |  |  |  | NORTH2001 | DALLAS | -0.013725 | -0.14433 | 0 | 0 |  | 138
INDST | INDST | 2975 | INDUST T |  |  |  |  | NORTH2001 | DALLAS | -0.013723 | -0.14434 | 0 | 0 |  | 138
INDST | INDST | 2976 | INDUST E |  |  |  |  | NORTH2001 | DALLAS | -0.013723 | -0.14435 | 0 | 0 |  | 138
WALST | WALST | 2977 | WALL ST1 | 34.102 |  |  |  | NORTH2001 | DALLAS | -0.013723 | -0.14435 | -0.46797 | -4.9225 |  | 138
CMPST | CMPST | 2981 | COMPTON1 | 17.411 |  |  |  | NORTH2001 | DALLAS | -0.013683 | -0.14398 | -0.23824 | -2.5068 |  | 138
CMPST | CMPST | 2982 | COMPTON2 | 13.788 |  |  |  | NORTH2001 | DALLAS | -0.013638 | -0.14356 | -0.18804 | -1.9794 |  | 69.6
WALST | WALST | 2983 | WALL ST2 | 25.159 |  |  |  | NORTH2001 | DALLAS | -0.013638 | -0.14356 | -0.34312 | -3.6118 |  | 69.6
BNTDR | BNTDR | 2984 | BUNTIN 1 | 10.751 |  |  |  | NORTH2001 | DALLAS | -0.013638 | -0.14356 | -0.14662 | -1.5434 |  | 69.6
BNTDR | BNTDR | 2985 | BUNTIN 2 | 13.013 |  |  |  | NORTH2001 | DALLAS | -0.01345 | -0.14453 | -0.17502 | -1.8807 |  | 138
SMPST | SMPST | 2986 | SMP ST2T |  |  |  |  | NORTH2001 | DALLAS | -0.013189 | -0.14587 | 0 | 0 |  | 138
SMPST | SMPST | 2987 | SMP ST2 | 14.877 |  |  |  | NORTH2001 | DALLAS | -0.013189 | -0.14587 | -0.19621 | -2.1701 |  | 138
SMPST | SMPST | 2988 | SMP ST1 | 14.261 |  |  |  | NORTH2001 | DALLAS | -0.012807 | -0.14021 | -0.18265 | -1.9995 |  | 138
SCLFP | SCLFP | 2989 | S CLIFF | 4.265 |  |  |  | NORTH2001 | DALLAS | -0.012837 | -0.13885 | -0.054748 | -0.59219 |  | 138
CMPWI | CMPWI | 2990 | CP WSD 2 | 26.508 |  |  |  | NORTH2001 | DALLAS | -0.012852 | -0.13812 | -0.34069 | -3.6612 |  | 138
SHAMP | SHAMP | 2992 | S HMP 1 | 28.425 |  |  |  | NORTH2001 | DALLAS | -0.012887 | -0.1365 | -0.36632 | -3.8799 |  | 138
SHAMP | SHAMP | 2993 | S HMP 2 | 22.499 |  |  |  | NORTH2001 | DALLAS | -0.012889 | -0.13642 | -0.28999 | -3.0693 |  | 138
LBTP1 | LBTP1 | 2994 | LVBRD 1T |  |  |  |  | NORTH2001 | DALLAS | -0.012904 | -0.1357 | 0 | 0 |  | 138
LVBRD | LVBRD | 2995 | LVBRD 1 | 20.6 |  |  |  | NORTH2001 | DALLAS | -0.012904 | -0.1357 | -0.26583 | -2.7955 |  | 138
DNCNV | DNCNV | 2999 | DVIL | 36.672 |  |  |  | NORTH2001 | DALLAS | -0.012928 | -0.13462 | -0.47409 | -4.9367 |  | 138
WMRLD | WMRLD | 3004 | WMRLND 2 | 27.788 |  |  |  | NORTH2001 | DALLAS | -0.013538 | -0.13723 | -0.3762 | -3.8132 |  | 138
HERTG | HERTG | 3009 | HRTG3 T |  |  |  |  | NORTH2001 | TARRANT | -0.019485 | -0.12167 | 0 | 0 |  | 138
HERTG | HERTG | 3010 | HRTG2 T |  |  |  |  | NORTH2001 | TARRANT | -0.019412 | -0.12172 | 0 | 0 |  | 138
HERTG | HERTG | 3011 | HRTG1 T |  |  |  |  | NORTH2001 | TARRANT | -0.016882 | -0.12206 | 0 | 0 |  | 69
CKRHL | CKRHL | 3014 | CKRELL 1 | 19.65 |  |  |  | NORTH2001 | DALLAS | -0.01357 | -0.13925 | -0.26666 | -2.7362 |  | 138
CKRHL | CKRHL | 3015 | CKRELL 2 | 24.902 |  |  |  | NORTH2001 | DALLAS | -0.013569 | -0.13925 | -0.33788 | -3.4677 |  | 138
HMTRD | HMTRD | 3016 | HMPTON 1 | 12.401 |  |  |  | NORTH2001 | DALLAS | -0.01359 | -0.14051 | -0.16853 | -1.7424 |  | 138
HMTRD | HMTRD | 3017 | HMPTON 2 | 13.819 |  |  |  | NORTH2001 | DALLAS | -0.013589 | -0.14053 | -0.18779 | -1.942 |  | 138
PLKTM | PLKTM | 3018 | POLK 1T |  |  |  |  | NORTH2001 | DALLAS | -0.013601 | -0.1412 | 0 | 0 |  | 138
PLKTM | PLKTM | 3019 | POLK 2T |  |  |  |  | NORTH2001 | DALLAS | -0.0136 | -0.14122 | 0 | 0 |  | 138
PLKST | PLKST | 3020 | POLK 1 | 25.814 |  |  |  | NORTH2001 | DALLAS | -0.013601 | -0.1412 | -0.3511 | -3.6449 |  | 138
PLKST | PLKST | 3021 | POLK 2 | 29.755 |  |  |  | NORTH2001 | DALLAS | -0.0136 | -0.14122 | -0.40467 | -4.2019 |  | 138
DAVST | DAVST | 3022 | DAV ST 2 | 25.984 |  |  |  | NORTH2001 | DALLAS | -0.0136 | -0.14122 | -0.35338 | -3.6694 |  | 138
OKCLS | OKCLS | 3023 | S OKCF 1 | 24.165 |  |  |  | NORTH2001 | DALLAS | -0.013611 | -0.14178 | -0.3289 | -3.4261 |  | 138
OKCLS | OKCLS | 3024 | S OKCF 2 | 26.715 |  |  |  | NORTH2001 | DALLAS | -0.013609 | -0.1418 | -0.36357 | -3.7881 |  | 138
LBTP2 | LBTP2 | 3032 | LVBRD 2T |  |  |  |  | NORTH2001 | DALLAS | -0.01357 | -0.13934 | 0 | 0 |  | 138
LVBRD | LVBRD | 3035 | LVBRD 2 | 14.595 |  |  |  | NORTH2001 | DALLAS | -0.01357 | -0.13934 | -0.19805 | -2.0336 |  | 138
WMRLD | WMRLD | 3042 | WMRLND 1 | 24.201 |  |  |  | NORTH2001 | DALLAS | -0.013431 | -0.13502 | -0.32505 | -3.2676 |  | 69.6
LTV_ | LTV__ | 3043 | LTV 1 | 21.995 |  |  |  | NORTH2001 | DALLAS | -0.013307 | -0.13242 | -0.29268 | -2.9126 |  | 69.6
LTV_ | LTV__ | 3044 | LTV 2 |  |  |  |  | NORTH2001 | DALLAS | -0.013307 | -0.13242 | 0 | 0 |  | 69.6
CDCSW | CDCSW | 3046 | EGL FD T |  |  |  |  | NORTH2001 | DALLAS | -0.012963 | -0.13243 | 0 | 0 |  | 138
EGFRD | EGFRD | 3048 | EGL FD 1 | 9.754 |  |  |  | NORTH2001 | DALLAS | -0.012963 | -0.13243 | -0.12645 | -1.2917 |  | 138
EGFRD | EGFRD | 3049 | EGL FD 2 |  |  |  |  | NORTH2001 | DALLAS | -0.012917 | -0.13248 | 0 | 0 |  | 138
SORCY | SORCY | 3050 | SORCEY 1 | 10.474 |  |  |  | NORTH2001 | DALLAS | -0.012837 | -0.13241 | -0.13446 | -1.3869 |  | 138
SORCY | SORCY | 3051 | SORCEY 2 | 0.605 |  |  |  | NORTH2001 | DALLAS | -0.01283 | -0.13241 | -0.0077624 | -0.080107 |  | 138
DCVSO | DCVSO | 3052 | DVIL S | 55.653 |  |  |  | NORTH2001 | DALLAS | -0.012736 | -0.13233 | -0.70882 | -7.3645 |  | 138
CDHIL | CDHIL | 3053 | CHILLTPL | 22.061 |  |  |  | NORTH2001 | DALLAS | -0.012307 | -0.13196 | -0.27151 | -2.9112 |  | 138
CDHCR | CDHCR | 3054 | CH CLRK | 50.481 |  |  |  | NORTH2001 | DALLAS | -0.012486 | -0.13211 | -0.63032 | -6.6693 |  | 138
DESHR | DESHR | 3059 | DES HP T | 48.93 |  |  |  | NORTH2001 | DALLAS | -0.012394 | -0.13636 | -0.60642 | -6.6723 |  | 138
DESPR | DESPR | 3060 | DES PLS | 56.585 |  |  |  | NORTH2001 | DALLAS | -0.012437 | -0.13857 | -0.70375 | -7.8412 |  | 138
LNCST | LNCST | 3066 | LNCST | 40.078 |  |  |  | NORTH2001 | DALLAS | -0.012515 | -0.14257 | -0.5016 | -5.7139 |  | 138
SGOVL | SGOVL | 3076 | SGVL | 34.364 |  |  |  | NORTH2001 | DALLAS | -0.01357 | -0.14049 | -0.46632 | -4.8278 |  | 138
KLBTP | KLBTP | 3077 | KLEBRG T |  |  |  |  | NORTH2001 | DALLAS | -0.013389 | -0.14166 | 0 | 0 |  | 138
KLBRG | KLBRG | 3078 | KLEBRG 1 | 24.069 |  |  |  | NORTH2001 | DALLAS | -0.013389 | -0.14166 | -0.32227 | -3.4095 |  | 138
SFTPW | SFTPW | 3079 | SSWWT2T |  |  |  |  | NORTH2001 | DALLAS | -0.013072 | -0.1437 | 0 | 0 |  | 138
SFILT | SFILT | 3080 | SSWWT 2 | 4.258 |  |  |  | NORTH2001 | DALLAS | -0.013072 | -0.1437 | -0.055662 | -0.61189 |  | 138
WILMR | WILMR | 3083 | WILMER |  |  |  |  | NORTH2001 | DALLAS | -0.01285 | -0.14514 | 0 | 0 |  | 138
WILMR | WILMR | 3084 | WILMER |  |  |  |  | NORTH2001 | DALLAS | -0.011836 | -0.13127 | 0 | 0 |  | 69.6
MLSES | MLSES | 3097 | MTNLK 1G |  |  | 750 | 756 | NORTH2001 | RUSK | -0.012299 | -0.11851 | -9.298 | -89.5972 |  | 20
MLSES | MLSES | 3098 | MTNLK 2G |  |  | 785 | 785 | NORTH2001 | RUSK | -0.012299 | -0.11851 | -9.6547 | -93.0341 |  | 20
MLSES | MLSES | 3099 | MTNLK 3G |  |  | 750 | 757 | NORTH2001 | RUSK | -0.012299 | -0.11851 | -9.3103 | -89.7157 |  | 20
MLSES | MLSES | 3100 | MARTINLK | 28.405 |  |  |  | NORTH2001 | RUSK | -0.012299 | -0.11851 | -0.34935 | -3.3664 |  | 345
SHBSW | SHBSW | 3103 | SHAMBRGR |  |  |  |  | NORTH2001 | SMITH | -0.013264 | -0.12226 | 0 | 0 |  | 345
SHBSW | SHBSW | 3104 | SHAMBRGR |  |  |  |  | NORTH2001 | SMITH | -0.012837 | -0.11877 | 0 | 0 |  | 138
ELKTN | ELKTN | 3105 | ELKTON |  |  |  |  | NORTH2001 | SMITH | -0.01276 | -0.12192 | 0 | 0 |  | 345
ELKTN | ELKTN | 3106 | ELKTON | 28.051 |  |  |  | NORTH2001 | SMITH | -0.012433 | -0.11552 | -0.34876 | -3.2404 |  | 138
SCSES | SCSES | 3107 | STRYK 1G |  |  | 164 | 181 | NORTH2001 | CHEROKEE | -0.011737 | -0.1092 | -2.1243 | -19.7645 |  | 13.8
SCSES | SCSES | 3108 | STRYK 2G |  |  | 468 | 510 | NORTH2001 | CHEROKEE | -0.011737 | -0.1092 | -5.9857 | -55.69 |  | 19
SCSES | SCSES | 3109 | STRYKER |  |  |  |  | NORTH2001 | CHEROKEE | -0.011617 | -0.11081 | 0 | 0 |  | 345
SCSES | SCSES | 3110 | STRYKER | 0.221 |  |  |  | NORTH2001 | CHEROKEE | -0.011737 | -0.1092 | -0.0025938 | -0.024132 |  | 138
SMRFT | SMRFT | 3112 | SMRFLD M |  |  |  |  | NORTH2001 | CHEROKEE | -0.01188 | -0.11049 | 0 | 0 |  | 138
PLSAL | PLSAL | 3114 | PAL ALCO |  |  |  |  | NORTH2001 | ANDERSON | -0.010935 | -0.089908 | 0 | 0 |  | 138
TGCCS | TGCCS | 3116 | TNSKGATE |  |  |  |  | NORTH2001 | RUSK | -0.012013 | -0.11484 | 0 | 0 |  | 345
LFKSW | LFKSW | 3117 | LUFKN SS |  |  |  |  | NORTH2001 | ANGELINA | -0.011674 | -0.11113 | 0 | 0 |  | 345
LFKSW | LFKSW | 3118 | LUFKN SS |  |  |  |  | NORTH2001 | ANGELINA | -0.011742 | -0.11151 | 0 | 0 |  | 138
NCDSE | NCDSE | 3119 | NACOG SE |  |  |  |  | NORTH2001 | NACOGDOCHES | -0.011964 | -0.11413 | 0 | 0 |  | 345
NCDSE | NCDSE | 3120 | NACOG SE |  |  |  |  | NORTH2001 | NACOGDOCHES | -0.011864 | -0.11269 | 0 | 0 |  | 138
TRSES | TRSES | 3123 | TRINDAD1 |  |  |  |  | NORTH2001 | HENDERSON | -0.010218 | -0.098494 | 0 | 0 |  | 345
TRSES | TRSES | 3124 | TRINDAD2 |  |  |  |  | NORTH2001 | HENDERSON | -0.010673 | -0.097873 | 0 | 0 |  | 345
TRSES | TRSES | 3125 | TDADTMOD |  |  |  |  | NORTH2001 | HENDERSON | -0.01107 | -0.10757 | 0 | 0 |  | 138
TRSES | TRSES | 3126 | TDAD 6 G |  |  | 211 | 240 | NORTH2001 | HENDERSON | -0.01107 | -0.10757 | -2.6568 | -25.816 |  | 21
TRSES | TRSES | 3127 | TRINIDAD |  |  |  |  | NORTH2001 | HENDERSON | -0.01107 | -0.10757 | 0 | 0 |  | 138
TRSES | TRSES | 3128 | TRINIDAD | 4.507 |  |  |  | NORTH2001 | HENDERSON | -0.01096 | -0.10568 | -0.049395 | -0.47632 |  | 69.6
FGRSW | FGRSW | 3130 | FOR GROV |  |  |  |  | NORTH2001 | HENDERSON | -0.010777 | -0.099207 | 0 | 0 |  | 345
FGRSW | FGRSW | 3131 | FOR GROV |  |  |  |  | NORTH2001 | HENDERSON | -0.011189 | -0.10445 | 0 | 0 |  | 138
TYWST | TYWST | 3139 | TYLER W | 48.283 |  |  |  | NORTH2001 | SMITH | -0.012577 | -0.11667 | -0.60723 | -5.6333 |  | 138
TYWST | TYWST | 3140 | TYLER W |  |  |  |  | NORTH2001 | SMITH | -0.012619 | -0.11702 | 0 | 0 |  | 69.6
TYLNW | TYLNW | 3141 | TYLER NW | 8.925 |  |  |  | NORTH2001 | SMITH | -0.012683 | -0.11753 | -0.1132 | -1.049 |  | 138
TYLNW | TYLNW | 3142 | TYLER NW |  |  |  |  | NORTH2001 | SMITH | -0.012638 | -0.11716 | 0 | 0 |  | 69.6
TYLSE | TYLSE | 3143 | TYLER SE |  |  |  |  | NORTH2001 | SMITH | -0.012468 | -0.11569 | 0 | 0 |  | 138
OVRTN | OVRTN | 3144 | OVERTON |  |  |  |  | NORTH2001 | RUSK | -0.012468 | -0.11569 | 0 | 0 |  | 138
TROUP | TROUP | 3147 | TROUP |  |  |  |  | NORTH2001 | CHEROKEE | -0.01213 | -0.11269 | 0 | 0 |  | 138
TROUP | TROUP | 3148 | TROUPPOD |  |  |  |  | NORTH2001 | CHEROKEE | -0.01213 | -0.11269 | 0 | 0 |  | 69.6
DIBSP | DIBSP | 3154 | DIBOL SP | 25.156 |  |  |  | NORTH2001 | ANGELINA | -0.011754 | -0.11162 | -0.29568 | -2.8078 |  | 138
DIBOL | DIBOL | 3155 | DIBOLL | 14.25 |  |  |  | NORTH2001 | ANGELINA | -0.011754 | -0.11162 | -0.16749 | -1.5905 |  | 138
DIALV | DIALV | 3160 | DIALVILL |  |  |  |  | NORTH2001 | CHEROKEE | -0.011186 | -0.097656 | 0 | 0 |  | 138
DIALV | DIALV | 3161 | DIAL POD |  |  |  |  | NORTH2001 | CHEROKEE | -0.011186 | -0.097656 | 0 | 0 |  | 69.4
|  | 3167 | ENTERP P |  |  |  |  | NORTH2001 | VAN ZANDT | -0.013705 | -0.12225 | 0 | 0 |  | 138
IRBTP | IRBTP | 3168 | IRONBR T |  |  |  |  | NORTH2001 | VAN ZANDT | -0.013705 | -0.12225 | 0 | 0 |  | 138
IRBRG | IRBRG | 3169 | IRONBRG | 8.078 |  |  |  | NORTH2001 | HUNT | -0.013705 | -0.12225 | -0.11071 | -0.98755 |  | 138
EMORY | EMORY | 3170 | EMORY |  |  |  |  | NORTH2001 | RAINS | -0.014125 | -0.12494 | 0 | 0 |  | 138
EMPOD | EMPOD | 3171 | EMORY N |  |  |  |  | NORTH2001 | RAINS | -0.014647 | -0.12828 | 0 | 0 |  | 138
CNTSW | CNTSW | 3174 | CANTN SS |  |  |  |  | NORTH2001 | VAN ZANDT | -0.013041 | -0.11801 | 0 | 0 |  | 138
CANTN | CANTN | 3175 | CANTON | 19.733 |  |  |  | NORTH2001 | VAN ZANDT | -0.012694 | -0.11547 | -0.2505 | -2.2786 |  | 138
MABNK | MABNK | 3176 | MABANK | 31.434 |  |  |  | NORTH2001 | HENDERSON | -0.011704 | -0.10822 | -0.36792 | -3.4019 |  | 138
EUSTC | EUSTC | 3177 | EUSTACE | 9.851 |  |  |  | NORTH2001 | HENDERSON | -0.011389 | -0.10592 | -0.11219 | -1.0434 |  | 138
EUSSE | EUSSE | 3178 | EUSTC SE |  |  |  |  | NORTH2001 | HENDERSON | -0.011366 | -0.10575 | 0 | 0 |  | 138
EDGWD | EDGWD | 3181 | EDGEWOOD | 5.321 |  |  |  | NORTH2001 | VAN ZANDT | -0.013416 | -0.1204 | -0.071385 | -0.64066 |  | 138
EDGWD | EDGWD | 3182 | EDGEWOOD |  |  |  |  | NORTH2001 | VAN ZANDT | -0.013416 | -0.1204 | 0 | 0 |  | 69
VAN | VAN__ | 3183 | VAN | 15.104 |  |  |  | NORTH2001 | VAN ZANDT | -0.012863 | -0.11728 | -0.19429 | -1.7714 |  | 138
|  | 3184 | PRIMROSE |  |  |  |  | NORTH2001 | VAN ZANDT | -0.012736 | -0.11676 | 0 | 0 |  | 138
IRBRG | IRBRG | 3185 | IRONBRG |  |  |  |  | NORTH2001 | HUNT | -0.013705 | -0.12225 | 0 | 0 |  | 69.6
DCVT1 | DCVT1 | 3187 | IRNBRG T |  |  |  |  | NORTH2001 | VAN ZANDT | -0.013416 | -0.1204 | 0 | 0 |  | 69.6
WLSPT | WLSPT | 3188 | WILLS PT | 17.539 |  |  |  | NORTH2001 | VAN ZANDT | -0.013416 | -0.1204 | -0.2353 | -2.1117 |  | 69.6
BSTTP | BSTTP | 3189 | BTSTAR T |  |  |  |  | NORTH2001 | VAN ZANDT | -0.013705 | -0.12225 | 0 | 0 |  | 69.6
BRTST | BRTST | 3190 | BRITSTAR |  |  |  |  | NORTH2001 | VAN ZANDT | -0.013705 | -0.12225 | 0 | 0 |  | 69.6
DCVT2 | DCVT2 | 3191 | DUCKCV T |  |  |  |  | NORTH2001 | HUNT | -0.013705 | -0.12225 | 0 | 0 |  | 69.6
DCKCV | DCKCV | 3192 | DUCKCOVE |  |  |  |  | NORTH2001 | KAUFMAN | -0.013705 | -0.12225 | 0 | 0 |  | 69.6
TYLSW | TYLSW | 3197 | TYLER SS |  |  |  |  | NORTH2001 | SMITH | -0.012529 | -0.11591 | 0 | 0 |  | 138
TYLKT | TYLKT | 3198 | TYLR KLY | 16.507 |  |  |  | NORTH2001 | SMITH | -0.012529 | -0.11591 | -0.20681 | -1.9133 |  | 138
LNDAL | LNDAL | 3201 | LINDALE | 15.758 |  |  |  | NORTH2001 | SMITH | -0.01275 | -0.11807 | -0.20091 | -1.8605 |  | 138
SWAN2 | SWAN2 | 3202 | SWAN 2 | 7.381 |  |  |  | NORTH2001 | SMITH | -0.012708 | -0.11773 | -0.093801 | -0.86898 |  | 138
LNDAL | LNDAL | 3203 | LNDALE T |  |  |  |  | NORTH2001 | SMITH | -0.012732 | -0.11793 | 0 | 0 |  | 138
TYPIP | TYPIP | 3204 | TYLER PP | 9.66 |  |  |  | NORTH2001 | SMITH | -0.012708 | -0.11773 | -0.12276 | -1.1373 |  | 138
HDWLK | HDWLK | 3205 | HIDAWYLK | 12.783 |  |  |  | NORTH2001 | SMITH | -0.012732 | -0.11793 | -0.16276 | -1.5074 |  | 138
TYLER | TYLER | 3207 | TYLER | 30.82 |  |  |  | NORTH2001 | SMITH | -0.012626 | -0.11707 | -0.38913 | -3.608 |  | 69.6
TYLNE | TYLNE | 3210 | TYLER NE | 31.542 |  |  |  | NORTH2001 | SMITH | -0.012778 | -0.11828 | -0.40306 | -3.7307 |  | 138
TYEST | TYEST | 3211 | TYLER E | 52.903 |  |  |  | NORTH2001 | SMITH | -0.012668 | -0.11736 | -0.67019 | -6.2088 |  | 138
TYOMN | TYOMN | 3212 | TYLR OMN | 58.596 |  |  |  | NORTH2001 | SMITH | -0.012568 | -0.11653 | -0.73646 | -6.8281 |  | 138
TYLGE | TYLGE | 3213 | TYLER GE | 42.954 |  |  |  | NORTH2001 | SMITH | -0.012498 | -0.11594 | -0.53683 | -4.9801 |  | 138
TYSTH | TYSTH | 3218 | TYLER S | 31.873 |  |  |  | NORTH2001 | SMITH | -0.012451 | -0.11561 | -0.39685 | -3.6847 |  | 138
TYBLR | TYBLR | 3219 | TYLR BUL | 62.872 |  |  |  | NORTH2001 | SMITH | -0.012442 | -0.11556 | -0.78226 | -7.2656 |  | 138
TSLVL | TSLVL | 3222 | TEASELVL | 26.364 |  |  |  | NORTH2001 | SMITH | -0.011971 | -0.10762 | -0.3156 | -2.8373 |  | 138
TEASELM | TEASELM | 3224 | TEASEL M |  |  |  |  | NORTH2001 | SMITH | -0.011851 | -0.10556 | 0 | 0 |  | 138
WHOUS | WHOUS | 3227 | WTHS POD |  |  |  |  | NORTH2001 | SMITH | -0.012377 | -0.11488 | 0 | 0 |  | 138
SWINY | SWINY | 3230 | SWINYTWN |  |  |  |  | NORTH2001 | SMITH | -0.012468 | -0.11569 | 0 | 0 |  | 138
OVRTN | OVRTN | 3231 | OVERTPOD |  |  |  |  | NORTH2001 | RUSK | -0.012468 | -0.11569 | 0 | 0 |  | 69.6
TYLSW | TYLSW | 3234 | TYLER SS |  |  |  |  | NORTH2001 | SMITH | -0.012619 | -0.11702 | 0 | 0 |  | 69.6
CHNDL | CHNDL | 3235 | CHADLER | 7.066 |  |  |  | NORTH2001 | HENDERSON | -0.012619 | -0.11702 | -0.089168 | -0.82683 |  | 69.6
BNBOR | BNBOR | 3236 | BRNSBORO | 7.882 |  |  |  | NORTH2001 | HENDERSON | -0.012619 | -0.11702 | -0.099465 | -0.92232 |  | 69.6
MCREA | MCREA | 3237 | MURCHREA |  |  |  |  | NORTH2001 | HENDERSON | -0.011317 | -0.10678 | 0 | 0 |  | 69.6
ATHNS | ATHNS | 3238 | ATHENS |  |  |  |  | NORTH2001 | HENDERSON | -0.011486 | -0.1073 | 0 | 0 |  | 138
ATHNS | ATHNS | 3239 | ATHENS | 15.192 |  |  |  | NORTH2001 | HENDERSON | -0.011317 | -0.10678 | -0.17192 | -1.6222 |  | 69.6
MCHSN | MCHSN | 3240 | MURCHISN | 0.869 |  |  |  | NORTH2001 | HENDERSON | -0.011317 | -0.10678 | -0.0098342 | -0.092792 |  | 69.6
ATHTP | ATHTP | 3247 | ATHENS T |  |  |  |  | NORTH2001 | HENDERSON | -0.011488 | -0.10731 | 0 | 0 |  | 138
ATHNW | ATHNW | 3248 | ATHNS NW | 39.181 |  |  |  | NORTH2001 | HENDERSON | -0.011419 | -0.10665 | -0.44741 | -4.1786 |  | 138
JKSVL | JKSVL | 3252 | JACK POD |  |  |  |  | NORTH2001 | CHEROKEE | -0.012093 | -0.11243 | 0 | 0 |  | 69.4
JKSVL | JKSVL | 3253 | JACKSNVL |  |  |  |  | NORTH2001 | CHEROKEE | -0.012093 | -0.11243 | 0 | 0 |  | 138
JKSVL | JKSVL | 3254 | JACKSNVL |  |  |  |  | NORTH2001 | CHEROKEE | -0.012093 | -0.11243 | 0 | 0 |  | 69.6
FRNKS | FRNKS | 3255 | FRANKSTN | 1.498 |  |  |  | NORTH2001 | ANDERSON | -0.012093 | -0.11243 | -0.018115 | -0.16842 |  | 69.6
POYNR | POYNR | 3256 | POYNOR | 2.588 |  |  |  | NORTH2001 | ANDERSON | -0.011317 | -0.10678 | -0.029288 | -0.27635 |  | 69.6
NPKTP | NPKTP | 3260 | NIPAK T |  |  |  |  | NORTH2001 | HENDERSON | -0.011207 | -0.10893 | 0 | 0 |  | 138
NIPAK | NIPAK | 3261 | NIPAK | 0.266 |  |  |  | NORTH2001 | HENDERSON | -0.011207 | -0.10893 | -0.0029811 | -0.028977 |  | 138
CDCRK | CDCRK | 3262 | CEDR CRK | 4.74 |  |  |  | NORTH2001 | HENDERSON | -0.011665 | -0.11351 | -0.055294 | -0.53803 |  | 138
CCPMP | CCPMP | 3263 | CEDR CKP | 7.874 |  |  |  | NORTH2001 | HENDERSON | -0.011665 | -0.11351 | -0.091853 | -0.89377 |  | 138
SVPTS | SVPTS | 3264 | SEVENPTS |  |  |  |  | NORTH2001 | HENDERSON | -0.012108 | -0.11793 | 0 | 0 |  | 138
MLKOF | MLKOF | 3267 | MALAKOFF |  |  |  |  | NORTH2001 | HENDERSON | -0.011109 | -0.10614 | 0 | 0 |  | 69.6
WLWSP | WLWSP | 3269 | WILOW SP | 2.349 |  |  |  | NORTH2001 | HENDERSON | -0.010718 | -0.098043 | -0.025175 | -0.2303 |  | 69.6
CRLSP | CRLSP | 3270 | CAROLSPG |  |  |  |  | NORTH2001 | ANDERSON | -0.010473 | -0.090318 | 0 | 0 |  | 69.6
PLSTH | PLSTH | 3271 | PALSTN S | 28.505 |  |  |  | NORTH2001 | ANDERSON | -0.010282 | -0.078735 | -0.2931 | -2.2443 |  | 138
PLSTN | PLSTN | 3272 | PALESTNE | 35.646 |  |  |  | NORTH2001 | ANDERSON | -0.010336 | -0.079672 | -0.36842 | -2.84 |  | 138
PLSTN | PLSTN | 3273 | PALESTNE |  |  |  |  | NORTH2001 | ANDERSON | -0.0099607 | -0.07415 | 0 | 0 |  | 69.6
MAREA | MAREA | 3274 | MONTALBA |  |  |  |  | NORTH2001 | ANDERSON | -0.010228 | -0.08259 | 0 | 0 |  | 69.6
MLKF2 | MLKF2 | 3276 | MALAKOFF | 10.304 |  |  |  | NORTH2001 | HENDERSON | -0.011132 | -0.10594 | -0.11471 | -1.0916 |  | 138
BLKFT | BLKFT | 3282 | BLACKFT | 8.177 |  |  |  | NORTH2001 | ANDERSON | -0.0098565 | -0.074769 | -0.080597 | -0.61138 |  | 138
NECSP | NECSP | 3296 | NECHES | 1.468 |  |  |  | NORTH2001 | ANDERSON | -0.010625 | -0.085912 | -0.015597 | -0.12612 |  | 138
CSHNG | CSHNG | 3299 | CUSHING | 6.114 |  |  |  | NORTH2001 | NACOGDOCHES | -0.011777 | -0.11029 | -0.072002 | -0.67433 |  | 138
CSETP | CSETP | 3300 | CUSH SE |  |  |  |  | NORTH2001 | NACOGDOCHES | -0.011798 | -0.11087 | 0 | 0 |  | 138
NCDCH | NCDCH | 3303 | NACGDCHS | 38.227 |  |  |  | NORTH2001 | NACOGDOCHES | -0.011832 | -0.11182 | -0.45232 | -4.2746 |  | 138
NCNTH | NCNTH | 3310 | NACOG N | 32.263 |  |  |  | NORTH2001 | NACOGDOCHES | -0.011843 | -0.11212 | -0.38211 | -3.6174 |  | 138
NCSFA | NCSFA | 3311 | NAC SFA | 30.242 |  |  |  | NORTH2001 | NACOGDOCHES | -0.011852 | -0.11235 | -0.35842 | -3.3977 |  | 138
CHRNO | CHRNO | 3312 | CHIRENO | 3.288 |  |  |  | NORTH2001 | NACOGDOCHES | -0.011864 | -0.11269 | -0.03901 | -0.37054 |  | 138
NCSTH | NCSTH | 3315 | NACOG S | 33.188 |  |  |  | NORTH2001 | NACOGDOCHES | -0.011853 | -0.11258 | -0.39339 | -3.7361 |  | 138
NCSTP | NCSTP | 3316 | NACOG ST |  |  |  |  | NORTH2001 | NACOGDOCHES | -0.01184 | -0.11243 | 0 | 0 |  | 138
HNRSW | HNRSW | 3319 | HERTY N |  |  |  |  | NORTH2001 | ANGELINA | -0.011793 | -0.11195 | 0 | 0 |  | 138
HNTNG | HNTNG | 3320 | HUNTNGTN | 21.452 |  |  |  | NORTH2001 | ANGELINA | -0.011793 | -0.11195 | -0.25297 | -2.4016 |  | 138
|  | 3321 | ZAVPMP T |  |  |  |  | NORTH2001 | ANGELINA | -0.011793 | -0.11195 | 0 | 0 |  | 138
|  | 3323 | ETOILE |  |  |  |  | NORTH2001 | NACOGDOCHES | -0.011793 | -0.11195 | 0 | 0 |  | 138
LFEST | LFEST | 3326 | LUFKIN E | 37.626 |  |  |  | NORTH2001 | ANGELINA | -0.011773 | -0.11178 | -0.44298 | -4.2059 |  | 138
LFSTE | LFSTE | 3327 | DIBOL ET |  |  |  |  | NORTH2001 | ANGELINA | -0.011765 | -0.11171 | 0 | 0 |  | 138
LFSTH | LFSTH | 3328 | LUFKIN S | 41.216 |  |  |  | NORTH2001 | ANGELINA | -0.01176 | -0.11167 | -0.48471 | -4.6026 |  | 138
LFPTP | LFPTP | 3329 | LUFPRS T |  |  |  |  | NORTH2001 | ANGELINA | -0.011757 | -0.11165 | 0 | 0 |  | 138
LPRSH | LPRSH | 3330 | LUF PRSH | 10.337 |  |  |  | NORTH2001 | ANGELINA | -0.011757 | -0.11165 | -0.12154 | -1.1541 |  | 138
LFSTW | LFSTW | 3331 | DIBOL WT |  |  |  |  | NORTH2001 | ANGELINA | -0.011754 | -0.11162 | 0 | 0 |  | 138
HUDSN | HUDSN | 3332 | HUDSON | 35.307 |  |  |  | NORTH2001 | ANGELINA | -0.011748 | -0.11156 | -0.41477 | -3.9389 |  | 138
TXFTP | TXFTP | 3333 | TX FND T |  |  |  |  | NORTH2001 | ANGELINA | -0.011744 | -0.11153 | 0 | 0 |  | 138
TXFND | TXFND | 3334 | TX FNDRY | 53.626 |  |  |  | NORTH2001 | ANGELINA | -0.011744 | -0.11153 | -0.62977 | -5.9807 |  | 138
LUFKN | LUFKN | 3340 | LUFKIN | 62.653 |  |  |  | NORTH2001 | ANGELINA | -0.011763 | -0.11161 | -0.737 | -6.9929 |  | 138
CNANG | CNANG | 3341 | CNTL ANG | 14.028 |  |  |  | NORTH2001 | ANGELINA | -0.011759 | -0.11124 | -0.16496 | -1.5604 |  | 138
BAYLC | BAYLC | 3342 | BAYOU LC | 0.284 |  |  |  | NORTH2001 | NACOGDOCHES | -0.011753 | -0.11067 | -0.0033378 | -0.031431 |  | 138
DGLAS | DGLAS | 3343 | DOUGLAS | 3.979 |  |  |  | NORTH2001 | NACOGDOCHES | -0.011749 | -0.11036 | -0.046751 | -0.43913 |  | 138
CHMPT | CHMPT | 3346 | CHAMPN T |  |  |  |  | NORTH2001 | ANGELINA | -0.011773 | -0.11173 | 0 | 0 |  | 138
CHAMP | CHAMP | 3347 | CHAMPION | 35.291 |  |  |  | NORTH2001 | ANGELINA | -0.011773 | -0.11173 | -0.41549 | -3.943 | 1 | 138
|  | 3348 | CHAMPN G |  |  | 42 | 0 | NORTH2001 | ANGELINA | -0.011773 | -0.11173 | 0 | 0 | 1 | 13.8
LFCML | LFCML | 3349 | TMPL INL | 0.606 |  |  |  | NORTH2001 | ANGELINA | -0.011742 | -0.11151 | -0.0071158 | -0.067578 |  | 138
KENRD | KENRD | 3350 | KENNARD |  |  |  |  | NORTH2001 | HOUSTON | -0.011742 | -0.11151 | 0 | 0 |  | 138
BEREA | BEREA | 3351 | BEREA |  |  |  |  | NORTH2001 | HOUSTON | -0.011742 | -0.11151 | 0 | 0 |  | 138
MTFSW | MTFSW | 3454 | MONTFTSS |  |  |  |  | NORTH2001 | NAVARRO | -0.011104 | -0.11187 | 0 | 0 |  | 138
CRSCN | CRSCN | 3455 | CORS | 33.335 |  |  |  | NORTH2001 | NAVARRO | -0.010794 | -0.10956 | -0.35982 | -3.6523 |  | 138
CRSWS | CRSWS | 3456 | CORS W | 28.833 |  |  |  | NORTH2001 | NAVARRO | -0.010668 | -0.10863 | -0.3076 | -3.132 |  | 138
CMOTP | CMOTP | 3457 | CORSMB T |  |  |  |  | NORTH2001 | NAVARRO | -0.010577 | -0.10795 | 0 | 0 |  | 138
CRMBL | CRMBL | 3458 | CORS MB | 1.215 |  |  |  | NORTH2001 | NAVARRO | -0.010577 | -0.10795 | -0.012851 | -0.13116 |  | 138
CRMPM | CRMPM | 3459 | CORS MAG | 3.167 |  |  |  | NORTH2001 | NAVARRO | -0.010556 | -0.10779 | -0.03343 | -0.34137 |  | 138
CORGT | CORGT | 3460 | CORSGL T |  |  |  |  | NORTH2001 | NAVARRO | -0.010554 | -0.10778 | 0 | 0 |  | 138
CRSGL | CRSGL | 3461 | CORSGLAS | 22.683 |  |  |  | NORTH2001 | NAVARRO | -0.010554 | -0.10778 | -0.2394 | -2.4447 |  | 138
CRGTP | CRGTP | 3462 | CORSGR T |  |  |  |  | NORTH2001 | NAVARRO | -0.010516 | -0.10749 | 0 | 0 |  | 138
CRSGU | CRSGU | 3463 | CORSGUAR | 10.082 |  |  |  | NORTH2001 | NAVARRO | -0.010516 | -0.10749 | -0.10602 | -1.0837 |  | 138
KERNS | KERNS | 3464 | EQUIPIPE | 3.28 |  |  |  | NORTH2001 | NAVARRO | -0.0069369 | -0.092032 | -0.022753 | -0.30187 |  | 69.6
|  | 3466 | KERENS | 3.92 |  |  |  | NORTH2001 | NAVARRO | -0.010944 | -0.10817 | -0.042902 | -0.42402 |  | 69.6
POWEL | POWEL | 3467 | POWELL | 1.248 |  |  |  | NORTH2001 | NAVARRO | -0.010939 | -0.10897 | -0.013652 | -0.136 |  | 69.6
CRSCN | CRSCN | 3468 | CORS |  |  |  |  | NORTH2001 | NAVARRO | -0.010926 | -0.11121 | 0 | 0 |  | 69.6
BLMGR | BLMGR | 3470 | BLOOMGRV | 2.353 |  |  |  | NORTH2001 | NAVARRO | -0.010926 | -0.11121 | -0.025708 | -0.26169 |  | 69.6
BARRY | BARRY | 3471 | BARRY | 1.27 |  |  |  | NORTH2001 | NAVARRO | -0.010926 | -0.11121 | -0.013876 | -0.14124 |  | 69.6
CRMTP | CRMTP | 3475 | CORSMGSS |  |  |  |  | NORTH2001 | NAVARRO | -0.010865 | -0.11034 | 0 | 0 |  | 69.6
V_EURKA | V_EURKA | 3477 | EUREKA M |  |  |  |  | NORTH2001 | NAVARRO | -0.01063 | -0.10689 | 0 | 0 |  | 138
NVARO | NVARO | 3478 | NAVARRO |  |  |  |  | NORTH2001 | NAVARRO | -0.010383 | -0.1065 | 0 | 0 |  | 138
NVARO | NVARO | 3479 | NAVARRO | 1.563 |  |  |  | NORTH2001 | NAVARRO | -0.010708 | -0.10809 | -0.016737 | -0.16894 |  | 69.4
MLDR2 | MLDR2 | 3480 | MILDRD#2 | 2.547 |  |  |  | NORTH2001 | NAVARRO | -0.010759 | -0.10881 | -0.027403 | -0.27715 |  | 69.4
GDLTP | GDLTP | 3483 | GOODLW M |  |  |  |  | NORTH2001 | NAVARRO | -0.010763 | -0.10709 | 0 | 0 |  | 138
RCHLD | RCHLD | 3486 | RICHLAND | 1.782 |  |  |  | NORTH2001 | NAVARRO | -0.010708 | -0.10809 | -0.019082 | -0.19261 |  | 69.4
WRGPT | WRGPT | 3487 | WRTHMPOD |  |  |  |  | NORTH2001 | FREESTONE | -0.010708 | -0.10809 | 0 | 0 |  | 69.4
|  | 3488 | WTXGFPOD |  |  |  |  | NORTH2001 | FREESTONE | -0.010708 | -0.10809 | 0 | 0 |  | 69.4
NVARO | NVARO | 3496 | STSUPR T |  |  |  |  | NORTH2001 | NAVARRO | -0.010709 | -0.10808 | 0 | 0 |  | 69.4
SPRRK | SPRRK | 3497 | STSUPRCK | 2.283 |  |  |  | NORTH2001 | NAVARRO | -0.010709 | -0.10808 | -0.024449 | -0.24674 |  | 69.4
EURKA | EURKA | 3498 | EUREKA | 0.388 |  |  |  | NORTH2001 | NAVARRO | -0.010792 | -0.10728 | -0.0041873 | -0.041627 |  | 69.4
BLKTP | BLKTP | 3499 | BLFT TAP |  |  |  |  | NORTH2001 | ANDERSON | -0.0098565 | -0.074769 | 0 | 0 |  | 138
FRFBE | FRFBE | 3504 | FAIRFL M |  |  |  |  | NORTH2001 | FREESTONE | -0.010303 | -0.086836 | 0 | 0 |  | 138
BBNTP | BBNTP | 3505 | BIGBRN T |  |  |  |  | NORTH2001 | FREESTONE | -0.010303 | -0.086836 | 0 | 0 |  | 138
BBMN1 | BBMN1 | 3506 | BIGBRNM1 | 7.132 |  |  |  | NORTH2001 | FREESTONE | -0.010258 | -0.085618 | -0.07316 | -0.61063 |  | 138
BBMN2 | BBMN2 | 3507 | BIGBRNM2 | 2.531 |  |  |  | NORTH2001 | FREESTONE | -0.01012 | -0.081886 | -0.025613 | -0.20725 |  | 138
WNKLR | WNKLR | 3508 | WINKLR M |  |  |  |  | NORTH2001 | FREESTONE | -0.010576 | -0.094215 | 0 | 0 |  | 138
BBMN1 | BBMN1 | 3509 | BB OPEN |  |  |  |  | NORTH2001 | FREESTONE | -0.01012 | -0.081886 | 0 | 0 |  | 138
BBNTP | BBNTP | 3510 | BB OPENT |  |  |  |  | NORTH2001 | FREESTONE | -0.010303 | -0.086836 | 0 | 0 |  | 138
NVRML | NVRML | 3511 | NAVMILLS | 1.182 |  |  |  | NORTH2001 | NAVARRO | -0.0067841 | -0.076494 | -0.0080188 | -0.090415 |  | 69
HANEY | HANEY | 3514 | HANEY M |  |  |  |  | NORTH2001 | NAVARRO | -0.0091811 | -0.10224 | 0 | 0 |  | 138
HUBRD | HUBRD | 3515 | HUBBARD | 8.782 |  |  |  | NORTH2001 | HILL | -0.0075813 | -0.096559 | -0.066579 | -0.84798 |  | 138
CHTTT | CHATM | 3516 | CHATT M |  |  |  |  | NORTH2001 | BOSQUE | -0.0061026 | -0.09131 | 0 | 0 |  | 138
BLUM | BLUM_ | 3518 | BLUM | 3.414 |  |  |  | NORTH2001 | HILL | -0.0077463 | -0.099096 | -0.026446 | -0.33831 |  | 138
HLSBR | HLSBR | 3522 | HILLBR | 29.936 |  |  |  | NORTH2001 | HILL | -0.0054421 | -0.088966 | -0.16292 | -2.6633 |  | 138
HLSBR | HLSBR | 3523 | HILLBR |  |  |  |  | NORTH2001 | HILL | -0.0069369 | -0.092032 | 0 | 0 |  | 69.6
ABBOT | ABBOT | 3524 | ABBOTT | 1.174 |  |  |  | NORTH2001 | HILL | -0.0053491 | -0.078849 | -0.0062798 | -0.092568 |  | 69.6
ITSCA | ITSCA | 3532 | ITASCA | 3.817 |  |  |  | NORTH2001 | HILL | -0.0077071 | -0.096082 | -0.029418 | -0.36674 |  | 69.4
MYPTP | MYPTP | 3533 | FILESS T |  |  |  |  | NORTH2001 | MCLENNAN | -0.0081342 | -0.098328 | 0 | 0 |  | 69.4
GVGLF | GVGLF | 3534 | GRANDVGF | 2.057 |  |  |  | NORTH2001 | HILL | -0.0081342 | -0.098328 | -0.016732 | -0.20226 |  | 69.4
FLSSN | FLSSN | 3535 | FILESSIN | 2.1 |  |  |  | NORTH2001 | MCLENNAN | -0.0081342 | -0.098328 | -0.017082 | -0.20649 |  | 69.4
MYPRL | MYPRL | 3536 | MAYPEARL | 4.424 |  |  |  | NORTH2001 | ELLIS | -0.0081342 | -0.098328 | -0.035986 | -0.435 |  | 69.4
GVFTW | GVFTW | 3537 | GRANDV | 6.458 |  |  |  | NORTH2001 | JOHNSON | -0.0082947 | -0.099172 | -0.053567 | -0.64045 |  | 69.4
MYPTX | MYPTX | 3538 | TXCOPUMP | 1.123 |  |  |  | NORTH2001 | ELLIS | -0.0081342 | -0.098328 | -0.0091347 | -0.11042 |  | 69.4
MRTNS | MRTNS | 3543 | MERTENS | 5.703 |  |  |  | NORTH2001 | HILL | -0.0069369 | -0.092032 | -0.039561 | -0.52486 |  | 69.6
WHTNY | WHTNY | 3546 | WHITNYTU |  |  |  |  | NORTH2001 | BOSQUE | -0.0014752 | -0.073449 | 0 | 0 |  | 138
|  | 5925 | DC-EAST | 10 |  | 45.712 | 700 | NORTH2001 | TITUS | -0.016266 | -0.13349 | -11.5487 | -94.7778 |  | 345
NORTHBR | NORTHBR | 6006 | NBRADY2 |  |  |  |  | NORTH2001 | MCCULLOCH | 0.12347 | -0.069665 | 0 | 0 |  | 69
HEXT | HEXT | 6368 | HEXT 2 | 0.5 |  |  |  | NORTH2001 | MENARD | 0.11799 | -0.067984 | 0.058997 | -0.033992 |  | 69
BRDS | BRDS | 6378 | BRDYSE 2 | 4.078 |  |  |  | NORTH2001 | MCCULLOCH | 0.12111 | -0.069018 | 0.49387 | -0.28146 |  | 69
BRDS | BRDS | 6379 | BRDYSET2 |  |  |  |  | NORTH2001 | MCCULLOCH | 0.12111 | -0.069018 | 0 | 0 |  | 69
MCEC | MCEC | 6381 | BRADYRE2 | 4.77 |  |  |  | NORTH2001 | MCCULLOCH | 0.12164 | -0.069166 | 0.58025 | -0.32992 |  | 69
BRDY | BRDY | 6382 | BRADYTP2 |  |  |  |  | NORTH2001 | MCCULLOCH | 0.12535 | -0.070178 | 0 | 0 |  | 69
BRDY | BRDY | 6383 | BRADY 2 | 6.184 |  |  |  | NORTH2001 | MCCULLOCH | 0.12535 | -0.070178 | 0.77514 | -0.43398 |  | 69
SHLO | SHLO | 6398 | SHELONT2 |  |  |  |  | NORTH2001 | KIMBLE | 0.11542 | -0.067297 | 0 | 0 |  | 69
KMJC | KMJC | 6399 | KIMJNCR2 | 3.46 |  |  |  | NORTH2001 | KIMBLE | 0.12232 | -0.069137 | 0.42322 | -0.23922 |  | 69
JUNC | JUNC | 6400 | JUNCTON2 | 7.14 |  |  |  | NORTH2001 | KIMBLE | 0.12308 | -0.069341 | 0.8788 | -0.49509 |  | 69
PHME | PHME | 6401 | MENPHTP2 |  |  |  |  | NORTH2001 | KIMBLE | 0.12933 | -0.071008 | 0 | 0 |  | 69
PHME | PHME | 6402 | MENRDPH2 |  |  |  |  | NORTH2001 | KIMBLE | 0.12933 | -0.071008 | 0 | 0 |  | 69
SHLO | SHLO | 6403 | SHELLON2 | 0.639 |  |  |  | NORTH2001 | KIMBLE | 0.11542 | -0.067297 | 0.073753 | -0.043003 |  | 69
HAMILRGE | HAMILRGE | 6567 | RGECCAN2 |  |  |  |  | NORTH2001 | VAL VERDE | 0.13407 | -0.066459 | 0 | 0 |  | 69
|  | 6693 | RAILRD 2 | 21.89 |  |  |  | NORTH2001 | PARKER | 0.039737 | -0.11618 | 0.86984 | -2.5432 |  | 69
|  | 6694 | WFORD1G |  |  | 5 | 5 | NORTH2001 | PARKER | 0.039156 | -0.11538 | 0.19578 | -0.57688 |  | 12
LK_WTH | LK_WTH | 6695 | NTHTEXAS | 5.61 |  |  |  | NORTH2001 | PARKER | 0.040318 | -0.11699 | 0.22618 | -0.65631 |  | 69
N_WTH | N_WTH | 6696 | NTWTHFRD | 22.36 |  |  |  | NORTH2001 | PARKER | 0.04361 | -0.11679 | 0.97512 | -2.6113 |  | 138
WTH_LVOK | WTH_LVOK | 6697 | LIVEOAK | 13.13 |  |  |  | NORTH2001 | PARKER | 0.039156 | -0.11538 | 0.51412 | -1.5149 |  | 69
DNDAM | DNDAM | 6698 | DENISNDM |  |  | 76.1 | 80 | NORTH2001 | SCURRY | -0.015668 | -0.13176 | -1.2534 | -10.5412 |  | 12
DNDAM | DNDAM | 6699 | DENISNDM |  |  |  |  | NORTH2001 | SCURRY | -0.015668 | -0.13176 | 0 | 0 |  | 138
DIBLWT4 | DIBLWT4 | 6700 | DIBL WT4 | 2.113 |  |  |  | NORTH2001 | ANGELINA | -0.011754 | -0.11162 | -0.024836 | -0.23585 |  | 138
SFIELD | SFIELD | 6703 | SFIELD | 7.026 |  |  |  | NORTH2001 | CHEROKEE | -0.01188 | -0.11049 | -0.083466 | -0.77633 |  | 138
OWTNWT4 | OWTNWT4 | 6705 | OWTN WT4 | 2.776 |  |  |  | NORTH2001 | SMITH | -0.012778 | -0.11828 | -0.035473 | -0.32834 |  | 138
BSCMWT4 | BSCMWT4 | 6707 | BSCM WT4 | 4.474 |  |  |  | NORTH2001 | SMITH | -0.012498 | -0.11594 | -0.055915 | -0.51872 |  | 138
TSLVILLE | TSLVILLE | 6709 | TSLVILLE | 11.128 |  |  |  | NORTH2001 | SMITH | -0.011851 | -0.10556 | -0.13187 | -1.1747 |  | 138
SWTNWT4 | SWTNWT4 | 6710 | SWTN WT4 | 13.354 |  |  |  | NORTH2001 | SMITH | -0.012468 | -0.11569 | -0.16649 | -1.5449 |  | 138
CSNGWT4 | CSNGWT4 | 6717 | CSNG WT4 | 2.023 |  |  |  | NORTH2001 | NACOGDOCHE | -0.011777 | -0.11029 | -0.023824 | -0.22312 |  | 138
|  | 6719 | CGSE WT4 | 5.688 |  |  |  | NORTH2001 | NACOGDOCHE | -0.011798 | -0.11087 | -0.067106 | -0.63063 |  | 138
SHNEWT4 | SHNEWT4 | 6720 | SHNE WT4 | 1.281 |  |  |  | NORTH2001 | NACOGDOCHE | -0.011832 | -0.11182 | -0.015157 | -0.14324 |  | 138
OKRDWT4 | OKRDWT4 | 6722 | OKRD WT4 | 4.541 |  |  |  | NORTH2001 | NACOGDOCHE | -0.011853 | -0.11258 | -0.053826 | -0.5112 |  | 138
HGTNWT4 | HGTNWT4 | 6723 | HGTN WT4 | 3.766 |  |  |  | NORTH2001 | ANGELINA | -0.011793 | -0.11195 | -0.044411 | -0.4216 |  | 138
ZVLAWT4 | ZVLAWT4 | 6724 | ZVLA WT4 | 2.574 |  |  |  | NORTH2001 | ANGELINA | -0.011793 | -0.11195 | -0.030354 | -0.28816 |  | 138
LFKNWT4 | LFKNWT4 | 6726 | LFKN WT4 | 2.518 |  |  |  | NORTH2001 | ANGELINA | -0.011748 | -0.11156 | -0.02958 | -0.28091 |  | 138
BYLCWT4 | BYLCWT4 | 6727 | BYLC WT4 | 4.923 |  |  |  | NORTH2001 | NACOGDOCHE | -0.011753 | -0.11067 | -0.057859 | -0.54485 |  | 138
|  | 6742 | TROUPWT2 | 13.826 |  |  |  | NORTH2001 | CHEROKEE | -0.01213 | -0.11269 | -0.16771 | -1.558 |  | 69
SEGOVTP | SEGOVTP | 6774 | SEGOVTP9 |  |  |  |  | NORTH2001 | KIMBLE | 0.12217 | -0.069098 | 0 | 0 |  | 69
SHDGV_RC | SHDGV RC | 6800 | SHDGV RC | 6.263 |  |  |  | NORTH2001 | HOPKINS | -0.014919 | -0.13002 | -0.09344 | -0.81432 |  | 138
SHRLM_RC | SHRLM RC | 6802 | SHRLM RC | 5.724 |  |  |  | NORTH2001 | GRAYSON | -0.014056 | -0.13115 | -0.080459 | -0.75071 |  | 138
WHTBR_RC | WHTBR RC | 6804 | WHTBR RC | 6.363 |  |  |  | NORTH2001 | GRAYSON | -0.011009 | -0.13027 | -0.070047 | -0.82889 |  | 138
SHRWD_RC | SHRWD RC | 6806 | SHRWD RC | 4.086 |  |  |  | NORTH2001 | GRAYSON | -0.015457 | -0.13162 | -0.063156 | -0.53779 |  | 69
BGWEL_RC | BGWEL RC | 6808 | BGWEL RC | 4.984 |  |  |  | NORTH2001 | RED RIVER | -0.016237 | -0.13266 | -0.080927 | -0.66118 |  | 69
GORDVLRC | GORDVLRC | 6810 | GORDVLRC | 2.008 |  |  |  | NORTH2001 | GRAYSON | -0.015457 | -0.13162 | -0.031037 | -0.26429 |  | 69
PNKHL | PNKHL | 6811 | PNKHL | 7.422 |  |  |  | NORTH2001 | GRAYSON | -0.015768 | -0.13185 | -0.11703 | -0.97856 |  | 138
DENSE_RC | DENSE RC | 6812 | DENSE RC | 1.468 |  |  |  | NORTH2001 | GRAYSON | -0.015634 | -0.13174 | -0.022951 | -0.19339 |  | 138
CHERY_RC | CHERY RC | 6814 | CHERY RC | 51.903 |  |  |  | NORTH2001 | GRAYSON | -0.015837 | -0.1319 | -0.822 | -6.8461 |  | 138
EVANALRC | EVANALRC | 6818 | EVANALRC | 11.777 |  |  |  | NORTH2001 | GRAYSON | -0.016326 | -0.13163 | -0.19227 | -1.5502 |  | 138
SHR_S_RC | SHR S RC | 6820 | SHR S RC | 1.638 |  |  |  | NORTH2001 | GRAYSON | -0.01566 | -0.13156 | -0.025651 | -0.2155 |  | 138
VAN_ALRC | VAN ALRC | 6822 | VAN ALRC | 4.834 |  |  |  | NORTH2001 | GRAYSON | -0.016595 | -0.13165 | -0.08022 | -0.6364 |  | 138
RENOS_RC | RENOS RC | 6824 | RENOS RC | 10.358 |  |  |  | NORTH2001 | LAMAR | -0.016237 | -0.13266 | -0.16819 | -1.3741 |  | 138
ALHUB_RC | ALHUB RC | 6826 | ALHUB RC | 7.852 |  |  |  | NORTH2001 | COLLIN | -0.016263 | -0.1312 | -0.1277 | -1.0302 |  | 138
ECTOR_RC | ECTOR RC | 6830 | ECTOR RC | 8.8 |  |  |  | NORTH2001 | FANNIN | -0.01567 | -0.13187 | -0.1379 | -1.1605 |  | 69
MINTR_RC | MINTR RC | 6832 | MINTR RC | 1.498 |  |  |  | NORTH2001 | LAMAR | -0.016054 | -0.13253 | -0.024048 | -0.19853 |  | 138
CKVL_RC | CKVL RC | 6836 | CKVL RC | 1.509 |  |  |  | NORTH2001 | RED RIVER | -0.015822 | -0.13236 | -0.023875 | -0.19973 |  | 69
WINDM_RC | WINDM RC | 6838 | WINDM RC | 6.583 |  |  |  | NORTH2001 | FANNIN | -0.015697 | -0.13191 | -0.10333 | -0.86833 |  | 69
BRKSTNRC | BRKSTNRC | 6840 | BRKSTNRC | 8.241 |  |  |  | NORTH2001 | LAMAR | -0.016259 | -0.13261 | -0.13399 | -1.0928 |  | 138
COMON_RC | COMON RC | 6842 | COMON RC | 2.817 |  |  |  | NORTH2001 | HOPKINS | -0.015266 | -0.13195 | -0.043004 | -0.37172 |  | 138
COPHWYRC | COPHWYRC | 6844 | COPHWYRC | 3.297 |  |  |  | NORTH2001 | HOPKINS | -0.01531 | -0.13199 | -0.050476 | -0.43516 |  | 138
COOPR_RC | COOPR RC | 6846 | COOPR RC | 2.377 |  |  |  | NORTH2001 | DELTA | -0.015458 | -0.13267 | -0.036743 | -0.31535 |  | 69
BNHMLKRC | BNHMLKRC | 6848 | BNHMLKRC | 1.528 |  |  |  | NORTH2001 | FANNIN | -0.015776 | -0.13203 | -0.024105 | -0.20175 |  | 138
WLF_C_RC | WLF C RC | 6850 | WLF C RC | 2.358 |  |  |  | NORTH2001 | HUNT | -0.015604 | -0.13208 | -0.036794 | -0.31145 |  | 138
|  | 6851 | WYLIE4 | 5.065 |  |  |  | NORTH2001 | COLLIN | -0.015781 | -0.13454 | -0.079932 | -0.68145 |  | 138
SULBF_RC | SULBF RC | 6852 | SULBF RC | 3.196 |  |  |  | NORTH2001 | HOPKINS | -0.015527 | -0.13214 | -0.049625 | -0.42233 |  | 138
|  | 6853 | CLIMX4 | 3.868 |  |  |  | NORTH2001 | COLLIN | -0.016794 | -0.13167 | -0.064959 | -0.50929 |  | 138
COMM_RC | COMM RC | 6854 | COMM RC | 3.056 |  |  |  | NORTH2001 | HUNT | -0.015461 | -0.13215 | -0.047249 | -0.40384 |  | 138
CADML_RC | CADML RC | 6856 | CADML RC | 3.567 |  |  |  | NORTH2001 | HUNT | -0.01545 | -0.13388 | -0.055109 | -0.47757 |  | 69
SUNYP_RC | SUNYP RC | 6858 | SUNYP RC | 17.891 |  |  |  | NORTH2001 | HUNT | -0.015369 | -0.13204 | -0.27497 | -2.3624 |  | 69
KIOWA_RC | KIOWA RC | 6860 | KIOWA RC |  |  |  |  | NORTH2001 | RAINS | -0.015369 | -0.13204 | 0 | 0 |  | 69
PAR_E_RC | PAR E RC | 6862 | PAR E RC | 3.356 |  |  |  | NORTH2001 | LAMAR | -0.016249 | -0.13267 | -0.054533 | -0.44524 |  | 138
FORNY_RC | FORNY RC | 6866 | FORNY RC | 3.856 |  |  |  | NORTH2001 | KAUFMAN | -0.014395 | -0.13898 | -0.055506 | -0.5359 |  | 138
COPVL_RC | COPVL RC | 6868 | COPVL RC | 2.068 |  |  |  | NORTH2001 | ROCKWALL | -0.015443 | -0.13485 | -0.031936 | -0.27888 |  | 138
MCKIN_RC | MCKIN RC | 6870 | MCKIN2RC |  |  |  |  | NORTH2001 | COLLIN | -0.017386 | -0.13192 | 0 | 0 |  | 138
MCKSW_RC | MCKSW RC | 6874 | MCKSW RC | 0.2 |  |  |  | NORTH2001 | COLLIN | -0.017439 | -0.13203 | -0.0034878 | -0.026406 |  | 138
MCKIN_RC | MCKIN RC | 6876 | MCKIN1RC | 10.168 |  |  |  | NORTH2001 | COLLIN | -0.017378 | -0.13191 | -0.1767 | -1.3412 |  | 138
ALLEN_RC | ALLEN RC | 6878 | ALLEN RC | 3.496 |  |  |  | NORTH2001 | COLLIN | -0.017527 | -0.13221 | -0.061273 | -0.4622 |  | 138
LAVON_RC | LAVON RC | 6880 | LAVON RC | 4.516 |  |  |  | NORTH2001 | COLLIN | -0.015688 | -0.13463 | -0.070849 | -0.60798 |  | 138
|  | 6881 | WYLIE RC | 10.638 |  |  |  | NORTH2001 | COLLIN | -0.015657 | -0.13466 | -0.16656 | -1.4325 |  | 138
WIELD_RC | WIELD RC | 6882 | WIELD RC | 48.837 |  |  |  | NORTH2001 | ROCKWALL | -0.015204 | -0.13451 | -0.74253 | -6.5691 |  | 138
QUINL_RC | QUINL RC | 6884 | QUINL RC |  |  |  |  | NORTH2001 | ROCKWALL | -0.015204 | -0.13451 | 0 | 0 |  | 138
BLDSW_RC | BLDSW RC | 6886 | BLDSW RC |  |  |  |  | NORTH2001 | ROCKWALL | -0.015204 | -0.13451 | 0 | 0 |  | 138
WMUNS_RC | WMUNS RC | 6888 | WMUNS RC |  |  |  |  | NORTH2001 | ROCKWALL | -0.015204 | -0.13451 | 0 | 0 |  | 138
RHILL | RHILL | 6894 | ROSHILRC | 3.816 |  |  |  | NORTH2001 | KAUFMAN | -0.013842 | -0.13255 | -0.05282 | -0.50581 |  | 138
TRLSW | TRLSW | 6898 | TERRL RC | 4.006 |  |  |  | NORTH2001 | KAUFMAN | -0.014104 | -0.13293 | -0.056499 | -0.5325 |  | 138
CLMX_RC | CLMX RC | 6900 | KEMP RC | 7.921 |  |  |  | NORTH2001 | KAUFMAN | -0.012527 | -0.12212 | -0.09923 | -0.96728 |  | 138
TALTY_RC | TALTY RC | 6902 | TALTY RC |  |  |  |  | NORTH2001 | KAUFMAN | -0.013842 | -0.13255 | 0 | 0 |  | 138
COMBINRC | COMBINRC | 6904 | COMBINRC | 15.603 |  |  |  | NORTH2001 | KAUFMAN | -0.013842 | -0.13255 | -0.21597 | -2.0682 |  | 138
RAND_RC | RAND RC | 6906 | RAND RC | 8.231 |  |  |  | NORTH2001 | KAUFMAN | -0.013227 | -0.1291 | -0.10888 | -1.0627 |  | 138
SCURY_RC | SCURY RC | 6908 | SCURY RC | 14.564 |  |  |  | NORTH2001 | KAUFMAN | -0.013227 | -0.1291 | -0.19264 | -1.8803 |  | 138
|  | 6909 | ALNNRT R | 4.684 |  |  |  | NORTH2001 | COLLIN | -0.01749 | -0.13213 | -0.081925 | -0.61889 |  | 138
MSQT_RC | MSQT RC | 6910 | MSQT RC | 0.669 |  |  |  | NORTH2001 | DALLAS | -0.014184 | -0.13959 | -0.0094889 | -0.093383 |  | 138
IRNBR_RC | IRNBR RC | 6912 | IRNBR RC | 3.406 |  |  |  | NORTH2001 | HUNT | -0.013705 | -0.12225 | -0.046679 | -0.41639 |  | 138
EMORY_RC | EMORY RC | 6914 | EMORY RC | 10.069 |  |  |  | NORTH2001 | RAINS | -0.014125 | -0.12494 | -0.14222 | -1.258 |  | 138
EDGWD_RC | EDGWD RC | 6916 | EDGWD RC | 1.398 |  |  |  | NORTH2001 | VAN ZANDT | -0.013416 | -0.1204 | -0.018755 | -0.16832 |  | 138
BTSTR_RC | BTSTR RC | 6918 | BTSTR RC | 3.726 |  |  |  | NORTH2001 | VAN ZANDT | -0.013705 | -0.12225 | -0.051064 | -0.45551 |  | 69
DCKCV_RC | DCKCV RC | 6920 | DCKCV RC | 7.102 |  |  |  | NORTH2001 | KAUFMAN | -0.013705 | -0.12225 | -0.097332 | -0.86823 |  | 69
COBSW_RC | COBSW RC | 6922 | COBSW RC | 2.307 |  |  |  | NORTH2001 | VAN ZANDT | -0.013416 | -0.1204 | -0.03095 | -0.27777 |  | 69
POYNR_RC | POYNR RC | 6924 | POYNR RC | 1.019 |  |  |  | NORTH2001 | ANDERSON | -0.011317 | -0.10678 | -0.011532 | -0.10881 |  | 69
SEVPT_RC | SEVPT RC | 6926 | SEVPT RC | 9.06 |  |  |  | NORTH2001 | HENDERSON | -0.012108 | -0.11793 | -0.1097 | -1.0684 |  | 138
TOOL_RC | TOOL RC | 6928 | TOOL RC | 3.316 |  |  |  | NORTH2001 | NAVARRO | -0.011665 | -0.11351 | -0.038682 | -0.37639 |  | 138
WILOW_RC | WILOW RC | 6930 | WILOW RC | 4.045 |  |  |  | NORTH2001 | HENDERSON | -0.010718 | -0.098043 | -0.043352 | -0.39658 |  | 69
|  | 6932 | CRLSP RC | 3.046 |  |  |  | NORTH2001 | ANDERSON | -0.010473 | -0.090318 | -0.0319 | -0.27511 |  | 69
MNTLB_RC | MNTLB RC | 6934 | MNTLB RC | 4.675 |  |  |  | NORTH2001 | ANDERSON | -0.010228 | -0.08259 | -0.047816 | -0.38611 |  | 69
MALKF_RC | MALKF RC | 6938 | MALKF RC | 1.308 |  |  |  | NORTH2001 | HENDERSON | -0.011132 | -0.10594 | -0.014561 | -0.13857 |  | 138
NECHS_RC | NECHS RC | 6942 | NECHS RC | 0.29 |  |  |  | NORTH2001 | ANDERSON | -0.010625 | -0.085912 | -0.0030812 | -0.024915 |  | 138
HAMILRGE | HAMILRGE | 8681 | RGERCAN2 |  |  |  |  | NORTH2001 | VAL VERDE | 0.13407 | -0.066459 | 0 | 0 |  | 69
ETCCS | ETCCS | 12322 | TRACEN1G |  | 106 |  |  | NORTH2001 | ELLIS | -0.011482 | -0.11911 | -1.2171 | -12.6255 |  | 13.8
ETCCS | ETCCS | 12323 | TRACEN2G |  | 106 |  |  | NORTH2001 | ELLIS | -0.011482 | -0.11911 | -1.2171 | -12.6255 |  | 13.8
TGCCS | TGCCS | 13116 | GATEWY1G |  | 179 |  |  | NORTH2001 | RUSK | -0.012013 | -0.11484 | -2.1503 | -20.557 |  | 18
TGCCS | TGCCS | 13117 | GATEWY2G |  | 179 |  |  | NORTH2001 | RUSK | -0.012013 | -0.11484 | -2.1503 | -20.557 |  | 18
TGCCS | TGCCS | 13118 | GATEWY3G |  | 179 |  |  | NORTH2001 | RUSK | -0.012013 | -0.11484 | -2.1503 | -20.557 |  | 18
TGCCS | TGCCS | 13119 | GATEWY4G |  | 417 |  |  | NORTH2001 | RUSK | -0.012013 | -0.11484 | -5.0094 | -47.8899 |  | 18
LKPNT | LKPNT | 37010 | LAKEPNTE | 43.2 |  | 2 | 4 | NORTH2001 | DENTON | -0.016971 | -0.13156 | -0.80105 | -6.2098 |  | 138
LWVJS | LWVJS | 37030 | JONES ST | 42.2 |  |  |  | NORTH2001 | DENTON | -0.0171 | -0.13074 | -0.72162 | -5.5172 |  | 138
LWSVH | LWSVH | 37050 | HIGHL TN |  |  |  |  | NORTH2001 | DENTON | -0.017078 | -0.13062 | 0 | 0 |  | 138
LWSVW | LWSVW | 37060 | WEST TN | 66.309 |  |  |  | NORTH2001 | DENTON | -0.017053 | -0.13083 | -1.1307 | -8.6755 |  | 138
LWVTI | LWVTI | 37080 | LEWTI TN | 45.371 |  |  |  | NORTH2001 | DENTON | -0.016981 | -0.13145 | -0.77045 | -5.9639 |  | 138
LWSVS | LWSVS | 37100 | SOUTH TN | 57.508 |  |  |  | NORTH2001 | DENTON | -0.01695 | -0.13168 | -0.97477 | -7.5724 |  | 138
KRUGRVLE | KRUGRVLE | 37120 | KRUGRVLE | 18.2 |  |  |  | NORTH2001 | DENTON | -0.017097 | -0.12884 | -0.31117 | -2.345 |  | 138
|  | 37140 | BELLS |  |  |  |  | NORTH2001 | GRAYSON | -0.015582 | -0.13177 | 0 | 0 |  | 69
WHITEWRT | WHITEWRT | 37160 | WHITEWRT | 14 |  |  |  | NORTH2001 | GRAYSON | -0.015582 | -0.13177 | -0.21815 | -1.8447 |  | 69
FRNTRTAP | FRNTRTAP | 37180 | FRNTRTAP |  |  |  |  | NORTH2001 | FANNIN | -0.015582 | -0.13177 | 0 | 0 |  | 69
FRONTIER | FRONTIER | 37190 | FRONTIER | 1.5 |  |  |  | NORTH2001 | FANNIN | -0.015582 | -0.13177 | -0.023373 | -0.19765 |  | 69
TRENTON | TRENTON | 37200 | TRENTON | 1.1 |  |  |  | NORTH2001 | FANNIN | -0.015582 | -0.13177 | -0.01714 | -0.14494 |  | 69
LEONARD | LEONARD | 37220 | LEONARD | 7.6 |  |  |  | NORTH2001 | FANNIN | -0.015443 | -0.13486 | -0.11737 | -1.0249 |  | 69
SWINDELL | SWINDELL | 37230 | SWINDELL | 20 |  |  |  | NORTH2001 | HUNT | -0.015864 | -0.13442 | -0.31729 | -2.6883 |  | 138
BLUERDGE | BLUERDGE | 37240 | BLUERDGE | 2 |  |  |  | NORTH2001 | COLLIN | -0.015443 | -0.13486 | -0.030886 | -0.26971 |  | 69
LONGNECK | LONGNECK | 37250 | LONGNECK | 3 |  |  |  | NORTH2001 | COLLIN | -0.015443 | -0.13486 | -0.046329 | -0.40457 |  | 69
CLIMAX | CLIMAX | 37260 | CLIMAX | 10.5 |  |  |  | NORTH2001 | COLLIN | -0.015443 | -0.13486 | -0.16215 | -1.416 |  | 138
CLIMAX | CLIMAX | 37280 | CLIMAX |  |  |  |  | NORTH2001 | COLLIN | -0.015443 | -0.13486 | 0 | 0 |  | 69
FRMRSVLE | FRMRSVLE | 37290 | FRMRSVLE | 5.9 |  |  |  | NORTH2001 | COLLIN | -0.015443 | -0.13486 | -0.091114 | -0.79565 |  | 69
EMORYTN | EMORYTN | 37300 | EMORY | 5.5 |  |  |  | NORTH2001 | RAINS | -0.014125 | -0.12494 | -0.077685 | -0.68716 |  | 138
TALCOWST | TALCOWST | 37320 | TALCOWST | 5 |  |  |  | NORTH2001 | FRANKLIN | -0.015734 | -0.1323 | -0.078672 | -0.66148 |  | 138
DEPORT | DEPORT | 37340 | DEPORT | 7.1 |  |  |  | NORTH2001 | LAMAR | -0.016054 | -0.13253 | -0.11398 | -0.94094 |  | 138
RED_RIVR | RED RIVR | 37350 | RED RIVR | 6.7 |  |  |  | NORTH2001 | RED RIVER | -0.015822 | -0.13236 | -0.10601 | -0.8868 |  | 69
LONE_OAK | LONE OAK | 37360 | LONE OAK | 2.3 |  |  |  | NORTH2001 | RAINS | -0.015369 | -0.13204 | -0.035349 | -0.3037 |  | 69
SAINT_JO | SAINT JO | 37370 | SAINT JO | 2.4 |  |  |  | NORTH2001 | MONTAGUE | 0.038992 | -0.12436 | 0.093581 | -0.29847 |  | 69
NOCONATN | NOCONATN | 37380 | NOCONA | 11.8 |  |  |  | NORTH2001 | MONTAGUE | 0.038992 | -0.12436 | 0.46011 | -1.4675 |  | 69
LKWHITNY | LKWHITNY | 37410 | LKWHITNY |  |  |  |  | NORTH2001 | BOSQUE | -0.0014661 | -0.073447 | 0 | 0 |  | 138
LKWHITNY | LKWHITNY | 37420 | LKWHITNY | 4.9 |  |  |  | NORTH2001 | BOSQUE | -0.0010974 | -0.073362 | -0.0053773 | -0.35947 |  | 69
WHITNEY | WHITNEY | 37440 | WHITNEY | 10.5 |  |  |  | NORTH2001 | BOSQUE | -0.0010974 | -0.073362 | -0.011523 | -0.7703 |  | 69
OLSEN | OLSEN | 37460 | OLSEN |  |  |  |  | NORTH2001 | BOSQUE | -0.0011255 | -0.073368 | 0 | 0 |  | 138
OLSEN | OLSEN | 37470 | OLSEN |  |  |  |  | NORTH2001 | BOSQUE | -0.0004116 | -0.073203 | 0 | 0 |  | 69
HNDLYTAP | HNDLYTAP | 37490 | HNDLYTAP |  |  |  |  | NORTH2001 | BOSQUE | -0.0004116 | -0.073203 | 0 | 0 |  | 69
HANDLEY | HANDLEY | 37500 | HANDLEY | 5.9 |  |  |  | NORTH2001 | BOSQUE | -0.0004116 | -0.073203 | -0.0024284 | -0.4319 |  | 69
VLLYMILS | VLLYMILS | 37510 | VLLYMILS | 7.7 |  |  |  | NORTH2001 | BOSQUE | -0.0004116 | -0.073203 | -0.0031693 | -0.56366 |  | 69
SYCAMORE | SYCAMORE | 37520 | SYCAMORE | 0.1 |  |  |  | NORTH2001 | BOSQUE | 0.0013864 | -0.072787 | 0.00013864 | -0.0072787 |  | 69
CORYELCO | CORYELCO | 37530 | CORYELCO | 0.2 |  |  |  | NORTH2001 | CORYELL | 0.00153 | -0.072753 | 0.00030601 | -0.014551 |  | 69
GATESVL1 | GATESVL1 | 37550 | GATESVL1 | 0.2 |  |  |  | NORTH2001 | CORYELL | 0.00153 | -0.072753 | 0.00030601 | -0.014551 |  | 69
GATESVL2 | GATESVL2 | 37570 | GATESVL2 | 0.2 |  |  |  | NORTH2001 | CORYELL | 0.00153 | -0.072753 | 0.00030601 | -0.014551 |  | 69
JNESBORO | JNESBORO | 37590 | JNESBORO |  |  |  |  | NORTH2001 | HAMILTON | 0.0013452 | -0.072796 | 0 | 0 |  | 69
CLIFTON1 | CLIFTON1 | 37600 | CLIFTON1 | 7 |  |  |  | NORTH2001 | BOSQUE | -0.0004116 | -0.073203 | -0.0028812 | -0.51242 |  | 69
CLFTNTAP | CLFTNTAP | 37620 | CLFTNTAP |  |  |  |  | NORTH2001 | BOSQUE | -0.0004116 | -0.073203 | 0 | 0 |  | 69
CLIFTON2 | CLIFTON2 | 37630 | CLIFTON2 | 6.7 |  |  |  | NORTH2001 | BOSQUE | -0.0004116 | -0.073203 | -0.0027577 | -0.49046 |  | 69
MERDNTAP | MERDNTAP | 37650 | MERDNTAP |  |  |  |  | NORTH2001 | BOSQUE | 0.018933 | -0.088533 | 0 | 0 |  | 69
MERID_TN | MERID TN | 37660 | MERIDIAN | 7 |  |  |  | NORTH2001 | BOSQUE | 0.018933 | -0.088533 | 0.13253 | -0.61973 |  | 69
WALNTSPR | WALNTSPR | 37680 | WALNTSPR | 3.4 |  |  |  | NORTH2001 | BOSQUE | 0.018933 | -0.088533 | 0.064373 | -0.30101 |  | 69
GLENR_TN | GLENR TN | 37700 | GLENROSE | 20.3 |  |  |  | NORTH2001 | SOMERVELL | 0.018933 | -0.088533 | 0.38435 | -1.7972 |  | 69
HICOTAP | HICOTAP | 37740 | HICOTAP |  |  |  |  | NORTH2001 | BOSQUE | 0.018933 | -0.088533 | 0 | 0 |  | 69
HICOTN | HICOTN | 37750 | HICO | 3.7 |  |  |  | NORTH2001 | HICO | 0.018933 | -0.088533 | 0.070053 | -0.32757 |  | 69
HAMLTNCO | HAMLTNCO | 37770 | HAMLTNCO | 4.5 |  |  |  | NORTH2001 | HAMILTON | 0.018933 | -0.088533 | 0.0852 | -0.3984 |  | 69
HAMLTNTN | HAMLTNTN | 37790 | HAMILTON | 7.9 |  |  |  | NORTH2001 | HAMILTON | 0.018933 | -0.088533 | 0.14957 | -0.69941 |  | 69
HILL_CO | HILL CO | 37810 | HILL CO | 4.8 |  |  |  | NORTH2001 | HILL | -0.008187 | -0.10103 | -0.039298 | -0.48496 |  | 138

## SelfServeLoads
BusId | BName | 01SUM1 Pl | TSP's SelfServe Pl |  | effective Pl | GenOff_max | Pgen | effective Pgen | Pmax | effectuve Pmax | Cluster | County of Bus | 1430 GRAHAM 345kV to 1436 PARKER 345kV ckt 1 | 46020 LIMESTONE 345 kV to 2428 WATERMILL 345 kV ckt1 | Pinj*SHF1 | Pinj*SHF2 | SelfServe Load ID | Tsp
3347 | CHAMPION | 77.291 | 42 |  | 35.291 | [5 empty] | 3 | ANGELINA | -0.011773 | -0.11173 | -0.90996 | -8.6356 | 1 | Txu
3348 | CHAMPN G | [5 empty] | 42 | 0 | 42 | 0 | 3 | ANGELINA | -0.011773 | -0.11173 | -0.49447 | -4.6926 | 1 | Txu
3430 | SANDOW | 324.5 | 360 | *1 | 109.7574 | [5 empty] | 1 | MILAM | 0.0032939 | -0.040017 | 1.0689 | -12.9857 | 2 | Txu
3431 | SANDOW | 219.5 |  |  | 74.2426 |  | 360 | 0 | 360 | 0 | 1 | MILAM | 0.0032939 | -0.040017 | 1.9088 | -23.1901 | 2 | Txu
40260 | CHAMON | 96.2 | 59 |  | 37.2 | [5 empty] | 1 | HARRIS | -0.00092084 | 0.0029326 | -0.088585 | 0.28211 | 3 | HLP
48590 | CHM1 | [5 empty] | 59 | 0 | 65 | 6 | 1 | HARRIS | -0.00092084 | 0.0029326 | -0.059855 | 0.19062 | 3 | HLP
40270 | CHANEL | 33 | 29.6 |  | 3.4 | [5 empty] | 1 | HARRIS | -0.00063272 | 0.0020298 | -0.02088 | 0.066984 | 4 | HLP
48601 | CHN1 | [5 empty] | 14.8 | 1.9073e-07 | 15 | 0.2 | 1 | HARRIS | -0.00063272 | 0.0020298 | -0.0094908 | 0.030447 | 4 | HLP
48602 | CHN2 | [5 empty] | 14.8 | 1.9073e-07 | 15 | 0.2 | 1 | HARRIS | -0.00063272 | 0.0020298 | -0.0094908 | 0.030447 | 4 | HLP
40480 | DIABOX | 224.5 | 183.5 |  | 41 | [5 empty] | 1 | HARRIS | -0.00068749 | 0.002211 | -0.15434 | 0.49637 | 5 | HLP
48611 | DIB1 | [5 empty] | 68.033 | 0.00036913 | 74.93 | 13.7824 | 1 | HARRIS | -0.00068749 | 0.002211 | -0.051514 | 0.16567 | 5 | HLP
48612 | DIB2 | [5 empty] | 68.033 | 0.00036913 | 74.93 | 13.7824 | 1 | HARRIS | -0.00068749 | 0.002211 | -0.051514 | 0.16567 | 5 | HLP
48613 | DIB3 | [5 empty] | 47.435 | 0.00025737 | 75 | 13.7953 | 1 | HARRIS | -0.00068749 | 0.002211 | -0.051562 | 0.16583 | 5 | HLP
40510 | ENPROD | 28.3 | 5 |  | 23.3 | [5 empty] | 1 | CHAMBERS | -0.00079208 | 0.0025443 | -0.022416 | 0.072004 | 6 | HLP
48651 | EP1 | [5 empty] | 5 | 0 | 5 | 0 | 1 | CHAMBERS | -0.00079208 | 0.0025443 | -0.0039604 | 0.012722 | 6 | HLP
40570 | EXXON_ | 373.8 | 339.2 |  | 34.6 | [5 empty] | 1 | HARRIS | -0.00073298 | 0.0023563 | -0.27399 | 0.88078 | 7 | HLP
48660 | EXN7 | [5 empty] | 138.452 | -1.2456e-06 | 200 | 85.0559 | 1 | HARRIS | -0.00073298 | 0.0023563 | -0.1466 | 0.47126 | 7 | HLP
48661 | EXXON1 | [5 empty] | 100.374 | -9.0306e-07 | 195.1 | 82.972 | 1 | HARRIS | -0.00073298 | 0.0023563 | -0.143 | 0.45971 | 7 | HLP
48662 | EXXON2 | [5 empty] | 100.374 | -9.0306e-07 | 195.1 | 82.972 | 1 | HARRIS | -0.00073298 | 0.0023563 | -0.143 | 0.45971 | 7 | HLP
41250 | PHILIP | 67.3 | 64.1 |  | 3.2 | [5 empty] | 1 | HARRIS | -0.00067995 | 0.0021895 | -0.045761 | 0.14735 | 8 | HLP
48551 | CALGT | [5 empty] | 163.9 | 121.8592 | 163.9 | 121.8592 | 1 | HARRIS | -0.00067995 | 0.0021895 | -0.11144 | 0.35886 | 8 | HLP
48552 | CALST | [5 empty] | 86 | 63.9408 | 86 | 63.9408 | 1 | HARRIS | -0.00067995 | 0.0021895 | -0.058476 | 0.1883 | 8 | HLP
41300 | PSARCO | 58.1 | 58.1 |  | 0 | [5 empty] | 1 | HARRIS | -0.00087467 | 0.0028093 | -0.050818 | 0.16322 | 9 | HLP
48791 | PWR1 | [5 empty] | 56.6 | 48.3788 | 84.9 | 77.0329 | 1 | HARRIS | -0.00087467 | 0.0028093 | -0.07426 | 0.23851 | 9 | HLP
48792 | PWR2 | [5 empty] | 56.6 | 48.3788 | 84.9 | 77.0329 | 1 | HARRIS | -0.00087467 | 0.0028093 | -0.07426 | 0.23851 | 9 | HLP
48793 | PWR3 | [5 empty] | 56.6 | 48.3788 | 84.9 | 77.0329 | 1 | HARRIS | -0.00087467 | 0.0028093 | -0.07426 | 0.23851 | 9 | HLP
48794 | PWR4 | [5 empty] | 56.6 | 48.3788 | 84.9 | 77.0329 | 1 | HARRIS | -0.00087467 | 0.0028093 | -0.07426 | 0.23851 | 9 | HLP
48795 | PWR5 | [5 empty] | 56.6 | 48.3788 | 84.9 | 77.0329 | 1 | HARRIS | -0.00087467 | 0.0028093 | -0.07426 | 0.23851 | 9 | HLP
48796 | PWR6 | [5 empty] | 69 | 58.9777 | 130.5 | 118.4074 | 1 | HARRIS | -0.00087467 | 0.0028093 | -0.11414 | 0.36661 | 9 | HLP
48797 | PWR8 | [5 empty] | 48 | 41.028 | 72 | 65.3282 | 1 | HARRIS | -0.00087467 | 0.0028093 | -0.062976 | 0.20227 | 9 | HLP
41330 | QUANUM | 29 | 3.3 |  | 25.7 | [5 empty] | 1 | HARRIS | -0.00070667 | 0.0022794 | -0.020493 | 0.066104 | 10 | HLP
48810 | QNM1 | [5 empty] | 3.3 | -4.7684e-08 | 5 | 1.7 | 1 | HARRIS | -0.00070667 | 0.0022794 | -0.0035333 | 0.011397 | 10 | HLP
41450 | SHELL_ | 199.7 | 192.2 |  | 7.5 | [5 empty] | 1 | HARRIS | -0.00068972 | 0.0022224 | -0.13774 | 0.44382 | 11 | HLP
48820 | SHELL_ | [5 empty] | 80.007 | 3.4935e-06 | 88 | 24.8896 | 1 | HARRIS | -0.00068972 | 0.0022224 | -0.060695 | 0.19557 | 11 | HLP
48821 | SHELL_ | [5 empty] | 80.007 | 3.4935e-06 | 88 | 24.8896 | 1 | HARRIS | -0.00068972 | 0.0022224 | -0.060695 | 0.19557 | 11 | HLP
48822 | SHL_CPS | [5 empty] | 32.186 | 1.4054e-06 | 92 | 26.0209 | 1 | HARRIS | -0.00068972 | 0.0022224 | -0.063454 | 0.20446 | 11 | HLP
41460 | SIMSON | 31.5 | 14 |  | 17.5 | [5 empty] | 1 | HARRIS | #REF! | 12 |  |  | 12 | HLP
48831 | SIM1 | [5 empty] | 7 | 0 | 14 | 7 | 1 | HARRIS | -0.00062362 | 0.0020022 | -0.0087307 | 0.028031 | 12 | HLP
48832 | SIM2 | [5 empty] | 7 | 0 | 14 | 7 | 1 | HARRIS | -0.00062362 | 0.0020022 | -0.0087307 | 0.028031 | 12 | HLP
41560 | TEXPET | 26 | 24 |  | 2 | [5 empty] | 1 | HARRIS | -0.00063117 | 0.002025 | -0.01641 | 0.05265 | 13 | HLP
48761 | PET1 | [5 empty] | 24 | 0 | 35 | 11 | 1 | HARRIS | -0.00063117 | 0.002025 | -0.022091 | 0.070875 | 13 | HLP
41580 | TIDAL_ | 129.7 | 94.7 |  | 35 | [5 empty] | 1 | HARRIS | -0.00069098 | 0.002224 | -0.08962 | 0.28845 | 14 | HLP
48901 | TID1 | [5 empty] | 36.406 | -1.1732e-06 | 45 | 10.1394 | 1 | HARRIS | -0.00069098 | 0.002224 | -0.031094 | 0.10008 | 14 | HLP
48902 | TID2 | [5 empty] | 58.294 | -1.8786e-06 | 77.244 | 17.4046 | 1 | HARRIS | -0.00069098 | 0.002224 | -0.053374 | 0.17179 | 14 | HLP
42090 | AMKOE_ | 72.5 | 32.3 |  | 40.2 | [5 empty] | 1 | BRAZORIA | 0.00050641 | -0.0016389 | 0.036715 | -0.11882 | 15 | HLP
48510 | AMO1 | [5 empty] | 32.3 | -7.6294e-07 | 34 | 1.7 | 1 | BRAZORIA | 0.00050641 | -0.0016389 | 0.017218 | -0.055724 | 15 | HLP
42150 | BASF__ | 94.2 | 64.2 |  | 30 | [5 empty] | 1 | BRAZORIA | 0.0018937 | -0.0060621 | 0.17839 | -0.57105 | 16 | HLP
48520 | BASF1 |  |  |  |  | 10 | 64.2 | -3.0518e-06 | 81.6 | 17.4 | 1 | BRAZORIA | 0.0018937 | -0.0060621 | 0.17347 | -0.55528 | 16 | HLP
42230 | CAPTOL | 44.4 | 44.4 |  | 0 | [5 empty] | 1 | HARRIS | -0.00055864 | 0.0017912 | -0.024804 | 0.079531 | 17 | HLP
48561 | CAP1 | [5 empty] | 82.399 | 70.3802 | 103.6 | 91.5522 | 1 | HARRIS | -0.00055864 | 0.0017912 | -0.057875 | 0.18557 | 17 | HLP
48562 | CAP2 | [5 empty] | 82.504 | 70.4699 | 103.6 | 91.5522 | 1 | HARRIS | -0.00055864 | 0.0017912 | -0.057875 | 0.18557 | 17 | HLP
48563 | CAP3 | [5 empty] | 82.771 | 70.6979 | 103.6 | 91.5522 | 1 | HARRIS | -0.00055864 | 0.0017912 | -0.057875 | 0.18557 | 17 | HLP
48564 | CAP4 | [5 empty] | 45.54 | 38.8975 | 57 | 50.3714 | 1 | HARRIS | -0.00055864 | 0.0017912 | -0.031843 | 0.1021 | 17 | HLP
48565 | CAP5 | [5 empty] | 11.185 | 9.5535 | 14 | 12.3719 | 1 | HARRIS | -0.00055864 | 0.0017912 | -0.007821 | 0.025077 | 17 | HLP
42520 | DOW_B 8 | 464.3 | 464.3 |  | 0 | [5 empty] | 1 | BRAZORIA | 0.0023985 | -0.007713 | 1.1136 | -3.5812 | 18 | HLP
48622 | DOW2 | [5 empty] | 507.552 | 43.252 | 916.84 | 452.54 | 1 | BRAZORIA | 0.0023985 | -0.007713 | 2.1991 | -7.0716 | 18 | HLP
42525 | DOW_E 8 | 464.3 | 464.3 |  | 0 | [5 empty] | 1 | BRAZORIA | 0.0023985 | -0.007713 | 1.1136 | -3.5812 | 19 | HLP
48621 | DOW1 | [5 empty] | 743.048 | 278.748 | 986 | 521.7 | 1 | BRAZORIA | 0.0023985 | -0.007713 | 2.3649 | -7.605 | 19 | HLP
42940 | MONSAN | 74.2 | 8.8 |  | 65.4 | [5 empty] | 1 | BRAZORIA | 0.0006405 | -0.0020697 | 0.047525 | -0.15357 | 20 | HLP
48730 | MNSN1 | [5 empty] | 8.8 | 1.9073e-07 | 51 | 42.2 | 1 | BRAZORIA | 0.0006405 | -0.0020697 | 0.032665 | -0.10555 | 20 | HLP
40990 | LYCHEM | 115.8 | 53.7 |  | 62.1 | [5 empty] | 1 | HARRIS | #REF! | 21 |  |  | 21 | HLP
48815 | SHLDN 5 | [5 empty] | 152.5 | 98.8 | 152.5 | 98.8 | 1 | HARRIS | #REF! | 21 |  |  | 21 | HLP
*1 | 360 MW load among busses 3430 and 3431

## NO Network Model Names LF Buses
01SUM1CSC Buses without ESCA or Siemens names
Load Flow Base Case Bus Number | Load Flow Base Case Bus Name | Congestion Management Zone Location | County Location of Load Flow Bus | kV | Corresponding ESCA Network Model Name | Corresponding Siemens Network Model Name
5505 | RAYGEN1 | 1 | VICTORIA | 13 | RAYBURN
5506 | RAYGEN2 | 1 | VICTORIA | 13 | RAYBURN
3087 | TXCTY1CG | 1 | GALVESTON | 13.8 | TXCTY
3088 | TXCTY2CG | 1 | GALVESTON | 13.8 | TXCTY
3089 | TXCTY3CG | 1 | GALVESTON | 13.8 | TXCTY
3090 | TXCTY4CG | 1 | GALVESTON | 13.8 | TXCTY
40 | JEWETT | 1 | LEON | 138
144 | HARHHGTS | 1 | CORYEL | 138
164 | PATTON | 3 | MCLENNAN | 69
192 | TELICO | 3 | ELLIS | 138
197 | OAKGROV | 1 | FREESTONE | 138
240 | WHITNEY | 1 | BOSQUE | 345
241 | WHITNEY | 3 | BOSQUE | 138
300 | JOHNSVIL | 3 | ERATH | 138
310 | IVAN | 2 | STEPHENS | 69
322 | LIPAN | 3 | PALO PINTO | 138
340 | WSTWTHFD | 3 | PARKER | 138
375 | AIRLIQD | 3 | JOHNSON | 138
399 | CROWLEY | 3 | JOHNSON | 138
498 | LIVEOAK | 3 | PARKER | 69
561 | JOPLINSW | 3 | WISE | 69
605 | WZZRDWLS | 3 | JACK | 69
659 | BRIDGES | 3 | COLLIN | 138
682 | DENTON | 3 | DENTON | 138
695 | MUENSTER | 3 | COOKE | 138
704 | MTNSPRGS | 3 | COOKE | 69
710 | WHITSBRO | 3 | GRAYSON | 69
719 | WFEC 12G | 2 | WICHITA | 13.8
720 | WFEC 34G | 2 | WICHITA | 13.8
721 | WICHSUTH | 2 | WICHITA | 138
722 | JORDAN | 3 | GRAYSON | 69
850 | BTU380 | 3 | HOOD | 69
851 | BTU373 | 3 | HOOD | 69
852 | BTU3752 | 3 | BOSQUE | 69
853 | BTU3753 | 3 | CORYELL | 69
854 | BTU3755 | 3 | CORYELL | 69
855 | BTU3757 | 3 | CORYELL | 69
856 | BTU3783 | 2 | YOUNG | 69
893 | BRSSWTCH | 1 | BRAZOS | 138
918 | TEASLY C | 3 | DENTON | 138
983 | ARCO C | 3 | DENTON | 138
1097 | TWPP MTR | 2 | CULBERSON | 138
1158 | SLMSA LE | 2 | DAWSON | 69.6
1162 | LMESA LE | 2 | DAWSON | 138
1213 | PEMBRK T | 2 | UPTON | 69
1226 | MDGULF T | 2 | MIDLAND | 69
1247 | WINK BET | 1 | WINKLER | 69
1331 | U CARBID | 2 | HOWARD | 138
1343 | TRENTIPP | 2 | NOLAN | 138
1350 | NWPWR G1 | 2 | HOWARD | 13.8
1353 | NWPWR T | 2 | HOWARD | 69.6
1398 | RADIUM M | 2 | JONES | 138
1470 | NEWPRT M | 3 | ARCHER | 138
1487 | HEMMERD | 2 | WICHITA | 138
1548 | MONTAG M | 3 | MONTAGUE | 69
1552 | WIZRDPOD | 3 | WISE | 69
1573 | GRAFORPT | 3 | PALO PINTO | 69
1574 | PALOPNTO | 3 | PALO PINTO | 138
1576 | MINWLJCT | 3 | PALO PINTO | 138
1579 | ALEDO TU | 3 | PARKER | 69
1649 | HASSE M | 3 | COMANCHE | 138
1714 | SHRM TI2 | 3 | GRAYSON | 138
1753 | MEMC TE | 3 | GRAYSON | 138
1775 | PARISN T | 3 | LAMAR | 138
1804 | PARS P | 3 | LAMAR | 69
1825 | GREENVIL | 3 | HUNT | 69
1885 | EVER 1BT | 3 | TARRANT | 345
1886 | EV EAST | 3 | TARRANT | 345
1887 | EVER 2BT | 3 | TARRANT | 345
1916 | LIG2 T | 3 | DALLAS | 345
1923 | LIGAUTO1 | 3 | DALLAS | 138
1924 | LIGSOUTH | 3 | DALLAS | 138
1925 | LIGAUTO2 | 3 | DALLAS | 138
1970 | HIGHL ME | 3 | DENTON | 138
1990 | KRUM MBZ | 3 | DENTON | 138
1996 | HIT 1T | 3 | DALLAS | 138
1997 | HIT 2T | 3 | DALLAS | 138
1998 | HIT 1 | 3 | DALLAS | 138
1999 | HIT 2 | 3 | DALLAS | 138
2007 | IV VALV2 | 3 | DALLAS | 138
2014 | COPPEL T | 3 | DALLAS | 138
2019 | KIMBALL1 | 3 | TARRANT | 138
2025 | MCK T | 3 | TARRANT | 138
2029 | KELSOU M | 3 | TARRANT | 138
2030 | FMPOD TU | 3 | DENTON | 138
2040 | MEADPRK2 | 3 | TARRANT | 138
2282 | SQW CK M | 3 | SOMERVELL | 138
2283 | AIRLQD M | 3 | JOHNSON | 138
2316 | MG IND T | 3 | ELLIS | 138
2322 | BARDWELL | 3 | ELLIS | 69
2327 | TRUMBULL | 3 | ELLIS | 138
2351 | INDIA | 3 | ELLIS | 69
2367 | N LAKE T | 3 | DALLAS | 138
2369 | WHTOAKS | 3 | COLLIN | 138
2385 | N LAKE S | 3 | DALLAS | 138
2390 | IV VR1 | 3 | DALLAS | 138
2393 | IV VR2 | 3 | DALLAS | 138
2404 | NORWDTIE | 3 | DALLAS | 138
2405 | NORWDPLW | 3 | DALLAS | 138
2425 | DES PKVL | 3 | DALLAS | 138
2435 | WATMLLDB | 3 | DALLAS | 345
2474 | ROYSE T | 3 | ROCKWALL | 345
2517 | BRIDGESM | 3 | DENTON | 138
2526 | PL CUST2 | 3 | COLLIN | 138
2546 | MCKIN 2 | 3 | COLLIN | 138
2547 | MCKINSW2 | 3 | COLLIN | 138
2576 | ADD TAP1 | 3 | DALLAS | 138
2577 | ADD TAP2 | 3 | DALLAS | 138
2578 | CLT E E | 3 | DALLAS | 138
2595 | AIR LQ T | 3 | DALLAS | 138
2672 | TWN STAR | 3 | COLLIN | 138
2686 | RICHCOL | 3 | DALLAS | 138
2697 | NW WYL M | 3 | COLLIN | 138
2708 | CLIMAX M | 3 | COLLIN | 138
2716 | TER ARCO | 3 | KAUFMAN | 138
2717 | TERARC T | 3 | KAUFMAN | 138
2738 | OATES M | 3 | DALLAS | 138
2974 | INDUST W | 3 | DALLAS | 138
3092 | CGNR | 1 | GALVESTON | 138
3133 | RICHLND1 | 1 | FREESTONE | 345
3134 | RICHLND2 | 1 | FREESTONE | 345
3167 | ENTERP P | 3 | VAN ZANDT | 138
3184 | PRIMROSE | 3 | VAN ZANDT | 138
3321 | ZAVPMP T | 3 | ANGELINA | 138
3323 | ETOILE | 3 | NACOGDOCHES | 138
3348 | CHAMPN G | 3 | ANGELINA | 13.8
3466 | KERENS | 3 | NAVARRO | 69.6
3488 | WTXGFPOD | 3 | FREESTONE | 69.4
3493 | TEAGUE | 1 | FREESTONE | 69
3612 | TEMP SE | 1 | BELL | 138
3622 | KILLPK T | 1 | BELL | 138
3654 | RNDRK SE | 1 | WILLIAMSON | 138
3656 | RR SE NT | 1 | WILLIAMSON | 138
3657 | RR SE ST | 1 | WILLIAMSON | 138
3661 | SALTY M | 1 | MILAM | 138
3674 | ELGIN ET | 1 | WILLIAMSON | 138
3695 | METER CS | 1 | BRAZOS | 138
5255 | LAREDO | 1 | BEXAR | 138
5479 | AVR1-M | 1 | BEXAR | 345
5545 | USRSTEC1 | 1 | WHARTON | 69
5659 | USRSTEC2 | 1 | JIM WELLS | 69
5685 | WGWTAP9 | 1 | LIVE OAK | 69
5701 | USRSTEC3 | 1 | ATASCOSA | 69
5810 | BADER | 1 | MEDINA | 69
5859 | TURTLECK | 1 | ZAVALA | 69
5901 | MIGUEL 5 | 1 | ATASCOSA | 345
5903 | MIGUEL | 1 | ATASCOSA | 22.8
5925 | DC-EAST | 3 | TITUS | 345
6000 | SILVRTP1 | 2 | COKE | 69
6003 | BRNHRTP2 | 2 | IRION | 69
6004 | CCTPATL2 | 2 | COLEMAN | 69
6017 | ORNNWP1 | 2 | PECOS | 34.5
6018 | ORNNWP4 | 2 | PECOS | 138
6019 | ORNTP4 | 2 | PECOS | 138
6022 | TAP4 | 2 | PECOS | 138
6056 | VRNMNTP2 | 2 | WILBARGER | 69
6095 | OK1DUM | 2 | WILBARGER | 250
6117 | EMUNDY14 | 2 | KNOX | 138
6151 | GIRARDT2 | 2 | KENT | 69
6160 | PC1DUM | 2 | HASKELL | 100
6191 | EXSHRN4 | 2 | SCURRY | 138
6234 | AMCWDUM | 2 | JONES | 250
6245 | ABRBPRS2 | 2 | JONES | 69
6250 | DELK 2 | 2 | JONES | 69
6251 | ELY9 | 2 | TAYLOR | 69
6252 | SCOTT9 | 2 | TAYLO | 69
6329 | GLDBSK9 | 2 | COLEMAN | 69
6336 | MECSNYDR | 2 | SCURRY | 69
6349 | NOVICE9 | 2 | COLEMAN | 69
6350 | DRESSY9 | 2 | CALLAHAN | 69
6416 | GRAPETP2 | 2 | IRION | 69
6417 | STRLNG9 | 2 | STERLING | 69
6483 | SAPS2 4 | 2 | TOM GREEN | 138
6503 | ELDSHBL2 | 2 | SCHLEICHER | 69
6524 | MERTZON9 | 2 | MASON | 69
6568 | RGECBVIL | 1 | KINNEY | 138
6570 | RGEC-EPS | 1 | MAVERICK | 138
6587 | SCROSS2 | 2 | PECOS | 69
6600 | CRNAIR T | 2 | CRANE | 69
6602 | CRANTP1 | 2 | CRANE | 69
6603 | CRANTP2 | 2 | CRANE | 69
6605 | CRANAIR2 | 2 | CRANE | 69
6632 | WDWRDTP | 2 | PECOS | 138
6633 | WDWRD 4 | 2 | PECOS | 138
6634 | WDWRDU1 | 2 | PECOS | 34.5
6635 | TAP4 | 2 | CRANE | 138
6668 | RGECAPT2 | 2 | BREWSTER | 69
6693 | RAILRD 2 | 3 | PARKER | 69
6694 | WFORD1G | 3 | PARKER | 12
6719 | CGSE WT4 | 3 | NACOGDOCHE | 138
6742 | TROUPWT2 | 3 | CHEROKEE | 69
6772 | ABINOPK4 | 2 | JONES | 138
6780 | OK1TERT | 2 | WILBARGER | 13.2
6789 | AMCWTERT | 2 | JONES | 13.2
6851 | WYLIE4 | 3 | COLLIN | 138
6853 | CLIMX4 | 3 | COLLIN | 138
6881 | WYLIE RC | 3 | COLLIN | 138
6909 | ALNNRT R | 3 | COLLIN | 138
6932 | CRLSP RC | 3 | ANDERSON | 69
6935 | LKVEW RC | 1 | ANDERSON | 138
6937 | TCKER RC | 1 | ANDERSON | 138
7038 | TWPP G1 | 1 | CULBERSON | 34.5
7327 | ELGINT13 | 1 | BASTROP | 138
7332 | ELGIN 13 | 1 | WILLIAMSON | 138
7454 | TXI 13 | 1 | COMAL | 138
7477 | PALPEC13 | 1 | TRAVIS | 138
7534 | AVERYR13 | 1 | HAYS | 138
7545 | HW32BP06 | 1 | HAYS | 69
7706 | LOTT TSE | 1 | FALLS | 69.6
7712 | FAIRF SE | 1 | FALLS | 138
7714 | LOTT SE | 1 | FALLS | 69.6
7715 | SMARL SE | 1 | FREESTONE | 69.6
7719 | MEX1 SE | 1 | FREESTONE | 138
7720 | MEX2 SE | 1 | FALLS | 138
7732 | OVERT SE | 1 | FREESTONE | 69.6
7750 | NJAX SE | 1 | SMITH | 69.6
7751 | TXLA TSE | 1 | CHEROKEE | 69.6
7753 | CHIPM SE | 1 | CHEROKEE | 69.6
7756 | CLTAP SE | 1 | SMITH | 69.4
7757 | W.JAX SE | 1 | CHEROKEE | 69.4
7758 | FRANK SE | 1 | ANDERSON | 69.6
7763 | RNLDS SE | 1 | CHEROKEE | 69.4
7787 | BMNT TSE | 1 | CHEROKEE | 69.4
7788 | BMNT SE | 1 | CHEROKEE | 69.4
8062 | NBRE#1 | 1 | NUECES | 69
8063 | NBRE#2 | 1 | NUECES | 69
8064 | NBRE#3 | 1 | NUECES | 69
8147 | UCAR #2 | 1 | CALHOUN | 13.8
8148 | UCAR #1 | 1 | CALHOUN | 13.8
8199 | LULNG M4 | 1 | CALDWELL | 69
8341 | ED1TERT | 1 | HIDALGO | 13.8
8356 | HIDGOB 4 | 1 | HIDALGO | 138
8391 | SHLND 4 | 1 | HIDALGO | 138
8431 | LVEOAK2 | 1 | ARANAS | 69
8506 | VAL #1 | 1 | DUVAL | 13.8
8507 | VAL #2 | 1 | DUVAL | 13.8
8511 | STARCO#1 | 1 | NUECES | 13.8
8545 | BC-TP 2 | 1 | MATAGORDA | 69
8651 | UNIVMEC | 1 | WEBB | 138
8755 | MVGANDY4 | 1 | HIDALGO | 138
8790 | MV.RAYTP | 1 | WILLACY | 138
8821 | TAYLOR | 1 | HILDAGO | 138
8904 | CFLD2TP2 | 1 | BEE | 69
8924 | BBGRVEL | 1 | COLORADO | 69
8930 | ICPGN#1 | 1 | NUECES | 18
8931 | ICPGN#2 | 1 | NUECES | 18
8932 | ICPGN#3 | 1 | NUECES | 18
8933 | FGNTS001 | 1 | HIDALGO | 18
8934 | FGNTS101 | 1 | HIDALGO | 18
8935 | FGNTS201 | 1 | HIDALGO | 18
8936 | CALGN#1 | 1 | HIDALGO | 16
8937 | CALGN#2 | 1 | HIDALGO | 16
8938 | CALGN#3 | 1 | HIDALGO | 16
8957 | MECLOPN4 | 1 | STARR | 138
8958 | MECBRUTP | 1 | WEBB | 138
8959 | AIRLIQ2 | 1 | NUECES | 69
8963 | HIDGO 4 | 1 | HIDALGO | 138
8968 | ICP | 1 | SAN PATRICIO | 138
8969 | CALGN#1 | 1 | HIDALGO | 138
8970 | CALGN#2 | 1 | HIDALGO | 138
8971 | CALGN#3 | 1 | HIDALGO | 138
8978 | AIRLQT 2 | 1 | NUECES | 138
8979 | AIRLQ 2 | 1 | NUECES | 138
8984 | MARKHMTP | 1 | MATAGORDA | 69
8985 | YGNACIO | 1 | ZAPATA | 138
8988 | WPT2DUM | 1 | SAN PATRICIO | 100
8989 | WPT2TERT | 1 | SAN PATRICIO | 13.8
8997 | FRTTS001 | 1 | HIDALGO | 138
8998 | FRTTS101 | 1 | HIDALGO | 138
8999 | FRTTS201 | 1 | HIDALGO | 138
9040 | AUSTROP | 1 | TRAVIS | 345
9164 | METCENTR | 1 | TRAVIS | 138
9244 | FIESTA | 1 | TRAVIS | 69
13131 | CALFRE1G | 1 | FREESTONE | 18
13132 | CALFRE2G | 1 | FREESTONE | 18
13133 | CALFRE3G | 1 | FREESTONE | 18
13134 | CALFRE4G | 1 | FREESTONE | 18
13135 | CALFRE5G | 1 | FREESTONE | 18
13136 | CALFRE6G | 1 | FREESTONE | 18
37140 | BELLS | 3 | GRAYSON | 69
38330 | WDWRDTAP | 2 | PECOS | 138
38331 | WDWRD4 | 2 | PECOS | 138
38332 | WDWRDU2 | 2 | PECOS | 34.5
38340 | AIRPORT | 2 | PECOS | 69
38420 | SWTECTNP | 2 | PECOS | 69
38470 | TNPGOMZ2 | 2 | PECOS | 69
38490 | TNPBEL2 | 2 | PECOS | 69
38990 | SEMINOLE | 1 | GALVESTON | 138
40111 | OPNAPD 8 | 1 | HARRIS | 138
40255 | CHAMBR 5 | 1 | CHAMBERS | 345
40425 | OPNDAY 8 | 1 | HARRIS | 138
40815 | CUST_3 | 1 | HARRIS | 138
40970 | LPEENY | 1 | HARRIS | 138
41165 | NOBEL 8 | 1 | HARRIS | 138
41430 | SHELDN 5 | 1 | HARRIS | 345
41530 | TAYLOR8 | 1 | HARRIS | 138
42520 | DOW_B 8 | 1 | BRAZORIA | 138
42525 | DOW_E 8 | 1 | BRAZORIA | 138
42705 | CUST_4 8 | 1 | HARRIS | 138
42835 | JONES 8 | 1 | BRAZORIA | 138
42951 | TERM_A 8 | 1 | GALVESTON | 138
42952 | OPN@T_A8 | 1 | GALVESTON | 138
42953 | TERM_B 8 | 1 | GALVESTON | 138
43225 | SEPTON 8 | 1 | HARRIS | 138
43355 | TIKIIS 8 | 1 | GALVESTON | 138
44651 | SIENNA 8 | 1 | FORT BEND | 138
44652 | SIENNA 8 | 1 | FORT BEND | 138
45971 | KUYDAL 5 | 1 | HARRIS | 345
45972 | KUYDAL 5 | 1 | HARRIS | 345
46070 | MINMAX 8 | 1 | HARRIS | 138
47515 | AUSTIN 8 | 1 | HARRIS | 138
47601 | E_SIDE 8 | 1 | HARRIS | 138
47602 | E_SIDE 8 | 1 | HARRIS | 138
48511 | APRO1 | 1 | HARRIS | 13.8
48512 | APRO2 | 1 | HARRIS | 13.8
48513 | APRO3 | 1 | HARRIS | 13.8
48514 | APRO4 | 1 | HARRIS | 13.8
48815 | SHLDN 5 | 1 | HARRIS | 16