## Summary with Notes&Assumptions
ENA TECHNICAL SERVICES
PROJECT COST ESTIMATE
2025-09-26
| CUSTOMER COMPANY NAME: | Enron North America (Houston Pipe Line Co.)
| PROJECT NAME: | Temporary Meter & Regulator Station for Midcon's Carbon Black Delivery
| W.O. NUMBER: | Not Assigned
| PROJECT ENGINEER: | Rodney Rogers |  | FILE NAME: | CostEstimateCarbonBlack.xls
REVISION NUMBER:
| PLANNER / MARKETER: | Ginger Causey/Mike Morris
Summary Page
Estimate with
|  | Estimate | Contingencies | Contingencies
| Material and Equipment Cost | 20005.1987 | 563.75 | 20568.9487
| Field Direct Costs | 8740 | 0 | 8740
| Project Support Costs | 2175 | 250 | 2425
| Other (Overhead, AFUDC, & As-Builts) | 4908.8204 | 129.1891 | 5038.0095
| Total | 35829.0191 | 942.9391 | 36771.9582
Notes and Assumption
1. A surface site will not be required. Plan to install temporary facilities on existing Clark Refinery Meter Station Site. (N)
2. Ingress and egress for construction activities can be obtained from Clark Refinery at no costs. (A)
3. Job duration is estimated at 4 Days (mobilization to clean-up), weather permitting. (N)
4. Cost est. is + or - 10%. (N)
5. Cost est. is based on HMS completing calibration of pressure and temperature recorders and tubing and adjustment of regulators. (N)
6. A fence is not required. (N)
7. Cost est. is based on starting construction activities on March 15, 2000 and completing construction activities on or before March 31, 2000. (N)
8. Project will be release by Marketing in a timely manner to allow materials to be obtained without expediting or hot shot services. (A)
9. Since no digging will be required, no environmental costs are included in the cost estimate. (N)
10. Cost estimate does include moneys for overpressure protection. (N)
11. Per Midcon, redundant parallel regulator runs will not be required. (N)
12. Cost est. does not include moneys for extensive safety requirements by Clark Refinery or Midcon. Clark Refinery will require all workers to
attend a one day safety training class. (N)
13. COST EST. DOES NOT INCLUDE MONEYS FOR INCOME TAX GROSS-UP. IF INCOME TAX GROSS-UP IS REQUIRED, DEAL MAKER SHALL DETERMINE
AND PROVIDE INCOME TAX GROSS-UP PERCENTAGE PRIOR TO SUBMITTING WORK ORDER AUTHORIZATION. (N)
14. Per Facility Planning, the minimum pressure and maximum flow at the proposed meter station will be 550 psig and 5 MMCF/Day. (N)
15. Per Midcon, the feed to the Carbon Black Station is steady (i.e no swings). (N)
16. Cost est. is based on the proposed meter and regulator station being in-service for approximately 3 to 4 weeks. (N)
17. Cost est. is based on the proposed meter & regulator station being installed and ready for service on April 1, 2000. (N)
18. Project will be constructed using hand sketches due to facilities being temporary (i.e. no detailed cad drawings will be prepared). (N)
19. Cost est. does not include any moneys for rock. All of the proposed facilities will be above grade. (N)
20. Cost est. is based utilizing the Special Project Team to perform and manage the physical construction activities. (N)
21. Cost est. is valid for 120 days. (N)
(A) - Assumption
(N) - Note

## Project Scope
ENA TECHNICAL SERVICES
PROJECT COST ESTIMATE
2025-09-26
| CUSTOMER COMPANY NAME: | Enron North America (Houston Pipe Line Co.)
| PROJECT NAME: | Temporary Meter & Regulator Station for Midcon's Carbon Black Delivery
| W.O. NUMBER: | Not Assigned
| PROJECT ENGINEER: | Rodney Rogers | FILE NAME: | CostEstimateCarbonBlack.xls
REVISION NUMBER:
| PLANNER/MARKETER: | Ginger Causey/Mike Morris
PROJECT SCOPE
SCOPE:
This project consists of installing a meter and regulator station at the existing HPL Port Arthur Field-Clark Refinery (3037) Sales Station for
temporary feed to Midcon's Carbon Black Station. The temporary meter and regulator station will be installed on Clark Refinery Plant Property
in Jefferson County, Texas. For the project location, see valve location maps VLM-54 & 54A and station drawings HC-3037-25-H &
HC-3037-26-H.
The proposed meter and regulator station will be connected to HPL's piping via an existing 4" 600# Nordstrom Plug Valve. The proposed
station will be designed and estimated to the following parameters:
Flow Rate: 5 MMCF/Day Maximum & 3 MMCF/Day Minimum (Note: Per Midcon, flow rate will be steady constant load.)
Pressure: 550 psig= HPL's Normal Station Pressure, 340 psig= Midcon's MAOP
Specific Gravity: 0.610
CO2 Mole Percent: 1.400
N2 Mole Percent: .950
Pressure Base: 14.65 psia
Temperature Base: 60 Deg F
Sales Description: Custody Tranfer
Flow Measurement: Orifice Meter with Barton Chart Recorder
Flow Direction: From HPL's 8" (3037) Port Arthur Line to Midcon
Redundant Service: Per Midcon, a redundant regulation will not be required.
Overpressure Protection: Yes (i.e. Monitor Regulator)
Gas Conditions: Pipeline Quality Gas
Reimbursable: 100% Reimbursable by Midcon
The proposed meter station will consist of one (1) 3" skid mounted senior orifice meter run and a single 2" regulator run with a 2" by-pass line.
The proposed regulator run will consist of one (1) 2" primary regulator and one (1) 2" monitor regulator. The primary regulator will reduce HPL's
pressure from 550 psig to 300 psig. Midcon's MAOP is 340 psig. The monitor regulator will function as overpressure protection.
The regulator run will be located just downstream of the proposed orifice meter run. Midcon will be responsible for installing the
proposed 3" pipeline from the proposed meter & regulator station to their connecting piping. The length of the proposed pipeline will be
approximately 300 feet. Per Midcon, they plan to install the temporary 3" pipeline on Clark Refinery's existing pipe rack in the near vicinity
of the project location.
The proposed meter and regulator station and related piping will be temporary (i.e. approximately 3 to 4 weeks).

## Notes (hidden)
ENA TECHNICAL SERVICES
PROJECT COST ESTIMATE
2025-09-26
| CUSTOMER COMPANY NAME: | Houston Pipe Line
PROJECT NAME:
W.O. NUMBER:
PROJECT ENGINEER:
REVISION NUMBER:
PLANNER / MARKETER:
NOTES AND ASSUMPTIONS
(A) - Assumption
(N) - Note

## M&E Costs
ENA TECHNICAL SERVICES
PROJECT COST ESTIMATE ANALYSIS
2025-09-26
| CUSTOMER COMPANY NAME: | Enron North America (Houston Pipe Line Co.)
| PROJECT NAME: | Temporary Meter & Regulator Station for Midcon's Carbon Black Delivery
| W.O. NUMBER: | Not Assigned
| PROJECT ENGINEER: | Rodney Rogers | FILE NAME: | CostEstimateCarbonBlack.xls
REVISION NUMBER:
| PLANNER / MARKETER: | Ginger Causey/Mike Morris
MATERIAL AND EQUIPMENT COSTS
[6 empty] | W.O.A. | W.O.A. | W.O.A.
|  |  | Est. | Est. | W.O.A. | COST | CONTINGENCY | CONTINGENCY
|  |  | Quantity | Unit | Unit Cost | ESTIMATE | ESTIMATE | EXPLANATION
(2/24/2000)
MATERIAL AND EQUIPMENT
Meter, Orifice, 3", 600#, RFFE, 0.216" W.T., Gr. B, Skid Mounted, |  |  | 1 | Ea. | 7699 | 7699
c/w 2- 3" 600# Ball Valves, 1-3" Check Valve, 2 Thermowells,
& a 200" Range Spring
Barton Chart Recorder, 202E, 0-200", 2 Pin |  |  | 1 | Ea. | 465 | 465
Meter House, Park Line, To enclose Press. & Temp. Rec.'s |  |  | 1 | Ea. | 100 | 100
Leveling Stands |  |  | 2 | Ea. | 35 | 70
5 Valve Manifold |  |  | 1 | Ea. | 133 | 133
Temperature Recorder |  |  | 1 | Ea. | 350 | 350
Pipe Stands, 2" x 18" & 2" x 24" |  |  | 2 | Ea. | 5 | 10
Regulator, Mooney, 2", 600#, Large Single Port, FG-31, |  |  | 2 | Ea. | 1533 | 3066
100% Capacity, c/w Grove 829S Pilot
Valve, 3", Ball, 600#, RFFE, Wrench Oper. |  |  | 2 | Ea. | 1100 | 2200
Valve, 2", Ball, 600#, RFFE, Wrench Oper. |  |  | 1 | Ea. | 765 | 765
Filter, Welker F-4 w/ by-pass & valve manifold |  |  | 2 | Ea. | 581 | 1162
Flanges, 4", 600#, R.F., Gr. B, XHvy |  |  | 1 | Ea. | 26.29 | 26.29
Gaskets for 4" Flanges, 600#, Spiral Wound |  |  | 2 | Ea. | 2.28 | 4.56
Stud Bolts, for 4", 600# Flanges, (8 per Set) |  |  | 8 | Ea. | 2 | 16
Flanges, 3", 600#, R.F., Gr. B, XHvy |  |  | 7 | Ea. | 16.95 | 118.65
Gaskets for 3" Flanges, 600#, Spiral Wound |  |  | 12 | Ea. | 1.62 | 19.44
Stud Bolts, for 3", 600# Flanges, (8 per Set) |  |  | 48 | Ea. | 1.29 | 61.92
Gaskets for 3" Flanges, 600#, Insulating |  |  | 1 | Ea. | 13.03 | 13.03
Stud Bolts, for 3", 600# Flanges, (8 per Set) |  |  | 8 | Ea. | 1.29 | 10.32
Flanges, 2", 600#, R.F., Gr. B, XHvy |  |  | 2 | Ea. | 10.23 | 20.46
Gaskets for 2" Flanges, 600#, Spiral Wound |  |  | 3 | Ea. | 1.24 | 3.72
Stud Bolts, for 2", 600# Flanges, (8 per Set) |  |  | 8 | Ea. | 0.83 | 6.64
Blind Flange, 4", 600#, RF |  |  | 1 | Ea. | 24.86 | 24.86
Blind Flange, 3", 600#, RF |  |  | 1 | Ea. | 14.12 | 14.12
Nipple, 1", 3", XHvy, NPT |  |  | 1 | Ea. | 2.01 | 2.01
Valve, 1", 3000#, Female, Screwed |  |  | 1 | Ea. | 73.8 | 73.8
Plug, 1", XHvy, Hex, Screwed |  |  | 2 | Ea. | 1.36 | 2.72
Plug, 3/4", XHvy, Hex, Screwed |  |  | 3 | Ea. | 0.54 | 1.62
Nipple, 1/2", 3", XHvy, NPT |  |  | 7 | Ea. | 0.5 | 3.5
Valve, 1/2", 3000#, Female, Screwed |  |  | 7 | Ea. | 45.67 | 319.69
Plug, 1/2", XHvy, Hex, Screwed |  |  | 7 | Ea. | 0.34 | 2.38
Tee, 3"x 2", 0.300" x 0.218" W.T., Gr. B |  |  | 2 | Ea. | 16.07 | 32.14
Ell, 3", 0.300" W.T., Gr. B, 90 Deg., LR |  |  | 3 | Ea. | 6.63 | 19.89
Ell, 2", 0.218" W.T., Gr. B, 90 Deg., LR |  |  | 2 | Ea. | 3.67 | 7.34
Reducer, 4"x3", 0.337"x 0.300" W.T., Gr. B, Conc. |  |  | 1 | Ea. | 6.63 | 6.63
Reducer, 3"x2", 0.300"x 0.218" W.T., Gr. B, Conc. |  |  | 2 | Ea. | 5.22 | 10.44
Pipe, 3.5"O.D., 0.300" W.T., Gr. B, Bare |  |  | 20 | Ft. | 5.06 | 101.2 | 0
Pipe, 2.375"O.D., 0.218" W.T., Gr. B, Bare |  |  | 20 | Ft. | 2.48 | 49.6 | 0
Misc. Materials |  |  | 1 | Lot | 750 | 750 | 500 | Additional unplanned misc. materials.
FREIGHT (4.50% of materials) | [5 empty] | 798.4336 | 22.5
TAX (8.25% of materials) | [5 empty] | 1463.795 | 41.25
MATL. & EQUIP. SUB-TOTAL | [5 empty] | 20005.1987 | 563.75
CONTINGENCIES | [5 empty] | 563.75
MATL. & EQUIP. SUB-TOTAL WITH CONTINGENCIES | [5 empty] | 20568.9487

## FD Costs
ENA TECHNICAL SERVICES
PROJECT COST ESTIMATE ANALYSIS
2025-09-26
| CUSTOMER COMPANY NAME: | Enron North America (Houston Pipe Line Co.)
| PROJECT NAME: | Temporary Meter & Regulator Station for Midcon's Carbon Black Delivery
| W.O. NUMBER: | Not Assigned
| PROJECT ENGINEER: | Rodney Rogers | FILE NAME: | CostEstimateCarbonBlack.xls
REVISION NUMBER:
| PLANNER / MARKETER: | Ginger Causey/Mike Morris
FIELD DIRECT COSTS
[6 empty] | W.O.A. | W.O.A. | W.O.A.
|  |  | Est. | Est. | W.O.A. | COST | CONTINGENCY | CONTINGENCY
|  |  | Quantity | Unit | Unit Cost | ESTIMATE | ESTIMATE | EXPLANATION
(2/28/2000)
CONSTRUCTION SUPPORT:
| SURVEY (Preliminary and As-Built) |  | 0 | Days | 720 | 0 | 0
FIELD INSPECTION :
|  | - Construction - 1 Chief Insp. | 0 | Days | 330 | 0 | 0
|  | - Construction - 1 Craft Insp. | 0 | Days | 295 | 0 | 0
|  | - Construction - QA Insp. | 0 | Days | 0 | 0 | 0
|  | - Contruction Management | 1 | Days | 480 | 480 | 0
| X-Ray |  | 1 | Day | 800 | 800 | 0
|  | CONSTRUCTION SUPPORT SUB TOTAL |  |  |  | 1280 | 0
CONTRACT INSTALLATION:
Special Project Team (Labor & Equipment) |  |  | 1 | Lp Sum | 6000 | 6000 | 0
Contract Labor & Equipment |  |  | 1 | Lp Sum | 500 | 500 | 0
Special Project Team |  |  | 4 | Days | 240 | 960 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
|  | CONTRACT INSTALLATION SUB TOTAL |  |  |  | 7460 | 0
FIELD DIRECT SUB TOTAL | [5 empty] | 8740 | 0
CONTINGENCIES | [5 empty] | 0
FIELD DIRECT SUB TOTAL WITH CONTINGENCIES | [5 empty] | 8740
TOTAL INSTALLED COST (Labor + Material) | [5 empty] | 28745.1987
CONTINGENCIES | [5 empty] | 563.75
TOTAL INSTALLED COST (Labor + Material) WITH CONTINGENCIES | [5 empty] | 29308.9487

## PS Costs
.
ENA TECHNICAL SERVICES
PROJECT COST ESTIMATE ANALYSIS
2025-09-26
| CUSTOMER COMPANY NAME: | Enron North America (Houston Pipe Line Co.)
| PROJECT NAME: | Temporary Meter & Regulator Station for Midcon's Carbon Black Delivery
| W.O. NUMBER: | Not Assigned
| PROJECT ENGINEER: | Rodney Rogers | FILE NAME: | CostEstimateCarbonBlack.xls
REVISION NUMBER:
| PLANNER / MARKETER: | Ginger Causey/Mike Morris
PROJECT SUPPORT COSTS
[6 empty] | W.O.A. | W.O.A. | W.O.A.
|  |  | Est. | Est. | W.O.A. | COST | CONTINGENCY | CONTINGENCY
|  |  | Quantity | Unit | Unit Cost | ESTIMATE | ESTIMATE | EXPLANATION
(2/28/2000)
ENVIRONMENTAL
| Permit Acquisition |  | 0 | Lot | 0 | 0 | 0
|  | ENVIRONMENTAL SUB TOTAL |  |  |  | 0 | 0
RIGHT OF WAY
| ROW Direct Salaries |  | 0 | Lot | 0 | 0 | 0
| ROW Damages |  | 0 | Lot | 0 | 0 | 0
| ROW Outside Services |  | 0 | Lot | 0 | 0 | 0
|  | RIGHT OF WAY SUB TOTAL |  |  |  | 0 | 0
DISTRICT LABOR
| DLAB |  | 0 | Lp Sum | 0 | 0 | 0
|  | DISTRICT LABOR SUB TOTAL |  |  |  | 0 | 0
ENGINEERING
| ENGINEERING - COMPANY |  | 1 | Lp Sum | 1500 | 1500 | 0
ENGINEERING - CONTRACT
|  | Drafting, Reprographics, Copying, etc. | 0 | Lp Sum | 0 | 0 | 0
|  | HMS Support | 1 | Lp Sum | 675 | 675 | 250
|  | ENGINEERING SUB TOTAL |  |  |  | 2175 | 250
GAS LOSS (Blowdown & Purge)
| Gas Blowdown and Purge |  | 0 | Ft3 | 2.5 | 0 | 0
|  | GAS LOSS SUB TOTAL |  |  |  | 0 | 0
PROJECT SUPPORT SUB TOTAL BEFORE "OTHER"CATEGORIES | [5 empty] | 2175 | 250
ENTIRE PROJECT SUB TOTAL WITHOUT "OTHER" CATEGORIES | [5 empty] | 30920.1987 | 813.75
OTHER
As-Built Package (2.0%) | [5 empty] | 618.404 | 16.275
AFUDC (6.5% per year, for 30 days) | [5 empty] | 168.4939 | 4.4344
Overhead (12.0% HPL & 1.0% NNG) | [5 empty] | 4121.9226 | 108.4797
|  | OTHER SUB TOTAL |  |  |  | 4908.8204 | 129.1891
PROJECT SUPPORT SUB TOTAL | [5 empty] | 7083.8204 | 379.1891
CONTINGENCIES | [5 empty] | 379.1891
PROJECT SUPPORT SUB TOTAL WITH CONTINGENCIES | [5 empty] | 7463.0095
TOTAL ESTIMATED COST FOR ENTIRE WORK ORDER | [5 empty] | 35829.0191
CONTINGENCIES | [5 empty] | 942.9391
TOTAL ESTIMATED COST FOR ENTIRE WORK ORDER WITH CONTINGENCIES | [5 empty] | 36771.9582

## Risk Factors
ENA TECHNICAL SERVICES
PROJECT COST ESTIMATE
2025-09-26
| CUSTOMER COMPANY NAME: | Enron North America (Houston Pipe Line Co.)
| PROJECT NAME: | Temporary Meter & Regulator Station for Midcon's Carbon Black Delivery
| W.O. NUMBER: | Not Assigned
| PROJECT ENGINEER: | Rodney Rogers | FILE NAME: | CostEstimateCarbonBlack.xls
REVISION NUMBER:
| PLANNER / MARKETER: | Ginger Causey/Mike Morris
RISK FACTORS
1. Delays and additional costs associated with access to Clark Refinery's property.
2. Delays and additional costs associated with bad weather.
3. Delays and additional costs associated with material availability and hot shot/ expediting requirements.
4. Delays and additional costs associated with project approval.
5. Delays and additional costs associated with not being able to utilize the Special Project Team to complete construction activities.

## Contact List
ENA TECHNICAL SERVICES
PROJECT COST ESTIMATE
2025-09-26
| CUSTOMER COMPANY NAME: | Enron North America (Houston Pipe Line Co.)
| PROJECT NAME: | Temporary Meter & Regulator Station for Midcon's Carbon Black Delivery
| W.O. NUMBER: | Not Assigned
| PROJECT ENGINEER: | Rodney Rogers |  | FILE NAME: | CostEstimateCarbonBlack.xls
REVISION NUMBER:
| PLANNER / MARKETER: | Ginger Causey/Mike Morris
PROJECT CONTACT LIST
| Name | Title | Office | Pager | Mobile
| Rodney Rogers | ENA Project Engineer | (713)853-5470 | (877)326-0099 | (713)569-0969
| Don Thomas | ENA Construction Manager | (713)853-5581 | (281)490-6549 | (713)818-4075
| Ron Suber | ENA Special Project Team Leader | (713)853-2245 | (800)632-5193 | (713)705-6654
| T.A. Mills | HMS Foreman | (281)652-2562 | (409)755-9433 | (409)656-4467
| Tom Cathey | HMS Division Measurement Engineer | (281)652-2004 | (281)490-1790 | (713)805-0181
| Randy Ernst | EOC Lumberton Team Member | (281)652-2559 | (409)755-5975 pin 083-4295 | (409)781-8590
| David Ayers | EOC Environment | (281)652-2003 | 800-960-6987 | (713)907-5075
| Bac Ly | ENA Designer | (713)853-4834 | 2812629163
| Charlie Thompson | EOC Tech Ops Director | (281)652-2102 | 7136081022 | 7138188314
| Steve Cherry | EOC Lumberton Team Advisor | 2814901484 | 7137050473 | 7137050473
| Ginger Causey | ENA Facility Planner | (713)853-7813 | 8007055829
| James Mckay | ENA Gas Control Director | (713)853-6448 | 8007167133 | 7132027839
| Kevin Kuehler | ENA Engineering & Constr. Director | (713)853-9319 | (800)980-6628 pin 0968634 | 2813810990
| Mike Morris | ENA Deal Maker | (713)853-7513
| Guy Lambert | Midcon Operations Coordinator | (409)843-4223 ext.225 | 4097265906 | 4097811404
cc: | Don Thomas
Ron Suber
T.A. Mills
Tom Cathey
Randy Ernst
David Ayers
Bac Ly
Charlie Thompson
Steve Cherry
Ginger Causey
James Mckay
Kevin Kuehler
Mike Morris
Nick Cocavessis