## Sheet1
Visualpro Channel Descriptions (NON CAN-BUSS) Red denotes not used
CHANNEL | DESCRIPTION | UNIT | MIN | MAX | CHANNEL | DESCRIPTION | UNIT | MIN | MAX
1 | POWER | kW | 0 | 2000 | 41 | TEMP SHAFT BEARING (ROTOR BEARING AT PILLOW BLOCK) | deg. Celcius | 0 | 100
2 | TOWER DEFLECTION | ms | 45 | 55 | 42 | HIGH SPEED RUNNING NUMBER |  | 0 | 20
3 | POWER FACTOR |  | -1.1 | 1.1 | 43 | DIGITAL 1 |  | 0 | 255
4 | REACTIVE POWER | kVar | -1000 | 1000 | 44 | DIGITAL 2 |  | 0 | 255
5 | VOLTAGE PHASE A_N | V | 0 | 600 | 45 | PARK POWER (NOT MONITORED) | kW | 0 | 30000
6 | VOLTAGE PHASE B_N | V | 0 | 600 | 46 | TOWER ACCELERATION | mm/s2 | 0 | 5000
7 | VOLTAGE PHASE C_N | V | 0 | 600 | 47 | DRIVE TRAIN ACCELERATION | mm/s2 | 0 | 1000
8 | CURRENT PHASE A | A | 0 | 2000 | 48 | TEMP GEARBOX BEARING B (NOT MONITORED) | deg. Celcius | 0 | 200
9 | CURRENT PHASE B | A | 0 | 2000 | 49 | T-TRANSFORMER 1 (NOT MONITORED) | deg. Celcius | -300 | 300
10 | CURRENT PHASE C | A | 0 | 2000 | 50 | T-TRANSFORMER 2 (NOT MONITORED) | deg. Celcius | -300 | 300
11 | GENERATOR SPEED | rpm | 0 | 2000 | 51 | T-TRANSFORMER 3 (NOT MONITORED) | deg. Celcius | -300 | 300
12 | ROTOR SPEED | rpm | 0 | 30 | 52 | RESERVE 4 |  | 0 | 1000
13 | BLADE 1 ACTUAL VALUE (BLADE POSITION) | degrees | -5 | 90 | 53 | RESERVE 5 |  | 0 | 1000
14 | WIND SPEED | m/s | 0 | 18 | 54 | RESERVE 6 |  | 0 | 1000
15 | NACELLE POSITION ( POSITION THE HUB IS POINTING) | degrees | -360 | 360 | 55 | RESERVE 7 |  | 0 | 1000
16 | NACELLE REVOLUTION ( TWIST COUNT) |  | -3 | 3 | 56 | RESERVE 8 |  | 0 | 1000
17 | GEN./GEARBOX SPEED (WATCHDOG SPEED) | rpm | 0 | 2000 | 57 | SCOPE CH 1 (P. 30 .1 SCOPE FUNC.) |  | -65000 | 65000
18 | WIND DEVIATION 1 SEC. |  | -200 | 200 | 58 | SCOPE CH 2 (P. 30 .2 SCOPE FUNC.) |  | -65000 | 65000
19 | BLADE 2 ACTUAL VALUE (BLADE POSITION) | degrees | -5 | 90 | 59 | SCOPE CH 3 (P. 30 .3 SCOPE FUNC.) |  | -65000 | 65000
20 | BLADE 3 ACTUAL VALUE (BLADE POSITION) | degrees | -5 | 90 | 60 | SCOPE CH 4 (P. 30 .4 SCOPE FUNC.) |  | -65000 | 65000
21 | BLADE 1 SET VALUE (COMMANDED VALUE FROM PLC) | degrees | -5 | 90 | 61 | DI 1 MAIN (CONVERT DECIMAL TO BINARY FOR STATUS) |  | 0 | 1000
22 | BLADE 2 SET VALUE (COMMANDED VALUE FROM PLC) | degrees | -5 | 90 | 62 | DI 2 MAIN (CONVERT DECIMAL TO BINARY FOR STATUS) |  | 0 | 1000
23 | BLADE 3 SET VALUE (COMMANDED VALUE FROM PLC) | degrees | -5 | 90 | 63 | DI 1 TOP (CONVERT DECIMAL TO BINARY FOR STATUS) |  | 0 | 1000
24 | POWER FACTOR SET VALUE (COS PHI) |  | -1 | 1 | 64 | DI 2 TOP (CONVERT DECIMAL TO BINARY FOR STATUS) |  | 0 | 1000
25 | N-SET 1 (SET 1440 RPM PITCH CONTROL) | rpm | 0 | 2000 | 65 | DI 3 TOP (CONVERT DECIMAL TO BINARY FOR STATUS) |  | 0 | 1000
26 | N-SET 2 (SET 1400 RPM TORQUE CONTROL) | rpm | 0 | 2000 | 66 | DI 4 TOP (CONVERT DECIMAL TO BINARY FOR STATUS) |  | 0 | 1000
27 | TORQUE ACTUAL VALUE ( ACTUAL TORQUE) | % | 0 | 100 | 67 | DO 1 MAIN (CONVERT DECIMAL TO BINARY FOR STATUS) |  | 0 | 1000
28 | TORQUE SET VALUE (COMMANDED TORQUE) | % | 0 | 100 | 68 | DO 2 MAIN (CONVERT DECIMAL TO BINARY FOR STATUS) |  | 0 | 1000
29 | OPERATING STATE ( NUMERICAL STATE OF TURBINE OPERATION) |  | 0 | 20 | 69 | DO 1 TOP (CONVERT DECIMAL TO BINARY FOR STATUS) |  | 0 | 1000
30 | CHANNEL 30 ( EMPTY) |  | 0 | 0 | 70 | DO 2 TOP (CONVERT DECIMAL TO BINARY FOR STATUS) |  | 0 | 1000
31 | WIND DEVIATION 10 SEC. |  | 0 | 300
32 | TEMP GENERATOR 1 (WINDING TEMP) | deg. Celcius | 0 | 150
33 | TEMP GENERATOR 2 (WINDING TEMP) | deg. Celcius | 0 | 150
34 | TEMP BEARING A ( AT FLEX COUPLING)) | deg. Celcius | 0 | 100
35 | TEMP BEARING B (REAR GENERATOR BELOW ENCODER) | deg. Celcius | 0 | 100
36 | TEMP GEARBOX (OIL SUMP) | deg. Celcius | 0 | 100
37 | TEMP OUTSIDE (AMBIENT OUTSIDE TEMP) | deg. Celcius | 0 | 50
38 | TEMP NACELLE (TEMP INSIDE NACELLE) | deg. Celcius | 0 | 50
39 | TEMP GENERATOR COOLING AIR (TEMP FROM HEAT EXCHANGE GEN.) | deg. Celcius | 0 | 120
40 | TEMP GEARBOX BEARING A (HIGH SPEED SHAFT AT BRAKE DISK) | deg. Celcius | 0 | 100

## Sheet2
Visualpro Channel Descriptions (CAN-BUSS) Red denotes not used
CHANNEL | DESCRIPTION | UNIT | MIN | MAX | CHANNEL | DESCRIPTION | UNIT | MIN | MAX
1 | POWER | kW | 0 | 2000 | 41 | TEMP SHAFT BEARING (ROTOR BEARING AT PILLOW BLOCK) | deg. Celcius | 0 | 100
2 | TOWER DEFLECTION | ms | 45 | 55 | 42 | HIGH SPEED RUNNING NUMBER |  | 0 | 20
3 | POWER FACTOR |  | -1.1 | 1.1 | 43 | DIGITAL 1 |  | 0 | 255
4 | REACTIVE POWER | kVar | -1000 | 1000 | 44 | DIGITAL 2 |  | 0 | 255
5 | VOLTAGE PHASE A_N | V | 0 | 600 | 45 | PARK POWER (NOT MONITORED) | kW | 0 | 30000
6 | VOLTAGE PHASE B_N | V | 0 | 600 | 46 | TOWER ACCELERATION | mm/s2 | 0 | 5000
7 | VOLTAGE PHASE C_N | V | 0 | 600 | 47 | DRIVE TRAIN ACCELERATION | mm/s2 | 0 | 1000
8 | CURRENT PHASE A | A | 0 | 2000 | 48 | TEMP GEARBOX BEARING B (NOT MONITORED) | deg. Celcius | 0 | 200
9 | CURRENT PHASE B | A | 0 | 2000 | 49 | T-TRANSFORMER 1 (NOT MONITORED) | deg. Celcius | -300 | 300
10 | CURRENT PHASE C | A | 0 | 2000 | 50 | T-TRANSFORMER 2 (NOT MONITORED) | deg. Celcius | -300 | 300
11 | GENERATOR SPEED | rpm | 0 | 2000 | 51 | T-TRANSFORMER 3 (NOT MONITORED) | deg. Celcius | -300 | 300
12 | ROTOR SPEED | rpm | 0 | 30 | 52 | RESERVE 4 |  | 0 | 1000
13 | BLADE 1 ACTUAL VALUE (BLADE POSITION) | degrees | -5 | 90 | 53 | RESERVE 5 |  | 0 | 1000
14 | WIND SPEED | m/s | 0 | 18 | 54 | RESERVE 6 |  | 0 | 1000
15 | NACELLE POSITION ( POSITION THE HUB IS POINTING) | degrees | -360 | 360 | 55 | RESERVE 7 |  | 0 | 1000
16 | NACELLE REVOLUTION ( TWIST COUNT) |  | -3 | 3 | 56 | RESERVE 8 |  | 0 | 1000
17 | GEN./GEARBOX SPEED (WATCHDOG SPEED) | rpm | 0 | 2000 | 57 | SCOPE CH 1 (P. 30 .1 SCOPE FUNC.) |  | -65000 | 65000
18 | WIND DEVIATION 1 SEC. |  | -200 | 200 | 58 | SCOPE CH 2 (P. 30 .2 SCOPE FUNC.) |  | -65000 | 65000
19 | BLADE 2 ACTUAL VALUE (BLADE POSITION) | degrees | -5 | 90 | 59 | SCOPE CH 3 (P. 30 .3 SCOPE FUNC.) |  | -65000 | 65000
20 | BLADE 3 ACTUAL VALUE (BLADE POSITION) | degrees | -5 | 90 | 60 | SCOPE CH 4 (P. 30 .4 SCOPE FUNC.) |  | -65000 | 65000
21 | BLADE 1 SET VALUE (COMMANDED VALUE FROM PLC) | degrees | -5 | 90 | 61 | DI 1 MAIN (CONVERT DECIMAL TO BINARY FOR STATUS) |  | 0 | 1000
22 | BLADE 2 SET VALUE (COMMANDED VALUE FROM PLC) | degrees | -5 | 90 | 62 | DI 2 MAIN (CONVERT DECIMAL TO BINARY FOR STATUS) |  | 0 | 1000
23 | BLADE 3 SET VALUE (COMMANDED VALUE FROM PLC) | degrees | -5 | 90 | 63 | DI 1 TOP (CONVERT DECIMAL TO BINARY FOR STATUS) |  | 0 | 1000
24 | POWER FACTOR SET VALUE (COS PHI) |  | -1 | 1 | 64 | DI 2 TOP (CONVERT DECIMAL TO BINARY FOR STATUS) |  | 0 | 1000
25 | N-SET 1 (SET 1440 RPM PITCH CONTROL) | rpm | 0 | 2000 | 65 | DI 3 TOP (CONVERT DECIMAL TO BINARY FOR STATUS) |  | 0 | 1000
26 | N-SET 2 (SET 1400 RPM TORQUE CONTROL) | rpm | 0 | 2000 | 66 | CAN_BUSS I/O (CONVERT DECIMAL TO BINARY FOR STATUS) |  | 0 | 1000
27 | TORQUE ACTUAL VALUE ( ACTUAL TORQUE) | % | 0 | 100 | 67 | DO 1 MAIN (CONVERT DECIMAL TO BINARY FOR STATUS) |  | 0 | 1000
28 | TORQUE SET VALUE (COMMANDED TORQUE) | % | 0 | 100 | 68 | DO 2 MAIN (CONVERT DECIMAL TO BINARY FOR STATUS) |  | 0 | 1000
29 | OPERATING STATE ( NUMERICAL STATE OF TURBINE OPERATION) |  | 0 | 20 | 69 | DO 1 TOP (CONVERT DECIMAL TO BINARY FOR STATUS) |  | 0 | 1000
30 | CHANNEL 30 ( EMPTY) |  | 0 | 0 | 70 | DO 2 TOP (CONVERT DECIMAL TO BINARY FOR STATUS) |  | 0 | 1000
31 | WIND DEVIATION 10 SEC. |  | 0 | 300
32 | TEMP GENERATOR 1 (WINDING TEMP) | deg. Celcius | 0 | 150
33 | TEMP GENERATOR 2 (WINDING TEMP) | deg. Celcius | 0 | 150
34 | TEMP BEARING A ( AT FLEX COUPLING)) | deg. Celcius | 0 | 100
35 | TEMP BEARING B (REAR GENERATOR BELOW ENCODER) | deg. Celcius | 0 | 100
36 | TEMP GEARBOX (OIL SUMP) | deg. Celcius | 0 | 100
37 | TEMP OUTSIDE (AMBIENT OUTSIDE TEMP) | deg. Celcius | 0 | 50
38 | TEMP NACELLE (TEMP INSIDE NACELLE) | deg. Celcius | 0 | 50
39 | TEMP GENERATOR COOLING AIR (TEMP FROM HEAT EXCHANGE GEN.) | deg. Celcius | 0 | 120
40 | TEMP GEARBOX BEARING A (HIGH SPEED SHAFT AT BRAKE DISK) | deg. Celcius | 0 | 100