## COVER
Desert Sky
MONTHLY REPORT
FOR
May '02

## WTG Down
DESERT SKY
SIGNIFICANT WTG DOWN TIME
Month: | May '02 |  |  |  | Reason: F=fault, U=unscheduled maint. S= scheduled maint. O= other.
WTG # | Date off | Time off | Date on | Time on | Hrs. | Reason | Comments
4 | 2002-05-01 | 0000 | 2002-05-01 | 1200 | 12 | F | Repaired broken gearbox oil pump mount
105 | 2002-05-01 | 230 | 2002-05-01 | 1530 | 15 | F | Safety chain
117 | 2002-05-01 | 0000 | 2002-05-01 | 1300 | 13 | F | IGBT overload
68 | 2002-05-01 | 0000 | 2002-05-01 | 1400 | 14 | F | Lost commissioning due to faulty Moeller DIL-EEM relay
67 | 2002-05-01 | 1730 | 2002-05-02 | 600 | 12.5 | F | Hub key fell off and hit e-stop
61 | 2002-05-11 | 2000 | 2002-05-12 | 1030 | 14.5 | F | IGBT overload caused by latched-up crowbar thyristor.
102 | 2002-05-04 | 1900 | 2002-05-06 | 1200 | 41 | F | Multiple hub faults caused by slip ring wiring that was stretched and cut. Repaired wiring and replaced fuse.
92 | 2002-05-10 | 1115 | 2002-05-11 | 1745 | 30.5 | F | Replaced broken sight glass in hub
56 | 2002-05-04 | 0845 | 2002-05-10 | 1000 | 145.25 | F | Axis 3 pitch encoder was bad. We had to wait for a new encoder.
69 | 2002-05-10 | 2030 | 2002-05-11 | 1300 | 16.5 | F | Hydraulic unit mount broke and fluid leaked out. Took mount from another down turbine.
108 | 2002-05-08 | 700 | 2002-05-31 | 2400 | 569 | F | Down for excessive generator vibration. TURBINE STILL DOWN
116 | 2002-05-08 | 800 | 2002-05-31 | 2400 | 568 | F | Down for excessive generator vibration. TURBINE STILL DOWN
72 | 2002-05-09 | 1015 | 2002-05-17 | 1145 | 193.5 | F | Oil pump mount broke and oil pump fell and cut oil hose. Had to wait for a new hose.
120 | 2002-05-22 | 1600 | 2002-05-23 | 1645 | 24.75 | F | Rotor j-box fell off and cut wires in brush wear circuit
62 | 2002-05-22 | 1730 | 2002-05-23 | 1445 | 21.25 | F | Replaced pitch encoder. Had to wait for new encoder
28 | 2002-05-21 | 1345 | 2002-05-23 | 1300 | 47.25 | F | Replaced pitch encoder. Had to wait for new encoder
83 | 2002-05-19 | 430 | 2002-05-21 | 830 | 52 | F | Repaired blade closeout that fell out
33 | 2002-05-24 | 1745 | 2002-05-25 | 1030 | 16.75 | F | Replaced blown CB-1 charging fuse
69 | 2002-05-28 | 2000 | 2002-05-29 | 930 | 13.5 | F | Replaced MS-3
35 | 2002-05-18 | 1400 | 2002-05-28 | 1115 | 237.5 | F | Oil pump motor was bad. We had to wait for a new motor.
70 | 2002-05-13 | 1230 | 2002-05-31 | 2400 | 443.5 | F | Down for excessive generator vibration. TURBINE STILL DOWN
62 | 2002-05-26 | 1400 | 2002-05-30 | 1100 | 93 | F | Rotor j-box fell off and cut wires in brush wear circuit
62 | 2002-05-22 | 1730 | 2002-05-23 | 1445 | 21.25 | F | Replaced pitch encoder. Had to wait for new encoder
67 | 2002-05-14 | 0800 | 2002-05-17 | 1230 | 76.5 | F | WindClean painted tower.
63 | 2002-05-20 | 1015 | 2002-05-21 | 1645 | 30.5 | F | Replaced bad pitch encoder
2 | 2002-05-21 | 0245 | 2002-05-24 | 1630 | 85.75 | F | Current asymmetry problem
88 | 2002-05-21 | 0645 | 2002-05-24 | 2000 | 85.25 | F | Converter had bad choke. Had to wait for new choke
13 | 2002-05-22 | 0545 | 2002-05-23 | 1515 | 33.5 | F | Converter had 2 bad IGBT's
72 | 2002-05-25 | 0900 | 2002-05-28 | 1330 | 76.45 | F | Replaced bad CSC SUR
56 | 2002-05-05 | 1415 | 2002-05-10 | 0930 | 91.25 | F | Replaced pitch encoder. Had to wait for new encoder
118 | 2002-05-01 | 0000 | 2002-05-01 | 1330 | 13.5 | F | Missing commissioning. Replaced K-5 in SEG.
41 | 2002-05-02 | 1530 | 2002-05-03 | 1200 | 20.5 | F | Repaired broken bolts on generator rotor j-box.

## GRID
DESERT SKY
GRID VARIANCE
Chargeable to: A=AEP, N=Force Majeure, E=Enron, T= TXU
Month: | May '02 |  |  | Reason: U=unscheduled outage, S= scheduled outage, F=fluctuation
Charge | Date off | Time off | Date on | Time on | Hrs. | Reason | Comments
E | 2002-05-07 | 09:57 | 2002-05-07 | 10:15 | 0.26 | S | Change taps on 138kV transformer.

## WEATHER
DESERT SKY
WEATHER EVENTS
Month: | May '02
Date | Time | Event | Comments
5/10 | 1900 | Thunderstorm | Heavy rain and hail. Burned up two oil pressure sensors and a hub fuse.
2002-05-28 | 2000 | Thunderstorm | Heavy rain and hail. Burned up two three pressure sensors.

## RECALL
DESERT SKY
CREW CALL-OUTS
Month: | May '02
Date | Time | Who | Reason
2002-05-11 | 2000 | Matt Allsup, John Hornbeck | Grid disturbance caused 25 CB-1 trips and 9 IGBT overloads.

## PARTS
DESERT SKY
PARTS USAGE
Month: | May
Date | WTG # | EW Part # | Description | Qty. | Comments
2002-05-07 | 46 | T56137900200 | PLC digital input | 1
2002-05-07 | 46 | T56137899700 | PLC digital input 32X | 1
2002-05-07 | 46 | T56137909700 | PLC analog In/Out | 2
2002-05-07 | 46 |  | Bolt M10 x 25 | 8
2002-05-07 | 41 | T56137900200 | PLC digital input | 1
2002-05-07 | 17 | T56151800005 | UPS | 1
2002-05-07 | 31 | T56151800005 | UPS | 1
2002-05-07 | 78 | T56151800005 | UPS | 1
2002-05-07 | 108 | UX59901000106 | Nut, M24 | 1
2002-05-07 | 17 | T56031020396 | MS3 | 1
2002-05-07 | 102 | T56225038310 | Positioning controller GEL | 1
2002-05-07 | 102 | UX59901000145 | PLC "CAN"Bus Master | 1
2002-05-07 | 102 | T56137900300 | PLC digital output 32x | 1
2002-05-07 | 102 | UX59901000029 | Fuse 50A Class J | 1
2002-05-07 | 105 | UX56750030070 | Sensor, Prox, 7M cable | 2
2002-05-07 | 105 | T56260102001 | Rotor-overspeed monitor | 1
2002-05-07 | 102 | T56602067718 | RDB DIL 250 | 1
2002-05-07 | 4 | T56602092560 | Relay 3p., 115v, 60Hz | 1
2002-05-07 | 19 | UX59901000029 | Fuse 50A Class J | 6
2002-05-07 | 17 | T56137900200 | PLC digital input | 1
2002-05-07 | 1 | T56151800005 | UPS | 1
2002-05-07 | 2 | T56151800005 | UPS | 1
2002-05-07 | 5 | T56151800005 | UPS | 1
2002-05-07 | 7 | T56151800005 | UPS | 1
2002-05-07 | 13 | T56151800005 | UPS | 1
2002-05-07 | 15 | T56151800005 | UPS | 1
2002-05-07 | 17 | T56151800005 | UPS | 1
2002-05-07 | 18 | T56151800005 | UPS | 1
2002-05-07 | 19 | T56151800005 | UPS | 1
2002-05-07 | 20 | T56151800005 | UPS | 1
2002-05-07 | 59 | T56602063220 | relay coil for G-DIL3M | 1
2002-05-07 | 59 | T56114798682 | Overvoltage protection plug | 1
2002-05-07 | 105 | UX59901000116 | Aux. Contact Block | 2
2002-05-07 | 17 | T56730000001 | doide for industrial relay | 1
2002-05-07 | 4 | T56602048645 | Relay oilpump gearbox | 1
2002-05-07 | 114 | T56602048645 | Relay oilpump gearbox | 1
2002-05-07 | 7 | T56602048645 | Relay oilpump gearbox | 1
2002-05-07 | 61 | T56602048645 | Relay oilpump gearbox | 1
2002-05-07 | 59 | T56602048645 | Relay oilpump gearbox | 1
2002-05-07 | 21 | T56151800005 | UPS | 1
2002-05-07 | 22 | T56151800005 | UPS | 1
2002-05-07 | 23 | T56151800005 | UPS | 1
2002-05-07 | 24 | T56151800005 | UPS | 1
2002-05-07 | 25 | T56151800005 | UPS | 1
2002-05-07 | 26 | T56151800005 | UPS | 1
2002-05-07 | 27 | T56151800005 | UPS | 1
2002-05-07 | 28 | T56151800005 | UPS | 1
2002-05-07 | 29 | T56151800005 | UPS | 1
2002-05-07 | 30 | T56151800005 | UPS | 1
2002-05-07 | 31 | T56151800005 | UPS | 1
2002-05-07 | 32 | T56151800005 | UPS | 1
2002-05-07 | 33 | T56151800005 | UPS | 1
2002-05-07 | 34 | T56151800005 | UPS | 1
2002-05-07 | 35 | T56151800005 | UPS | 1
2002-05-07 | 36 | T56151800005 | UPS | 1
2002-05-07 | 107 | T56151800005 | UPS | 1
2002-05-07 | 108 | T56151800005 | UPS | 1
2002-05-07 | 113 | T56151800005 | UPS | 1
2002-05-07 | 114 | T56151800005 | UPS | 1
2002-05-07 | 116 | T56151800005 | UPS | 1
2002-05-07 | 117 | T56151800005 | UPS | 1
2002-05-07 | 115 | T56151800005 | UPS | 1
2002-05-07 | 118 | T56151800005 | UPS | 1
2002-05-07 | 119 | T56151800005 | UPS | 1
2002-05-07 | 120 | T56151800005 | UPS | 1
2002-05-07 | 121 | T56151800005 | UPS | 1
2002-05-07 | 122 | T56151800005 | UPS | 1
2002-05-07 | 1 | 901307 | brackets for UPS | 2
2002-05-07 | 2 | 901307 | brackets for UPS | 2
2002-05-07 | 5 | 901307 | brackets for UPS | 2
2002-05-07 | 7 | 901307 | brackets for UPS | 2
2002-05-07 | 13 | 901307 | brackets for UPS | 2
2002-05-07 | 15 | 901307 | brackets for UPS | 2
2002-05-07 | 17 | 901307 | brackets for UPS | 2
2002-05-07 | 18 | 901307 | brackets for UPS | 2
2002-05-07 | 19 | 901307 | brackets for UPS | 2
2002-05-07 | 20 | 901307 | brackets for UPS | 2
2002-05-07 | 21 | 901307 | brackets for UPS | 2
2002-05-07 | 22 | 901307 | brackets for UPS | 2
2002-05-07 | 23 | 901307 | brackets for UPS | 2
2002-05-07 | 24 | 901307 | brackets for UPS | 2
2002-05-07 | 25 | 901307 | brackets for UPS | 2
2002-05-07 | 26 | 901307 | brackets for UPS | 2
2002-05-07 | 27 | 901307 | brackets for UPS | 2
2002-05-07 | 28 | 901307 | brackets for UPS | 2
2002-05-07 | 29 | 901307 | brackets for UPS | 2
2002-05-07 | 30 | 901307 | brackets for UPS | 2
2002-05-07 | 31 | 901307 | brackets for UPS | 2
2002-05-07 | 32 | 901307 | brackets for UPS | 2
2002-05-07 | 33 | 901307 | brackets for UPS | 2
2002-05-07 | 34 | 901307 | brackets for UPS | 2
2002-05-07 | 35 | 901307 | brackets for UPS | 2
2002-05-07 | 36 | 901307 | brackets for UPS | 2
2002-05-07 | 37 | 901307 | brackets for UPS | 2
2002-05-07 | 60 | 901307 | brackets for UPS | 2
2002-05-07 | 63 | 901307 | brackets for UPS | 2
2002-05-07 | 65 | 901307 | brackets for UPS | 2
2002-05-07 | 66 | 901307 | brackets for UPS | 2
2002-05-07 | 70 | 901307 | brackets for UPS | 2
2002-05-07 | 71 | 901307 | brackets for UPS | 2
2002-05-07 | 72 | 901307 | brackets for UPS | 2
2002-05-07 | 73 | 901307 | brackets for UPS | 2
2002-05-07 | 74 | 901307 | brackets for UPS | 2
2002-05-07 | 78 | 901307 | brackets for UPS | 2
2002-05-07 | 79 | 901307 | brackets for UPS | 2
2002-05-07 | 80 | 901307 | brackets for UPS | 2
2002-05-07 | 81 | 901307 | brackets for UPS | 2
2002-05-07 | 82 | 901307 | brackets for UPS | 2
2002-05-07 | 83 | 901307 | brackets for UPS | 2
2002-05-07 | 84 | 901307 | brackets for UPS | 2
2002-05-07 | 85 | 901307 | brackets for UPS | 2
2002-05-07 | 86 | 901307 | brackets for UPS | 2
2002-05-07 | 87 | 901307 | brackets for UPS | 2
2002-05-07 | 88 | 901307 | brackets for UPS | 2
2002-05-07 | 89 | 901307 | brackets for UPS | 2
2002-05-07 | 96 | 901307 | brackets for UPS | 2
2002-05-07 | 100 | 901307 | brackets for UPS | 2
2002-05-07 | 102 | 901307 | brackets for UPS | 2
2002-05-07 | 103 | 901307 | brackets for UPS | 2
2002-05-07 | 104 | 901307 | brackets for UPS | 2
2002-05-07 | 105 | 901307 | brackets for UPS | 2
2002-05-07 | 107 | 901307 | brackets for UPS | 2
2002-05-07 | 108 | 901307 | brackets for UPS | 2
2002-05-07 | 113 | 901307 | brackets for UPS | 2
2002-05-07 | 114 | 901307 | brackets for UPS | 2
2002-05-07 | 115 | 901307 | brackets for UPS | 2
2002-05-07 | 116 | 901307 | brackets for UPS | 2
2002-05-07 | 117 | 901307 | brackets for UPS | 2
2002-05-07 | 118 | 901307 | brackets for UPS | 2
2002-05-07 | 119 | 901307 | brackets for UPS | 2
2002-05-07 | 120 | 901307 | brackets for UPS | 2
2002-05-07 | 121 | 901307 | brackets for UPS | 2
2002-05-07 | 122 | 901307 | brackets for UPS | 2
2002-05-07 | 37 | T56151800005 | UPS | 1
2002-05-07 | 60 | T56151800005 | UPS | 1
2002-05-07 | 63 | T56151800005 | UPS | 1
2002-05-07 | 65 | T56151800005 | UPS | 1
2002-05-07 | 66 | T56151800005 | UPS | 1
2002-05-07 | 72 | T56151800005 | UPS | 1
2002-05-07 | 73 | T56151800005 | UPS | 1
2002-05-07 | 74 | T56151800005 | UPS | 1
2002-05-07 | 78 | T56151800005 | UPS | 1
2002-05-07 | 79 | T56151800005 | UPS | 1
2002-05-07 | 80 | T56151800005 | UPS | 1
2002-05-07 | 81 | T56151800005 | UPS | 1
2002-05-07 | 82 | T56151800005 | UPS | 1
2002-05-07 | 83 | T56151800005 | UPS | 1
2002-05-07 | 84 | T56151800005 | UPS | 1
2002-05-07 | 85 | T56151800005 | UPS | 1
2002-05-07 | 86 | T56151800005 | UPS | 1
2002-05-07 | 87 | T56151800005 | UPS | 1
2002-05-07 | 88 | T56151800005 | UPS | 1
2002-05-07 | 89 | T56151800005 | UPS | 1
2002-05-07 | 96 | T56151800005 | UPS | 1
2002-05-07 | 100 | T56151800005 | UPS | 1
2002-05-07 | 102 | T56151800005 | UPS | 1
2002-05-07 | 103 | T56151800005 | UPS | 1
2002-05-07 | 104 | T56151800005 | UPS | 1
2002-05-07 | 105 | T56151800005 | UPS | 1
2002-05-07 |  | UX59901000145 | PLC"CAN"Bus Master | 1 | used during commisioning/paid back to Manuf.
2002-05-07 | 4 | T56602074464 | Interference suppression circuit | 1
2002-05-07 | 114 | T56602074464 |  | 1
2002-05-07 | 7 | T56602074464 |  | 1
2002-05-07 | 61 | T56602074464 |  | 1
2002-05-07 | 59 | T56602074464 |  | 1
2002-05-07 | 4 |  | 1/2" washer | 8
2002-05-07 | Sub | T56151801115 | UPS | 2
2002-05-08 | 56 | UX59901000128 | Pitch Motor Encoder | 1
2002-05-10 | 114 | T56031019947 | Control System for main | 1
2002-05-10 | 56 | T56779400916 | light | 1
2002-05-10 | 56 | UX56203000003 | lamp | 2
2002-05-10 | 56 | T56779400916 | light | 1
2002-05-10 | 53 | T56731010267 | Vibration Monitor | 1
2002-05-10 | 106 | T56602074464 | Interference suppression circuit | 2
2002-05-10 | 106 | T56602048645 | Relay oilpump gearbox | 2
2002-05-10 | 109 |  | half moon pipe | 2
2002-05-10 | 109 |  | clamp for half moon pipe | 2
2002-05-10 | 75 | UX59901000073 | Switch/Transducer pressure | 1
2002-05-10 | scada | T56151801115 | UPS 115v Merlin | 3
2002-05-10 | 118 | T56836060333 | Computer, 60Hz, TZ1.5 | 1
2002-05-10 | 56 | UX59901000128 | Pitch Motor Encoder | 1
2002-05-10 | 105 | UX87002000700 | Hoist | 1
2002-05-10 | 73 | UX87002000700 | Hoist | 1
2002-05-10 | 17 |  | 8" oil level indicator | 1
2002-05-10 | 1 |  | Grease bucket/mainshaft | 1
2002-05-13 | 92 | UX59901000103 | OIL SIGHT GLASS | 1
2002-05-13 | 14 | UX59901000073 | Switch/Transducer pressure | 1
2002-05-13 | 51 | UX56750030070 | Sensor, Prox, 7m cable | 2
2002-05-13 | 37 | UX59901000115 | Generator Encoder | 1
2002-05-13 | 92 | UX56203000003 | Flourscent bulb, nacelle | 2
2002-05-13 | 61 | UX59901000067 | Thyristor | 1
2002-05-13 | 59 | UX59901000128 | Pitch Motor Encoder | 1
2002-05-20 | 62 |  | M10x25 bolts | 6
2002-05-20 | 71 | T56031020396 | MS3 | 1
2002-05-20 | 62 | T56602061217 | Air contactor 3 pole | 1
2002-05-20 | 62 | T56602074464 | Interfenerce suppression circuit | 1
2002-05-20 | 62 | UX59901000073 | Switch/Transducer pressure | 1
2002-05-20 | 116 | 3M-06273 | Zip ties | 25
2002-05-20 | 49 | T56228220903 | Fuse 690/40A | 2
2002-05-20 | 83 | T56622120013 | Roller Lever wh/Roller type SCK-Y13 | 2
2002-05-20 | 83 | T56622110001 | 90 degree limit switch | 2
2002-05-21 | 88 | T56031031646 | Air contactor 3 pole | 1
2002-05-21 | 63 | T56779400916 | Hub Light | 2
2002-05-21 | 63 | UX56205400910 | Bulb, Florescent | 2
2002-05-21 | 88 | T56743006167 | Wind Cap 3 phase Capacitor | 2
2002-05-21 | 88 | T56031027722 | Overvoltage arrestor | 3
2002-05-21 | 63 | UX59901000128 | Pitch Motor Encoder | 1
2002-05-21 | 83 | T85121221000 | Sikaflex | 11
2002-05-21 | 63 | T56602063220 | Relay coil | 1
2002-05-21 | 28 | UX59901000128 | Pitch Motor Encoder | 1
2002-05-21 | 60 | UX59901000128 | Pitch Motor Encoder | 1
2002-05-22 | 103 | T56151800005 | UPS | 1
2002-05-23 | 88 |  | SEG Choke | 1
2002-05-28 | 60 | T56602063220 | Relay coil | 1
2002-05-28 | SCADA | UX90901901228 | FOM-0102 PCB ASY,DVAR | 5
2002-05-28 | 2 | T56735137500 | Power Supply Monitoring MFR 13 | 1
2002-05-28 | 2 | T56031019947 | Control System for main | 1
2002-05-28 | 2 | UX59901000076 | Contact Element EC11, Contact Block | 1
2002-05-28 | 2 | T56137899700 | PLC digital Input 32x | 1
2002-05-28 | 2 | T56137932300 | PLC power supply Bachmann | 1
2002-05-28 | 2 | T56137965000 | PLC COM -interface | 1
2002-05-28 | 2 | T56137900400 | PLC dgiital output 16x | 1
2002-05-28 | 2 | T56137909700 | PLC analog In/Out | 2
2002-05-28 | 2 | T56137049500 | PLC Fast Busmaster | 1
2002-05-28 | 2 | T56604010213 | Aux. Relay 3 pole | 2
2002-05-28 | 2 | T56870000204 | Operation Panel | 1
2002-05-28 | 89 | T56031020396 | MS3 | 1
2002-05-28 | 31 | UX59901000029 | Fuse 50A Class J | 3
2002-05-28 | 28 | UX59901000128 | Pitch Motor Encoder | 1
2002-05-28 | 37 | T56228220903 | Fuse 690/40A | 2
2002-05-28 | 26 | T56031020396 | MS3 | 1
2002-05-28 | 57 | UX59901000067 | Thyristor | 1
2002-05-28 | 102 | T56228220903 | Fuse 690/40A | 2
2002-05-28 | 36 | T56604010213 | Aux. Relay 3 pole | 1
2002-05-28 | 27 | T56836060337 | 15" Monitor | 1
2002-05-28 | 20 | T56031019936 | Control System for main | 1
2002-05-30 | 120 | T56602074464 | Interface suppression circuit | 1
2002-05-30 | 100 | T56602074464 | Interface suppression circuit | 1
2002-05-30 | 120 | T56602061217 | Air contactor 3 pole | 1
2002-05-30 | 100 | T56602061217 | Air contactor 3 pole | 1
2002-05-30 | 69 | T56031020396 | MS3 | 1
2002-05-30 | 88 | UX59901000073 | Switch/Transducer pressure | 1
2002-05-30 | 56 | UX59901000073 | Switch/Transducer pressure | 1
2002-05-30 | 15 | UX59901000073 | Switch/Transducer pressure | 1
2002-05-30 | 35 |  | Oil pump motor (gearbox) | 1
2002-05-30 | 19 | UX59901000008 | UV Trip 110-120vac | 1
2002-05-30 | 105 | T56137070900 | PLC Inc1 Inc 2 | 1
2002-05-31 | 19 | T56604010213 | Aux. Relay 3 pole | 1

## LOW PRODUCERS
DESERT SKY
BOTTOM FIVE PRODUCERS
WTG | kW Hours | Sys. Avl | Mach. Avl | Line Avl | Reason

## CURTAILMENTS
DESERT SKY
CURTAILMENTS
Month: | May '02 |  |  |  | Turbine off |  |  | Turbine on
WTG | Date off | Time off | Date on | Time on | Name | CPS operator | Comments | Name | CPS operator | Comments
1 | 2002-05-01 | 17:10 | 2002-05-01 | 18:10 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
2 | 2002-05-01 | 17:10 | 2002-05-01 | 18:10 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
3 | 2002-05-01 | 17:10 | 2002-05-01 | 18:10 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
4 | 2002-05-01 | 17:10 | 2002-05-01 | 18:10 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
5 | 2002-05-01 | 17:10 | 2002-05-01 | 18:10 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
7 | 2002-05-01 | 17:10 | 2002-05-01 | 18:10 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
8 | 2002-05-01 | 17:10 | 2002-05-01 | 18:10 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
9 | 2002-05-01 | 17:10 | 2002-05-01 | 18:10 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
13 | 2002-05-01 | 17:10 | 2002-05-01 | 18:05 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
4 | 2002-05-01 | 17:10 | 2002-05-01 | 18:05 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
15 | 2002-05-01 | 17:10 | 2002-05-01 | 18:05 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
17 | 2002-05-01 | 17:10 | 2002-05-01 | 18:05 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
18 | 2002-05-01 | 17:10 | 2002-05-01 | 18:05 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
19 | 2002-05-01 | 17:10 | 2002-05-01 | 18:05 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
20 | 2002-05-01 | 17:10 | 2002-05-01 | 18:05 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
21 | 2002-05-01 | 17:10 | 2002-05-01 | 18:05 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
22 | 2002-05-01 | 18:30 | 2002-05-01 | 19:20 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
23 | 2002-05-01 | 18:30 | 2002-05-01 | 19:20 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
1 | 2002-05-01 | 21:00 | 2002-05-01 | 21:25 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
2 | 2002-05-01 | 21:00 | 2002-05-01 | 21:25 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
3 | 2002-05-01 | 21:00 | 2002-05-01 | 21:25 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
4 | 2002-05-01 | 21:00 | 2002-05-01 | 21:25 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
5 | 2002-05-01 | 21:00 | 2002-05-01 | 21:25 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
7 | 2002-05-01 | 21:00 | 2002-05-01 | 21:30 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
8 | 2002-05-01 | 21:00 | 2002-05-01 | 21:30 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
9 | 2002-05-01 | 21:00 | 2002-05-01 | 21:30 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
13 | 2002-05-01 | 21:00 | 2002-05-01 | 21:30 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
14 | 2002-05-01 | 21:00 | 2002-05-01 | 21:30 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
15 | 2002-05-01 | 21:00 | 2002-05-01 | 21:40 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
17 | 2002-05-01 | 21:00 | 2002-05-01 | 21:40 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
18 | 2002-05-01 | 21:00 | 2002-05-01 | 21:40 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
19 | 2002-05-01 | 21:00 | 2002-05-01 | 21:40 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
20 | 2002-05-01 | 21:00 | 2002-05-01 | 21:40 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
21 | 2002-05-01 | 21:00 | 2002-05-01 | 21:40 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
22 | 2002-05-01 | 21:00 | 2002-05-01 | 21:40 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
63 | 2002-05-01 | 18:25 | 2002-05-01 | 19:40 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
64 | 2002-05-01 | 18:25 | 2002-05-01 | 19:40 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
65 | 2002-05-01 | 18:25 | 2002-05-01 | 19:40 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
66 | 2002-05-01 | 18:25 | 2002-05-01 | 19:40 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
67 | 2002-05-01 | 18:25 | 2002-05-01 | 19:40 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
68 | 2002-05-01 | 18:25 | 2002-05-01 | 19:40 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
69 | 2002-05-01 | 18:25 | 2002-05-01 | 19:40 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
70 | 2002-05-01 | 18:25 | 2002-05-01 | 19:40 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
71 | 2002-05-01 | 18:25 | 2002-05-01 | 19:40 | Charlie | Johnny | OO'med to 20 MW per line | Charlie | Johnny | OO'med to 20 MW per line
72 | 2002-05-02 | 18:55 | 2002-05-02 | 20:30 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
73 | 2002-05-02 | 18:55 | 2002-05-02 | 20:30 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
74 | 2002-05-02 | 18:55 | 2002-05-02 | 21:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
75 | 2002-05-02 | 18:55 | 2002-05-02 | 21:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
76 | 2002-05-02 | 18:55 | 2002-05-02 | 21:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
77 | 2002-05-02 | 18:55 | 2002-05-02 | 21:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
78 | 2002-05-02 | 18:55 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
79 | 2002-05-02 | 18:55 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
80 | 2002-05-02 | 18:55 | 2002-05-02 | 22:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
81 | 2002-05-02 | 18:55 | 2002-05-02 | 22:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
82 | 2002-05-02 | 18:55 | 2002-05-02 | 22:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
83 | 2002-05-02 | 18:55 | 2002-05-02 | 22:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
84 | 2002-05-02 | 18:55 | 2002-05-02 | 22:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
85 | 2002-05-02 | 18:55 | 2002-05-02 | 22:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
86 | 2002-05-02 | 18:55 | 2002-05-02 | 22:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
87 | 2002-05-02 | 18:55 | 2002-05-02 | 22:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
88 | 2002-05-02 | 18:55 | 2002-05-02 | 22:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
89 | 2002-05-02 | 18:55 | 2002-05-02 | 22:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
90 | 2002-05-02 | 18:55 | 2002-05-02 | 22:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
91 | 2002-05-02 | 18:55 | 2002-05-02 | 22:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
92 | 2002-05-02 | 18:55 | 2002-05-02 | 22:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
93 | 2002-05-02 | 18:55 | 2002-05-02 | 22:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
96 | 2002-05-02 | 20:00 | 2002-05-02 | 22:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
100 | 2002-05-02 | 20:00 | 2002-05-02 | 22:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
102 | 2002-05-02 | 20:00 | 2002-05-02 | 22:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
103 | 2002-05-02 | 20:00 | 2002-05-02 | 22:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
104 | 2002-05-02 | 20:00 | 2002-05-02 | 22:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
105 | 2002-05-02 | 20:00 | 2002-05-02 | 22:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
106 | 2002-05-02 | 20:00 | 2002-05-02 | 22:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
23 | 2002-05-01 | 21:00 | 2002-05-01 | 21:40 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
24 | 2002-05-01 | 21:00 | 2002-05-01 | 23:55 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
25 | 2002-05-02 | 18:54 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
26 | 2002-05-02 | 18:54 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
27 | 2002-05-02 | 18:54 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
28 | 2002-05-02 | 18:54 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
29 | 2002-05-02 | 18:54 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
30 | 2002-05-02 | 18:54 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
32 | 2002-05-02 | 18:54 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
33 | 2002-05-02 | 18:54 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
34 | 2002-05-02 | 18:54 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
35 | 2002-05-02 | 18:54 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
36 | 2002-05-02 | 18:54 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
37 | 2002-05-02 | 18:54 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
38 | 2002-05-02 | 18:54 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
39 | 2002-05-02 | 18:54 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
40 | 2002-05-02 | 18:54 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
42 | 2002-05-02 | 18:54 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
43 | 2002-05-02 | 18:54 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
44 | 2002-05-02 | 18:54 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
45 | 2002-05-02 | 19:50 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
46 | 2002-05-02 | 19:50 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
47 | 2002-05-02 | 20:40 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
49 | 2002-05-02 | 20:40 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
50 | 2002-05-02 | 20:50 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
51 | 2002-05-02 | 20:50 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
52 | 2002-05-02 | 20:50 | 2002-05-02 | 22:25 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
55 | 2002-05-02 | 20:50 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
56 | 2002-05-02 | 20:50 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
57 | 2002-05-02 | 20:50 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
58 | 2002-05-02 | 20:50 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
59 | 2002-05-02 | 20:50 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
1 | 2002-05-02 | 20:55 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
2 | 2002-05-02 | 20:55 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
3 | 2002-05-02 | 20:55 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
4 | 2002-05-02 | 21:00 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
5 | 2002-05-02 | 21:00 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
7 | 2002-05-02 | 21:00 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
8 | 2002-05-02 | 22:00 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
9 | 2002-05-02 | 22:00 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
13 | 2002-05-02 | 22:00 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
14 | 2002-05-02 | 22:00 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
15 | 2002-05-02 | 22:00 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
107 | 2002-05-02 | 22:00 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
108 | 2002-05-02 | 22:00 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
109 | 2002-05-02 | 22:00 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
120 | 2002-05-02 | 22:00 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
113 | 2002-05-02 | 22:00 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
114 | 2002-05-02 | 22:00 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
118 | 2002-05-02 | 22:00 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
119 | 2002-05-02 | 22:00 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
121 | 2002-05-02 | 22:00 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
122 | 2002-05-02 | 22:00 | 2002-05-02 | 22:45 | Charlie | Buck | OO'med to 20 MW per line | Charlie | Buck | OO'med to 20 MW per line
1 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
2 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
3 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
4 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
5 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
7 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
8 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
9 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
13 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
14 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
15 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
17 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
18 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
19 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
20 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
21 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
22 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
23 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
24 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
25 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
26 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
27 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
28 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
29 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
30 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
35 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
36 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
37 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
38 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
39 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
40 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
32 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
33 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
34 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
43 | 2002-05-05 | 9:30 | 2002-05-05 | 11:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
44 | 2002-05-05 | 9:30 | 2002-05-05 | 11:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
45 | 2002-05-05 | 9:30 | 2002-05-05 | 11:00 | Bryan | Johnny | OO'med to 20 MW per line | Bryan | Johnny | OO'med to 20 MW per line
63 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
64 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
65 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
66 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
67 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
68 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
69 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
70 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
71 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
72 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
73 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
74 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
75 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
76 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
77 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
78 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
79 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
80 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
81 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
82 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
83 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
84 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
85 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
86 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
87 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
88 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
89 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
90 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
91 | 2002-05-05 | 9:30 | 2002-05-05 | 21:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
92 | 2002-05-05 | 9:30 | 2002-05-05 | 11:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
93 | 2002-05-05 | 9:30 | 2002-05-05 | 11:00 | John | Johnny | OO'med to 25 MW on line 2 | Bryan | Johnny | OOM released
1 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
2 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
3 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
4 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
5 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
7 | 2002-05-04 | 17:45 | 2002-05-04 | 21:30 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
8 | 2002-05-04 | 17:45 | 2002-05-04 | 21:30 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
9 | 2002-05-04 | 17:45 | 2002-05-04 | 21:30 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
13 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
14 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
15 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
17 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
18 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
19 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
20 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
21 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
22 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
23 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
24 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
25 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
26 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
27 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
28 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
29 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
30 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
32 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
33 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
34 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
35 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
36 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
37 | 2002-05-04 | 17:45 | 2002-05-05 | 4:00 | Bryan | Gilbert | Oomed to 35 MW on line 1 | Bryan | Gilbert | OOM released
69 | 2002-05-04 | 17:45 | 2002-05-05 | 5:30 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
70 | 2002-05-04 | 17:45 | 2002-05-05 | 5:30 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
71 | 2002-05-04 | 17:45 | 2002-05-05 | 5:30 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
72 | 2002-05-04 | 17:45 | 2002-05-05 | 5:30 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
73 | 2002-05-04 | 17:45 | 2002-05-05 | 5:30 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
74 | 2002-05-04 | 17:45 | 2002-05-05 | 5:30 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
75 | 2002-05-04 | 17:45 | 2002-05-05 | 5:30 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
76 | 2002-05-04 | 17:45 | 2002-05-05 | 5:30 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
77 | 2002-05-04 | 17:45 | 2002-05-05 | 5:30 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
78 | 2002-05-04 | 17:45 | 2002-05-05 | 5:30 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
79 | 2002-05-04 | 17:45 | 2002-05-05 | 5:30 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
80 | 2002-05-04 | 17:45 | 2002-05-05 | 5:30 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
81 | 2002-05-04 | 17:45 | 2002-05-05 | 5:30 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
82 | 2002-05-04 | 17:45 | 2002-05-05 | 5:30 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
83 | 2002-05-04 | 17:45 | 2002-05-05 | 5:30 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
84 | 2002-05-04 | 17:45 | 2002-05-05 | 5:30 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
85 | 2002-05-04 | 17:45 | 2002-05-05 | 5:30 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
86 | 2002-05-04 | 17:45 | 2002-05-05 | 5:00 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
87 | 2002-05-04 | 17:45 | 2002-05-05 | 5:00 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
88 | 2002-05-04 | 17:45 | 2002-05-05 | 5:00 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
89 | 2002-05-04 | 17:45 | 2002-05-05 | 5:00 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
90 | 2002-05-04 | 17:45 | 2002-05-05 | 5:00 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
91 | 2002-05-04 | 17:45 | 2002-05-05 | 5:00 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
92 | 2002-05-04 | 17:45 | 2002-05-05 | 5:00 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
93 | 2002-05-04 | 17:45 | 2002-05-05 | 5:00 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
96 | 2002-05-04 | 17:45 | 2002-05-04 | 21:30 | Bryan | Gilbert | Oomed to 35 MW on line 2 | Bryan | Gilbert | OOM released
78 | 2002-05-05 | 22:30 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
79 | 2002-05-05 | 22:30 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
80 | 2002-05-05 | 22:30 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
81 | 2002-05-05 | 22:30 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
82 | 2002-05-05 | 22:30 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
83 | 2002-05-05 | 22:30 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
84 | 2002-05-05 | 22:30 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
85 | 2002-05-05 | 22:30 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
86 | 2002-05-05 | 22:30 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
87 | 2002-05-05 | 22:30 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
88 | 2002-05-05 | 22:30 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
89 | 2002-05-05 | 22:30 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
90 | 2002-05-05 | 22:30 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
91 | 2002-05-05 | 22:30 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
92 | 2002-05-05 | 22:30 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
93 | 2002-05-05 | 22:30 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
96 | 2002-05-05 | 22:30 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
100 | 2002-05-05 | 22:30 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
103 | 2002-05-05 | 22:30 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
104 | 2002-05-05 | 22:30 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
108 | 2002-05-05 | 22:30 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
109 | 2002-05-05 | 22:30 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
120 | 2002-05-05 | 22:30 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
113 | 2002-05-05 | 22:30 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
119 | 2002-05-05 | 22:30 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
91 | 2002-05-06 | 0:05 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
92 | 2002-05-06 | 0:05 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
93 | 2002-05-06 | 0:05 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
1 | 2002-05-05 | 23:15 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
2 | 2002-05-05 | 23:15 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
3 | 2002-05-05 | 23:15 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
4 | 2002-05-05 | 23:15 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
5 | 2002-05-05 | 23:15 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
7 | 2002-05-05 | 23:15 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
8 | 2002-05-05 | 23:15 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
9 | 2002-05-05 | 23:15 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
13 | 2002-05-05 | 23:15 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
14 | 2002-05-05 | 23:15 | 2002-05-06 | 6:30 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
15 | 2002-05-05 | 23:15 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
17 | 2002-05-05 | 23:15 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
18 | 2002-05-05 | 23:15 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
19 | 2002-05-05 | 23:15 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
20 | 2002-05-05 | 23:15 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
21 | 2002-05-05 | 23:15 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
22 | 2002-05-05 | 23:15 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
23 | 2002-05-05 | 23:15 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
24 | 2002-05-05 | 23:15 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
25 | 2002-05-05 | 23:15 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
26 | 2002-05-05 | 23:15 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
27 | 2002-05-05 | 23:15 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
28 | 2002-05-05 | 23:15 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
29 | 2002-05-05 | 23:15 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
30 | 2002-05-05 | 23:15 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
32 | 2002-05-05 | 23:15 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
33 | 2002-05-05 | 23:15 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
34 | 2002-05-05 | 23:15 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
35 | 2002-05-06 | 0:05 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
36 | 2002-05-06 | 0:05 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
37 | 2002-05-06 | 0:05 | 2002-05-06 | 6:45 | Bryan | Buck | Oomed to 35 MW on line 2 | Bryan | Buck | OOM released
1 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
2 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
3 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
4 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
5 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
7 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
8 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
9 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
13 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
14 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
15 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
17 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
18 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
19 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
20 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
21 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
22 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
23 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
24 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
25 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
26 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
27 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
28 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
29 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
30 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
32 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
33 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
34 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
35 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
36 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
37 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
38 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
39 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
40 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
41 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
42 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
43 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Buck | Oomed to 20 MW on line 1 | Matt | Roger | OOM released
44 | 2002-05-06 | 7:00 | 2002-05-06 | 11:20 | Matt | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
45 | 2002-05-06 | 7:00 | 2002-05-06 | 12:20 | Matt | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
46 | 2002-05-06 | 7:00 | 2002-05-06 | 13:20 | Matt | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
47 | 2002-05-06 | 7:00 | 2002-05-06 | 14:20 | Matt | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
49 | 2002-05-06 | 8:15 | 2002-05-06 | 15:20 | Matt | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
50 | 2002-05-06 | 8:15 | 2002-05-06 | 16:20 | Matt | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
51 | 2002-05-06 | 8:15 | 2002-05-06 | 17:20 | Matt | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
52 | 2002-05-06 | 8:15 | 2002-05-06 | 18:20 | Matt | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
55 | 2002-05-06 | 8:15 | 2002-05-06 | 19:20 | Matt | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
63 | 2002-05-06 | 8:15 | 2002-05-06 | 20:20 | Matt | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
83 | 2002-05-06 | 8:15 | 2002-05-06 | 21:20 | Matt | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
108 | 2002-05-06 | 8:15 | 2002-05-06 | 22:20 | Matt | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
109 | 2002-05-06 | 8:15 | 2002-05-06 | 23:20 | Matt | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
120 | 2002-05-06 | 8:15 | 2002-05-06 | 24:20 | Matt | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
119 | 2002-05-06 | 8:15 | 2002-05-06 | 25:20 | Matt | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
117 | 2002-05-06 | 8:15 | 2002-05-06 | 26:20 | Matt | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
116 | 2002-05-06 | 8:15 | 2002-05-06 | 27:20 | Matt | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
57 | 2002-05-06 | 9:00 | 2002-05-06 | 28:20 | Matt | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
63 | 2002-05-06 | 9:00 | 2002-05-06 | 29:20 | Matt | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
64 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
65 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
66 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
67 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
68 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
69 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
70 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
71 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
72 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
73 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
74 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
75 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
76 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
77 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
78 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
79 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
80 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
81 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
82 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
84 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
85 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
86 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
87 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
88 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
89 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
90 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
91 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
92 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
93 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
96 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
100 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
103 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
104 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
106 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
107 | 2002-05-06 | 7:00 | 2002-05-06 | 10:20 | Bryan | Roger | Oomed to 10 MW per line | Matt | Roger | OOM released
44 | 2002-05-07 | 8:36 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Shut down for substation outage
45 | 2002-05-07 | 8:36 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Shut down for substation outage
46 | 2002-05-07 | 8:36 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Shut down for substation outage
47 | 2002-05-07 | 8:40 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Shut down for substation outage
49 | 2002-05-07 | 9:00 | 2002-05-07 | 9:25 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Shut down for substation outage
50 | 2002-05-07 | 9:00 | 2002-05-07 | 9:25 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Shut down for substation outage
51 | 2002-05-07 | 9:00 | 2002-05-07 | 9:25 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Shut down for substation outage
52 | 2002-05-07 | 9:00 | 2002-05-07 | 9:25 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Shut down for substation outage
54 | 2002-05-07 | 9:00 | 2002-05-07 | 9:25 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Shut down for substation outage
55 | 2002-05-07 | 9:00 | 2002-05-07 | 9:25 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Shut down for substation outage
57 | 2002-05-07 | 9:00 | 2002-05-07 | 9:25 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Shut down for substation outage
58 | 2002-05-07 | 9:00 | 2002-05-07 | 9:25 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Shut down for substation outage
59 | 2002-05-07 | 9:00 | 2002-05-07 | 9:25 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Shut down for substation outage
104 | 2002-05-07 | 9:25 | 2002-05-07 | 11:10 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
32 | 2002-05-07 | 10:30 | 2002-05-07 | 11:50 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
33 | 2002-05-07 | 10:30 | 2002-05-07 | 11:50 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
34 | 2002-05-07 | 10:30 | 2002-05-07 | 11:50 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
35 | 2002-05-07 | 10:30 | 2002-05-07 | 11:50 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
36 | 2002-05-07 | 10:30 | 2002-05-07 | 11:50 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
37 | 2002-05-07 | 10:30 | 2002-05-07 | 11:50 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
38 | 2002-05-07 | 10:30 | 2002-05-07 | 11:50 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
39 | 2002-05-07 | 10:30 | 2002-05-07 | 11:50 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
40 | 2002-05-07 | 10:30 | 2002-05-07 | 11:50 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
41 | 2002-05-07 | 10:30 | 2002-05-07 | 11:55 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Still oomed to 25 MW with low winds
42 | 2002-05-07 | 10:30 | 2002-05-07 | 11:55 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Still oomed to 25 MW with low winds
43 | 2002-05-07 | 10:30 | 2002-05-07 | 11:55 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Still oomed to 25 MW with low winds
44 | 2002-05-07 | 10:30 | 2002-05-07 | 11:55 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Still oomed to 25 MW with low winds
45 | 2002-05-07 | 10:30 | 2002-05-07 | 11:55 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Still oomed to 25 MW with low winds
46 | 2002-05-07 | 10:30 | 2002-05-07 | 11:55 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Still oomed to 25 MW with low winds
47 | 2002-05-07 | 10:30 | 2002-05-07 | 11:55 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Still oomed to 25 MW with low winds
49 | 2002-05-07 | 10:30 | 2002-05-07 | 11:55 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Still oomed to 25 MW with low winds
50 | 2002-05-07 | 10:30 | 2002-05-07 | 11:55 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Still oomed to 25 MW with low winds
51 | 2002-05-07 | 10:30 | 2002-05-07 | 11:55 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Still oomed to 25 MW with low winds
52 | 2002-05-07 | 10:30 | 2002-05-07 | 11:55 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Still oomed to 21 MW with low winds
55 | 2002-05-07 | 10:30 | 2002-05-07 | 11:05 | Matt | Johnny | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
69 | 2002-05-07 | 8:16 | 2002-05-07 | 10:45 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
70 | 2002-05-07 | 8:16 | 2002-05-07 | 10:45 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
71 | 2002-05-07 | 8:16 | 2002-05-07 | 10:45 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
72 | 2002-05-07 | 8:16 | 2002-05-07 | 10:45 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
73 | 2002-05-07 | 8:16 | 2002-05-07 | 10:45 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
74 | 2002-05-07 | 8:16 | 2002-05-07 | 10:45 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
75 | 2002-05-07 | 8:16 | 2002-05-07 | 11:00 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
76 | 2002-05-07 | 8:16 | 2002-05-07 | 11:00 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
77 | 2002-05-07 | 8:16 | 2002-05-07 | 11:00 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
78 | 2002-05-07 | 8:16 | 2002-05-07 | 11:55 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Still oomed to 21 MW with low winds
79 | 2002-05-07 | 8:16 | 2002-05-07 | 11:55 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Still oomed to 21 MW with low winds
80 | 2002-05-07 | 8:16 | 2002-05-07 | 11:55 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Still oomed to 21 MW with low winds
81 | 2002-05-07 | 8:16 | 2002-05-07 | 11:55 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Still oomed to 21 MW with low winds
82 | 2002-05-07 | 8:16 | 2002-05-07 | 11:55 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Still oomed to 21 MW with low winds
83 | 2002-05-07 | 8:16 | 2002-05-07 | 11:55 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Still oomed to 21 MW with low winds
84 | 2002-05-07 | 8:16 | 2002-05-07 | 11:55 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Still oomed to 21 MW with low winds
85 | 2002-05-07 | 8:16 | 2002-05-07 | 11:55 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Still oomed to 21 MW with low winds
86 | 2002-05-07 | 8:16 | 2002-05-07 | 11:55 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Still oomed to 21 MW with low winds
87 | 2002-05-07 | 8:16 | 2002-05-07 | 11:55 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Still oomed to 21 MW with low winds
88 | 2002-05-07 | 8:24 | 2002-05-07 | 11:55 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Still oomed to 21 MW with low winds
89 | 2002-05-07 | 8:24 | 2002-05-07 | 11:55 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Still oomed to 21 MW with low winds
90 | 2002-05-07 | 8:24 | 2002-05-07 | 11:55 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Still oomed to 21 MW with low winds
91 | 2002-05-07 | 8:24 | 2002-05-07 | 11:55 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Still oomed to 21 MW with low winds
92 | 2002-05-07 | 8:24 | 2002-05-07 | 11:55 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Still oomed to 21 MW with low winds
93 | 2002-05-07 | 8:24 | 2002-05-07 | 11:55 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Still oomed to 21 MW with low winds
96 | 2002-05-07 | 8:24 | 2002-05-07 | 11:55 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Still oomed to 21 MW with low winds
100 | 2002-05-07 | 8:31 | 2002-05-07 | 11:10 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
102 | 2002-05-07 | 8:31 | 2002-05-07 | 11:10 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
103 | 2002-05-07 | 8:31 | 2002-05-07 | 11:10 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Oomed to 21MW per line
37 | 2002-05-07 | 8:36 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Shut down for substation outage
38 | 2002-05-07 | 8:36 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Shut down for substation outage
39 | 2002-05-07 | 8:36 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Shut down for substation outage
40 | 2002-05-07 | 8:36 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Shut down for substation outage
41 | 2002-05-07 | 8:36 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Shut down for substation outage
42 | 2002-05-07 | 8:36 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Shut down for substation outage
43 | 2002-05-07 | 8:36 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21MW per line | Matt | Johnny | Shut down for substation outage
63 | 2002-05-06 | 16:45 | 2002-05-06 | 17:45 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
64 | 2002-05-06 | 16:45 | 2002-05-06 | 17:45 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
65 | 2002-05-06 | 16:45 | 2002-05-06 | 17:45 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
66 | 2002-05-06 | 16:45 | 2002-05-06 | 17:45 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
67 | 2002-05-06 | 16:45 | 2002-05-06 | 17:45 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
68 | 2002-05-06 | 16:45 | 2002-05-07 | 0:05 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
69 | 2002-05-06 | 16:45 | 2002-05-07 | 0:05 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
70 | 2002-05-06 | 16:45 | 2002-05-07 | 0:05 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
71 | 2002-05-06 | 16:45 | 2002-05-07 | 0:05 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
72 | 2002-05-06 | 16:45 | 2002-05-07 | 2:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Art | Oomed to 20 MW per line- low wind
73 | 2002-05-06 | 16:45 | 2002-05-07 | 2:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Art | Oomed to 20 MW per line- low wind
74 | 2002-05-06 | 16:45 | 2002-05-07 | 2:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Art | Oomed to 20 MW per line- low wind
75 | 2002-05-06 | 16:45 | 2002-05-07 | 2:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Art | Oomed to 20 MW per line- low wind
76 | 2002-05-06 | 16:45 | 2002-05-07 | 2:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Art | Oomed to 20 MW per line- low wind
77 | 2002-05-06 | 16:45 | 2002-05-07 | 2:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Art | Oomed to 20 MW per line- low wind
78 | 2002-05-06 | 16:45 | 2002-05-07 | 2:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Art | Oomed to 20 MW per line- low wind
79 | 2002-05-06 | 16:45 | 2002-05-07 | 2:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Art | Oomed to 20 MW per line- low wind
80 | 2002-05-06 | 16:45 | 2002-05-07 | 4:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Art | Raised to 30 MW
81 | 2002-05-06 | 16:45 | 2002-05-07 | 4:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Art | Raised to 30 MW
82 | 2002-05-06 | 16:45 | 2002-05-07 | 4:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Art | Raised to 30 MW
83 | 2002-05-06 | 16:45 | 2002-05-07 | 4:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Art | Raised to 30 MW
84 | 2002-05-06 | 16:45 | 2002-05-07 | 4:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Art | Raised to 30 MW
85 | 2002-05-06 | 16:45 | 2002-05-07 | 4:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Art | Raised to 30 MW
86 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Released to full power
87 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Released to full power
88 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Released to full power
89 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Released to full power
90 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Released to full power
91 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Released to full power
92 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Released to full power
93 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Released to full power
96 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Released to full power
100 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Released to full power
102 | 2002-05-06 | 18:20 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Released to full power
103 | 2002-05-06 | 18:20 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Released to full power
104 | 2002-05-06 | 18:30 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Released to full power
1 | 2002-05-06 | 16:45 | 2002-05-06 | 17:45 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
2 | 2002-05-06 | 16:45 | 2002-05-06 | 17:45 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
3 | 2002-05-06 | 16:45 | 2002-05-06 | 17:45 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
4 | 2002-05-06 | 16:45 | 2002-05-06 | 17:45 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
5 | 2002-05-06 | 16:45 | 2002-05-06 | 17:45 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
7 | 2002-05-06 | 16:45 | 2002-05-07 | 0:05 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
8 | 2002-05-06 | 16:45 | 2002-05-07 | 0:05 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
9 | 2002-05-06 | 16:45 | 2002-05-07 | 0:05 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
13 | 2002-05-06 | 16:45 | 2002-05-07 | 0:05 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
14 | 2002-05-06 | 16:45 | 2002-05-07 | 0:05 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
15 | 2002-05-06 | 16:45 | 2002-05-07 | 2:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
17 | 2002-05-06 | 16:45 | 2002-05-07 | 2:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
18 | 2002-05-06 | 16:45 | 2002-05-07 | 2:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
19 | 2002-05-06 | 16:45 | 2002-05-07 | 2:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
20 | 2002-05-06 | 16:45 | 2002-05-07 | 2:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
21 | 2002-05-06 | 16:45 | 2002-05-07 | 2:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
22 | 2002-05-06 | 16:45 | 2002-05-07 | 2:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
23 | 2002-05-06 | 16:45 | 2002-05-07 | 2:00 | Charlie | Roger | Oomed to 20 MW per line | Charlie | Roger | Oomed to 20 MW per line- low wind
24 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
25 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
26 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
27 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
28 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
29 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
30 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
31 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
32 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
34 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
35 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
36 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
37 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
38 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
39 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
40 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
41 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
42 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
43 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
44 | 2002-05-06 | 16:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
45 | 2002-05-06 | 18:30 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
46 | 2002-05-06 | 18:30 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
47 | 2002-05-06 | 18:30 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
49 | 2002-05-06 | 18:40 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
114 | 2002-05-06 | 18:40 | 2002-05-07 | 6:50 | Charlie | Roger | Oomed to 10 MW per line | Tootie | Art | Oom released
115 | 2002-05-06 | 18:40 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 10 MW per line | Tootie | Art | Oom released
116 | 2002-05-06 | 18:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 10 MW per line | Tootie | Art | Oom released
50 | 2002-05-06 | 18:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 10 MW per line | Tootie | Art | Oom released
51 | 2002-05-06 | 18:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 10 MW per line | Tootie | Art | Oom released
52 | 2002-05-06 | 18:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 10 MW per line | Tootie | Art | Oom released
54 | 2002-05-06 | 18:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 10 MW per line | Tootie | Art | Oom released
55 | 2002-05-06 | 18:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 10 MW per line | Tootie | Art | Oom released
57 | 2002-05-06 | 19:25 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 10 MW per line | Tootie | Art | Oom released
58 | 2002-05-06 | 19:25 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 10 MW per line | Tootie | Art | Oom released
59 | 2002-05-06 | 20:00 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 10 MW per line | Tootie | Art | Oom released
1 | 2002-05-06 | 20:40 | 2002-05-07 | 0:05 | Charlie | Art | Oomed to 10 MW per line | Charlie | Roger | Raised to 20 MW
2 | 2002-05-07 | 0:45 | 2002-05-07 | 0:05 | Charlie | Art | Oomed to 7 MW per line | Charlie | Roger | Raised to 20 MW
3 | 2002-05-07 | 0:45 | 2002-05-07 | 0:05 | Charlie | Art | Oomed to 7 MW per line | Charlie | Roger | Raised to 20 MW
4 | 2002-05-07 | 0:45 | 2002-05-07 | 0:05 | Charlie | Art | Oomed to 7 MW per line | Charlie | Roger | Raised to 20 MW
5 | 2002-05-07 | 0:45 | 2002-05-07 | 0:05 | Charlie | Art | Oomed to 7 MW per line | Charlie | Roger | Raised to 20 MW
7 | 2002-05-07 | 0:45 | 2002-05-07 | 0:05 | Charlie | Art | Oomed to 7 MW per line | Charlie | Roger | Raised to 20 MW
8 | 2002-05-07 | 0:45 | 2002-05-07 | 0:05 | Charlie | Art | Oomed to 7 MW per line | Charlie | Roger | Raised to 20 MW
9 | 2002-05-07 | 0:45 | 2002-05-07 | 0:05 | Charlie | Art | Oomed to 7 MW per line | Charlie | Roger | Raised to 20 MW
23 | 2002-05-07 | 6:50 | 2002-05-07 | 7:30 | Charlie | Art | Oomed to 7 MW per line | Tootie | Art | Oom released
105 | 2002-05-06 | 18:30 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
106 | 2002-05-06 | 18:30 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
107 | 2002-05-06 | 18:30 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 20 MW per line | Tootie | Art | Oom released
108 | 2002-05-06 | 18:40 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 10 MW per line | Tootie | Art | Oom released
109 | 2002-05-06 | 18:40 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 10 MW per line | Tootie | Art | Oom released
120 | 2002-05-06 | 18:40 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 10 MW per line | Tootie | Art | Oom released
113 | 2002-05-06 | 18:40 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 10 MW per line | Tootie | Art | Oom released
117 | 2002-05-06 | 18:40 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 10 MW per line | Tootie | Art | Oom released
118 | 2002-05-06 | 18:40 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 10 MW per line | Tootie | Art | Oom released
119 | 2002-05-06 | 18:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 10 MW per line | Tootie | Art | Oom released
121 | 2002-05-06 | 18:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 10 MW per line | Tootie | Art | Oom released
122 | 2002-05-06 | 18:45 | 2002-05-07 | 7:30 | Charlie | Roger | Oomed to 10 MW per line | Tootie | Art | Oom released
63 | 2002-05-07 | 0:45 | 2002-05-07 | 7:30 | Charlie | Art | Oomed to 20 MW per line | Tootie | Art | Oom released
64 | 2002-05-07 | 0:45 | 2002-05-07 | 7:30 | Charlie | Art | Oomed to 20 MW per line | Tootie | Art | Oom released
65 | 2002-05-07 | 0:45 | 2002-05-07 | 7:30 | Charlie | Art | Oomed to 20 MW per line | Tootie | Art | Oom released
66 | 2002-05-07 | 0:45 | 2002-05-07 | 7:30 | Charlie | Art | Oomed to 20 MW per line | Tootie | Art | Oom released
67 | 2002-05-07 | 0:45 | 2002-05-07 | 7:30 | Charlie | Art | Oomed to 20 MW per line | Tootie | Art | Oom released
68 | 2002-05-07 | 0:45 | 2002-05-07 | 7:30 | Charlie | Art | Oomed to 20 MW per line | Tootie | Art | Oom released
69 | 2002-05-07 | 0:45 | 2002-05-07 | 7:30 | Charlie | Art | Oomed to 20 MW per line | Tootie | Art | Oom released
70 | 2002-05-07 | 0:45 | 2002-05-07 | 7:30 | Charlie | Art | Oomed to 20 MW per line | Tootie | Art | Oom released
67 | 2002-05-06 | 14:00 | 2002-05-07 | 0:05 | Charlie | Roger | Curtailed to 10 MW per line | Charlie | Roger | Raised to 20 MW
66 | 2002-05-06 | 14:00 | 2002-05-07 | 0:05 | Charlie | Roger | Curtailed to 10 MW per line | Charlie | Roger | Raised to 20 MW
1 | 2002-05-07 | 8:07 | 2002-05-07 | 8:24 | Tootie | Art | Oomed to 21 MW per line | Tootie | Art | Oomed to 21 MW per line
2 | 2002-05-07 | 8:07 | 2002-05-07 | 8:24 | Tootie | Art | Oomed to 21 MW per line | Tootie | Art | Oomed to 21 MW per line
3 | 2002-05-07 | 8:07 | 2002-05-07 | 8:24 | Tootie | Art | Oomed to 21 MW per line | Tootie | Art | Oomed to 21 MW per line
4 | 2002-05-07 | 8:07 | 2002-05-07 | 8:24 | Tootie | Art | Oomed to 21 MW per line | Tootie | Art | Oomed to 21 MW per line
5 | 2002-05-07 | 8:07 | 2002-05-07 | 8:24 | Tootie | Art | Oomed to 21 MW per line | Tootie | Art | Oomed to 21 MW per line
7 | 2002-05-07 | 8:07 | 2002-05-07 | 8:29 | Tootie | Art | Oomed to 21 MW per line | Tootie | Art | Oomed to 21 MW per line
14 | 2002-05-07 | 8:07 | 2002-05-07 | 8:29 | Tootie | Art | Oomed to 21 MW per line | Tootie | Art | Oomed to 21 MW per line
15 | 2002-05-07 | 8:07 | 2002-05-07 | 8:29 | Tootie | Art | Oomed to 21 MW per line | Tootie | Art | Oomed to 21 MW per line
17 | 2002-05-07 | 8:07 | 2002-05-07 | 8:29 | Tootie | Art | Oomed to 21 MW per line | Tootie | Art | Oomed to 21 MW per line
18 | 2002-05-07 | 8:07 | 2002-05-07 | 8:29 | Tootie | Art | Oomed to 21 MW per line | Tootie | Art | Oomed to 21 MW per line
19 | 2002-05-07 | 8:07 | 2002-05-07 | 8:29 | Tootie | Art | Oomed to 21 MW per line | Tootie | Art | Oomed to 21 MW per line
20 | 2002-05-07 | 8:07 | 2002-05-07 | 8:29 | Tootie | Art | Oomed to 21 MW per line | Tootie | Art | Oomed to 21 MW per line
21 | 2002-05-07 | 8:07 | 2002-05-07 | 8:29 | Tootie | Art | Oomed to 21 MW per line | Tootie | Art | Oomed to 21 MW per line
22 | 2002-05-07 | 8:07 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21 MW per line | Matt | Johnny | Shut down for substation outage
23 | 2002-05-07 | 8:07 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21 MW per line | Matt | Johnny | Shut down for substation outage
24 | 2002-05-07 | 8:07 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21 MW per line | Matt | Johnny | Shut down for substation outage
25 | 2002-05-07 | 8:07 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21 MW per line | Matt | Johnny | Shut down for substation outage
26 | 2002-05-07 | 8:07 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21 MW per line | Matt | Johnny | Shut down for substation outage
27 | 2002-05-07 | 8:07 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21 MW per line | Matt | Johnny | Shut down for substation outage
28 | 2002-05-07 | 8:07 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21 MW per line | Matt | Johnny | Shut down for substation outage
29 | 2002-05-07 | 8:07 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21 MW per line | Matt | Johnny | Shut down for substation outage
30 | 2002-05-07 | 8:07 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21 MW per line | Matt | Johnny | Shut down for substation outage
32 | 2002-05-07 | 8:07 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21 MW per line | Matt | Johnny | Shut down for substation outage
33 | 2002-05-07 | 8:07 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21 MW per line | Matt | Johnny | Shut down for substation outage
34 | 2002-05-07 | 8:07 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21 MW per line | Matt | Johnny | Shut down for substation outage
35 | 2002-05-07 | 8:07 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21 MW per line | Matt | Johnny | Shut down for substation outage
36 | 2002-05-07 | 8:07 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21 MW per line | Matt | Johnny | Shut down for substation outage
63 | 2002-05-07 | 8:16 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
64 | 2002-05-07 | 8:16 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
65 | 2002-05-07 | 8:16 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
66 | 2002-05-07 | 8:16 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
68 | 2002-05-07 | 8:16 | 2002-05-07 | 9:25 | Tootie | Art | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
65 | 2002-05-07 | 14:00 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Charlie | Gilbert | Oomed to 21 MW per line
64 | 2002-05-07 | 14:00 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Charlie | Gilbert | Oomed to 21 MW per line
63 | 2002-05-07 | 14:00 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Charlie | Gilbert | Oomed to 21 MW per line
69 | 2002-05-07 | 14:00 | 2002-05-08 | 8:01 | Matt | Johnny | Oomed to 21 MW per line | Charlie | Gilbert | Oomed to 21 MW per line
70 | 2002-05-07 | 14:00 | 2002-05-07 | 23:50 | Matt | Johnny | Oomed to 21 MW per line | Charlie | Gilbert | Oomed to 21 MW per line
71 | 2002-05-07 | 14:00 | 2002-05-07 | 23:50 | Matt | Johnny | Oomed to 21 MW per line | Charlie | Gilbert | Oomed to 21 MW per line
72 | 2002-05-07 | 14:00 | 2002-05-07 | 23:50 | Matt | Johnny | Oomed to 21 MW per line | Charlie | Gilbert | Oomed to 21 MW per line
54 | 2002-05-07 | 14:00 | 2002-05-07 | 21:00 | Matt | Johnny | Oomed to 21 MW per line | Charlie | Gilbert | Oomed to 21 MW per line
57 | 2002-05-07 | 14:12 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
58 | 2002-05-07 | 14:12 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
59 | 2002-05-07 | 14:12 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
73 | 2002-05-07 | 14:15 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
74 | 2002-05-07 | 14:15 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
75 | 2002-05-07 | 14:15 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
76 | 2002-05-07 | 14:15 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
77 | 2002-05-07 | 14:15 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
78 | 2002-05-07 | 14:15 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
79 | 2002-05-07 | 14:15 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
80 | 2002-05-07 | 14:15 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
47 | 2002-05-07 | 14:15 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
46 | 2002-05-07 | 14:15 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
1 | 2002-05-07 | 14:30 | 2002-05-08 | 7:49 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
2 | 2002-05-07 | 14:30 | 2002-05-08 | 7:49 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
3 | 2002-05-07 | 14:30 | 2002-05-08 | 7:49 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
4 | 2002-05-07 | 14:30 | 2002-05-08 | 8:08 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
5 | 2002-05-07 | 14:30 | 2002-05-08 | 8:08 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
7 | 2002-05-07 | 14:30 | 2002-05-08 | 8:08 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
8 | 2002-05-07 | 14:30 | 2002-05-08 | 8:08 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
9 | 2002-05-07 | 14:30 | 2002-05-08 | 8:08 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
13 | 2002-05-07 | 14:30 | 2002-05-08 | 8:08 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
14 | 2002-05-07 | 14:30 | 2002-05-08 | 8:24 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
15 | 2002-05-07 | 14:30 | 2002-05-08 | 8:24 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
17 | 2002-05-07 | 14:30 | 2002-05-08 | 8:24 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
18 | 2002-05-07 | 14:30 | 2002-05-08 | 8:24 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
19 | 2002-05-07 | 14:30 | 2002-05-08 | 8:24 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
20 | 2002-05-07 | 14:30 | 2002-05-08 | 8:24 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
57 | 2002-05-07 | 10:30 | 2002-05-07 | 11:05 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
58 | 2002-05-07 | 10:30 | 2002-05-07 | 11:05 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
59 | 2002-05-07 | 10:30 | 2002-05-07 | 11:05 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
115 | 2002-05-07 | 10:30 | 2002-05-07 | 11:55 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
116 | 2002-05-07 | 10:30 | 2002-05-07 | 11:55 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
41 | 2002-05-07 | 11:56 | 2002-05-07 | 12:20 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
42 | 2002-05-07 | 11:56 | 2002-05-07 | 12:20 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
43 | 2002-05-07 | 11:56 | 2002-05-07 | 12:20 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
44 | 2002-05-07 | 11:56 | 2002-05-07 | 12:20 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
45 | 2002-05-07 | 11:56 | 2002-05-07 | 12:20 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
46 | 2002-05-07 | 11:56 | 2002-05-07 | 12:20 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
47 | 2002-05-07 | 11:56 | 2002-05-07 | 12:20 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
40 | 2002-05-07 | 12:05 | 2002-05-07 | 12:20 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
39 | 2002-05-07 | 12:05 | 2002-05-07 | 12:20 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
38 | 2002-05-07 | 12:05 | 2002-05-07 | 12:20 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
21 | 2002-05-07 | 12:05 | 2002-05-07 | 12:20 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
22 | 2002-05-07 | 12:05 | 2002-05-07 | 12:20 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
23 | 2002-05-07 | 12:05 | 2002-05-07 | 12:20 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
24 | 2002-05-07 | 12:05 | 2002-05-07 | 12:20 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
25 | 2002-05-07 | 12:05 | 2002-05-07 | 12:20 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
26 | 2002-05-07 | 12:05 | 2002-05-07 | 12:20 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
32 | 2002-05-07 | 12:25 | 2002-05-07 | 12:40 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
33 | 2002-05-07 | 12:25 | 2002-05-07 | 12:40 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
34 | 2002-05-07 | 12:25 | 2002-05-07 | 12:40 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
35 | 2002-05-07 | 12:25 | 2002-05-07 | 12:40 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
36 | 2002-05-07 | 12:25 | 2002-05-07 | 12:40 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
37 | 2002-05-07 | 12:25 | 2002-05-07 | 12:40 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
30 | 2002-05-07 | 12:25 | 2002-05-07 | 12:40 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
29 | 2002-05-07 | 12:25 | 2002-05-07 | 12:40 | Matt | Johnny | Oomed to 21 MW per line | Matt | Johnny | Oomed to 21 MW per line
49 | 2002-05-07 | 13:30 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
50 | 2002-05-07 | 13:30 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
51 | 2002-05-07 | 13:30 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
52 | 2002-05-07 | 13:30 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
55 | 2002-05-07 | 13:30 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
68 | 2002-05-07 | 14:00 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
60 | 2002-05-07 | 14:00 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
81 | 2002-05-07 | 14:30 | 2002-05-08 | 3:45 | Matt | Johnny | Oomed to 21 MW per line | Charlie | Gilbert | Oomed to 21 MW per line
82 | 2002-05-07 | 14:30 | 2002-05-08 | 3:45 | Matt | Johnny | Oomed to 21 MW per line | Charlie | Gilbert | Oomed to 21 MW per line
83 | 2002-05-07 | 14:40 | 2002-05-08 | 3:45 | Matt | Johnny | Oomed to 21 MW per line | Charlie | Gilbert | Oomed to 21 MW per line
84 | 2002-05-07 | 14:40 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
85 | 2002-05-07 | 14:40 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
86 | 2002-05-07 | 14:40 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
87 | 2002-05-07 | 14:40 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
32 | 2002-05-07 | 14:40 | 2002-05-08 | 5:50 | Matt | Johnny | Oomed to 21 MW per line | Charlie | Gilbert | Oomed to 21 MW per line
33 | 2002-05-07 | 14:40 | 2002-05-08 | 5:50 | Matt | Johnny | Oomed to 21 MW per line | Charlie | Gilbert | Oomed to 21 MW per line
34 | 2002-05-07 | 14:40 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
35 | 2002-05-07 | 14:40 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
36 | 2002-05-07 | 14:40 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
37 | 2002-05-07 | 14:40 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
88 | 2002-05-07 | 14:45 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
89 | 2002-05-07 | 14:45 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
90 | 2002-05-07 | 14:45 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
91 | 2002-05-07 | 14:45 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
92 | 2002-05-07 | 14:45 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
45 | 2002-05-07 | 14:45 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
44 | 2002-05-07 | 14:45 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
38 | 2002-05-07 | 14:50 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
39 | 2002-05-07 | 14:50 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
93 | 2002-05-07 | 15:03 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
96 | 2002-05-07 | 15:03 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
40 | 2002-05-07 | 15:40 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
41 | 2002-05-07 | 15:40 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
42 | 2002-05-07 | 15:40 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
43 | 2002-05-07 | 15:40 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
100 | 2002-05-07 | 15:40 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
102 | 2002-05-07 | 15:45 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
103 | 2002-05-07 | 15:45 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
104 | 2002-05-07 | 15:45 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
105 | 2002-05-08 | 2:05 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
106 | 2002-05-08 | 2:05 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
107 | 2002-05-08 | 2:05 | 2002-05-08 | 8:44 | Matt | Johnny | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
21 | 2002-05-08 | 2:10 | 2002-05-08 | 8:24 | Charlie | Gilbert | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
22 | 2002-05-08 | 2:10 | 2002-05-08 | 8:24 | Charlie | Gilbert | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
23 | 2002-05-08 | 2:10 | 2002-05-08 | 8:24 | Charlie | Gilbert | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
69 | 2002-05-08 | 8:21 | 2002-05-08 | 8:44 | Tootie | Gilbert | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
70 | 2002-05-08 | 8:21 | 2002-05-08 | 8:44 | Tootie | Gilbert | Oomed to 21 MW per line | Tootie | Gilbert | Oomed to 21 MW per line
63 | 2002-05-08 | 18:50 | 2002-05-08 | 19:45 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
64 | 2002-05-08 | 18:50 | 2002-05-08 | 19:45 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
65 | 2002-05-08 | 18:50 | 2002-05-08 | 19:45 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
66 | 2002-05-08 | 18:50 | 2002-05-08 | 19:45 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
67 | 2002-05-08 | 18:50 | 2002-05-08 | 19:45 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
68 | 2002-05-08 | 18:50 | 2002-05-08 | 19:45 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
69 | 2002-05-08 | 18:50 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
70 | 2002-05-08 | 18:50 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
71 | 2002-05-08 | 18:50 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
72 | 2002-05-08 | 18:50 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
73 | 2002-05-08 | 18:50 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
74 | 2002-05-08 | 18:50 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
75 | 2002-05-08 | 18:50 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
76 | 2002-05-08 | 18:50 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
77 | 2002-05-08 | 18:50 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
78 | 2002-05-08 | 18:50 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
79 | 2002-05-08 | 18:50 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
80 | 2002-05-08 | 18:50 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
81 | 2002-05-08 | 18:50 | 2002-05-08 | 20:15 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
82 | 2002-05-08 | 18:50 | 2002-05-08 | 20:15 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
83 | 2002-05-08 | 18:50 | 2002-05-08 | 20:15 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
84 | 2002-05-08 | 18:50 | 2002-05-08 | 20:15 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
85 | 2002-05-08 | 18:50 | 2002-05-08 | 20:15 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
86 | 2002-05-08 | 18:50 | 2002-05-08 | 20:15 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
87 | 2002-05-08 | 18:50 | 2002-05-08 | 20:15 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
1 | 2002-05-08 | 18:45 | 2002-05-08 | 19:25 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
2 | 2002-05-08 | 18:45 | 2002-05-08 | 19:25 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
3 | 2002-05-08 | 18:45 | 2002-05-08 | 19:25 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
4 | 2002-05-08 | 18:45 | 2002-05-08 | 19:25 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
5 | 2002-05-08 | 18:45 | 2002-05-08 | 19:25 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
7 | 2002-05-08 | 18:45 | 2002-05-08 | 19:25 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
8 | 2002-05-08 | 18:45 | 2002-05-08 | 19:25 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
9 | 2002-05-08 | 18:45 | 2002-05-08 | 19:25 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
13 | 2002-05-08 | 18:45 | 2002-05-08 | 19:25 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
14 | 2002-05-08 | 18:45 | 2002-05-08 | 19:25 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
15 | 2002-05-08 | 18:45 | 2002-05-08 | 19:25 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
17 | 2002-05-08 | 18:45 | 2002-05-08 | 19:25 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
18 | 2002-05-08 | 18:45 | 2002-05-08 | 19:25 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
19 | 2002-05-08 | 18:45 | 2002-05-08 | 19:25 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
20 | 2002-05-08 | 18:45 | 2002-05-08 | 19:25 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
21 | 2002-05-08 | 18:45 | 2002-05-08 | 19:25 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
22 | 2002-05-08 | 18:45 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
23 | 2002-05-08 | 18:45 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
24 | 2002-05-08 | 18:45 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
25 | 2002-05-08 | 18:45 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
26 | 2002-05-08 | 18:45 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
27 | 2002-05-08 | 18:45 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
28 | 2002-05-08 | 18:45 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
29 | 2002-05-08 | 18:45 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
30 | 2002-05-08 | 18:45 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
32 | 2002-05-08 | 18:45 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
33 | 2002-05-08 | 18:45 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
34 | 2002-05-08 | 18:45 | 2002-05-08 | 20:00 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
35 | 2002-05-08 | 18:45 | 2002-05-08 | 20:30 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
36 | 2002-05-08 | 18:45 | 2002-05-08 | 20:30 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
37 | 2002-05-08 | 18:45 | 2002-05-08 | 20:30 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
38 | 2002-05-08 | 18:45 | 2002-05-08 | 20:40 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
39 | 2002-05-08 | 18:45 | 2002-05-08 | 20:40 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
40 | 2002-05-08 | 18:45 | 2002-05-08 | 20:40 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
41 | 2002-05-08 | 18:45 | 2002-05-08 | 20:40 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
63 | 2002-05-08 | 20:50 | 2002-05-08 | 21:45 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
64 | 2002-05-08 | 20:50 | 2002-05-08 | 21:45 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
65 | 2002-05-08 | 20:50 | 2002-05-08 | 21:45 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
66 | 2002-05-08 | 20:50 | 2002-05-08 | 21:45 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
67 | 2002-05-08 | 20:50 | 2002-05-08 | 21:45 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
68 | 2002-05-08 | 20:50 | 2002-05-08 | 22:10 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
69 | 2002-05-08 | 20:55 | 2002-05-08 | 22:10 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
70 | 2002-05-08 | 20:55 | 2002-05-08 | 22:10 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
71 | 2002-05-08 | 20:55 | 2002-05-08 | 22:10 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
72 | 2002-05-08 | 20:55 | 2002-05-08 | 22:10 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
73 | 2002-05-08 | 20:55 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
74 | 2002-05-08 | 20:55 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
75 | 2002-05-08 | 20:55 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
76 | 2002-05-08 | 20:55 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
77 | 2002-05-08 | 20:55 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
78 | 2002-05-08 | 20:55 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
79 | 2002-05-08 | 20:55 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
80 | 2002-05-08 | 20:55 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
81 | 2002-05-08 | 20:55 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
82 | 2002-05-08 | 20:55 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
83 | 2002-05-08 | 20:55 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
84 | 2002-05-08 | 20:55 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
85 | 2002-05-08 | 20:55 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
1 | 2002-05-08 | 21:10 | 2002-05-08 | 22:10 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
2 | 2002-05-08 | 21:10 | 2002-05-08 | 22:10 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
3 | 2002-05-08 | 21:10 | 2002-05-08 | 22:10 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
4 | 2002-05-08 | 21:10 | 2002-05-08 | 22:10 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
5 | 2002-05-08 | 21:10 | 2002-05-08 | 22:10 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
7 | 2002-05-08 | 21:10 | 2002-05-08 | 22:40 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
8 | 2002-05-08 | 21:10 | 2002-05-08 | 22:40 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
9 | 2002-05-08 | 21:10 | 2002-05-08 | 22:40 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
13 | 2002-05-08 | 21:10 | 2002-05-08 | 22:40 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
14 | 2002-05-08 | 21:10 | 2002-05-08 | 22:40 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
15 | 2002-05-08 | 21:10 | 2002-05-08 | 22:40 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
17 | 2002-05-08 | 21:10 | 2002-05-08 | 22:40 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
18 | 2002-05-08 | 21:10 | 2002-05-08 | 22:40 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
19 | 2002-05-08 | 21:10 | 2002-05-08 | 22:40 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
20 | 2002-05-08 | 21:10 | 2002-05-08 | 22:40 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
21 | 2002-05-08 | 21:10 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
22 | 2002-05-08 | 21:10 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
23 | 2002-05-08 | 21:10 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
24 | 2002-05-08 | 21:10 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
25 | 2002-05-08 | 21:10 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
26 | 2002-05-08 | 21:10 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
27 | 2002-05-08 | 21:10 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
28 | 2002-05-08 | 21:10 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
29 | 2002-05-08 | 21:10 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
30 | 2002-05-08 | 21:45 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
32 | 2002-05-08 | 21:45 | 2002-05-08 | 22:50 | Charlie | Art | Oomed to 21 MW per line | Charlie | Art | Oomed to 21 MW per line
63 | 2002-05-09 | 5:00 | 2002-05-09 | 7:20 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
64 | 2002-05-09 | 5:00 | 2002-05-09 | 7:20 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
65 | 2002-05-09 | 5:00 | 2002-05-09 | 7:20 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
66 | 2002-05-09 | 5:00 | 2002-05-09 | 7:20 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
67 | 2002-05-09 | 5:00 | 2002-05-09 | 7:20 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
68 | 2002-05-09 | 5:00 | 2002-05-09 | 7:20 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
69 | 2002-05-09 | 5:00 | 2002-05-09 | 7:20 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
70 | 2002-05-09 | 5:00 | 2002-05-09 | 7:25 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
71 | 2002-05-09 | 5:00 | 2002-05-09 | 7:25 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
72 | 2002-05-09 | 5:00 | 2002-05-09 | 7:25 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
73 | 2002-05-09 | 5:00 | 2002-05-09 | 7:25 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
74 | 2002-05-09 | 5:00 | 2002-05-09 | 7:25 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
75 | 2002-05-09 | 5:00 | 2002-05-09 | 7:25 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
76 | 2002-05-09 | 5:00 | 2002-05-09 | 7:25 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
77 | 2002-05-09 | 5:40 | 2002-05-09 | 7:25 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
78 | 2002-05-09 | 5:40 | 2002-05-09 | 7:25 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
79 | 2002-05-09 | 5:40 | 2002-05-09 | 7:30 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
80 | 2002-05-09 | 5:40 | 2002-05-09 | 7:30 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
81 | 2002-05-09 | 5:40 | 2002-05-09 | 7:30 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
82 | 2002-05-09 | 5:55 | 2002-05-09 | 7:30 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
83 | 2002-05-09 | 5:55 | 2002-05-09 | 7:30 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
84 | 2002-05-09 | 5:55 | 2002-05-09 | 7:30 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
85 | 2002-05-09 | 5:55 | 2002-05-09 | 7:30 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
86 | 2002-05-09 | 6:15 | 2002-05-09 | 7:30 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
87 | 2002-05-09 | 6:15 | 2002-05-09 | 7:30 | Kevin | Buck | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
1 | 2002-05-09 | 4:30 | 2002-05-09 | 7:15 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
2 | 2002-05-09 | 4:30 | 2002-05-09 | 7:15 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
3 | 2002-05-09 | 4:30 | 2002-05-09 | 7:15 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
4 | 2002-05-09 | 4:30 | 2002-05-09 | 7:15 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
5 | 2002-05-09 | 4:30 | 2002-05-09 | 7:15 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
7 | 2002-05-09 | 4:30 | 2002-05-09 | 7:20 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
8 | 2002-05-09 | 4:30 | 2002-05-09 | 7:20 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
9 | 2002-05-09 | 4:30 | 2002-05-09 | 7:35 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
13 | 2002-05-09 | 4:30 | 2002-05-09 | 7:35 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
14 | 2002-05-09 | 4:30 | 2002-05-09 | 7:35 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
15 | 2002-05-09 | 4:30 | 2002-05-09 | 7:35 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
17 | 2002-05-09 | 4:30 | 2002-05-09 | 7:35 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
18 | 2002-05-09 | 5:15 | 2002-05-09 | 7:35 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
19 | 2002-05-09 | 5:15 | 2002-05-09 | 7:35 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
20 | 2002-05-09 | 5:15 | 2002-05-09 | 7:40 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
21 | 2002-05-09 | 5:15 | 2002-05-09 | 7:40 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
22 | 2002-05-09 | 5:45 | 2002-05-09 | 7:40 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
23 | 2002-05-09 | 5:45 | 2002-05-09 | 7:40 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
24 | 2002-05-09 | 5:45 | 2002-05-09 | 7:40 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
25 | 2002-05-09 | 5:45 | 2002-05-09 | 7:40 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
26 | 2002-05-09 | 5:45 | 2002-05-09 | 7:40 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
27 | 2002-05-09 | 5:45 | 2002-05-09 | 7:40 | Charlie | Art | Oomed to 21 MW per line | Kevin | Buck | Oomed to 21 MW per line
105 | 2002-05-09 | 20:30 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
104 | 2002-05-09 | 20:30 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
103 | 2002-05-09 | 20:30 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
102 | 2002-05-09 | 20:30 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
113 | 2002-05-09 | 20:30 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
109 | 2002-05-09 | 20:30 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
96 | 2002-05-09 | 20:30 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
119 | 2002-05-09 | 20:30 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
120 | 2002-05-09 | 21:00 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
118 | 2002-05-09 | 21:00 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
59 | 2002-05-09 | 10:13 | 2002-05-09 | 11:57 | Tootie | Buck | Oomed to 21 MW per line | Tootie | Buck | Oomed to 21 MW per line
58 | 2002-05-09 | 10:13 | 2002-05-09 | 11:57 | Tootie | Buck | Oomed to 21 MW per line | Tootie | Buck | Oomed to 21 MW per line
57 | 2002-05-09 | 10:13 | 2002-05-09 | 11:57 | Tootie | Buck | Oomed to 21 MW per line | Tootie | Buck | Oomed to 21 MW per line
55 | 2002-05-09 | 10:13 | 2002-05-09 | 11:57 | Tootie | Buck | Oomed to 21 MW per line | Tootie | Buck | Oomed to 21 MW per line
49 | 2002-05-09 | 10:13 | 2002-05-09 | 12:02 | Tootie | Buck | Oomed to 21 MW per line | Tootie | Buck | Oomed to 21 MW per line
47 | 2002-05-09 | 10:13 | 2002-05-09 | 12:02 | Tootie | Buck | Oomed to 21 MW per line | Tootie | Buck | Oomed to 21 MW per line
52 | 2002-05-09 | 10:13 | 2002-05-09 | 12:02 | Tootie | Buck | Oomed to 21 MW per line | Tootie | Buck | Oomed to 21 MW per line
51 | 2002-05-09 | 10:13 | 2002-05-09 | 12:02 | Tootie | Buck | Oomed to 21 MW per line | Tootie | Buck | Oomed to 21 MW per line
50 | 2002-05-09 | 10:13 | 2002-05-09 | 12:02 | Tootie | Buck | Oomed to 21 MW per line | Tootie | Buck | Oomed to 21 MW per line
46 | 2002-05-09 | 10:13 | 2002-05-09 | 12:06 | Tootie | Buck | Oomed to 21 MW per line | Tootie | Buck | Oomed to 21 MW per line
45 | 2002-05-09 | 10:13 | 2002-05-09 | 12:06 | Tootie | Buck | Oomed to 21 MW per line | Tootie | Buck | Oomed to 21 MW per line
44 | 2002-05-09 | 10:13 | 2002-05-09 | 12:06 | Tootie | Buck | Oomed to 21 MW per line | Tootie | Buck | Oomed to 21 MW per line
43 | 2002-05-09 | 10:13 | 2002-05-09 | 12:06 | Tootie | Buck | Oomed to 21 MW per line | Tootie | Buck | Oomed to 21 MW per line
42 | 2002-05-09 | 10:21 | 2002-05-09 | 12:06 | Tootie | Buck | Oomed to 21 MW per line | Tootie | Buck | Oomed to 21 MW per line
41 | 2002-05-09 | 10:21 | 2002-05-09 | 12:06 | Tootie | Buck | Oomed to 21 MW per line | Tootie | Buck | Oomed to 21 MW per line
40 | 2002-05-09 | 10:21 | 2002-05-09 | 12:06 | Tootie | Buck | Oomed to 21 MW per line | Tootie | Buck | Oomed to 21 MW per line
39 | 2002-05-09 | 10:21 | 2002-05-09 | 12:06 | Tootie | Buck | Oomed to 21 MW per line | Tootie | Buck | Oomed to 21 MW per line
29 | 2002-05-09 | 20:00 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
30 | 2002-05-09 | 20:00 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
49 | 2002-05-09 | 20:00 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
50 | 2002-05-09 | 20:00 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
51 | 2002-05-09 | 20:00 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
55 | 2002-05-09 | 20:00 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
57 | 2002-05-09 | 20:00 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
58 | 2002-05-09 | 20:00 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
59 | 2002-05-09 | 20:00 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
32 | 2002-05-09 | 20:00 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
33 | 2002-05-09 | 20:00 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
34 | 2002-05-09 | 20:00 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
35 | 2002-05-09 | 20:00 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
36 | 2002-05-09 | 20:00 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
37 | 2002-05-09 | 20:00 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
38 | 2002-05-09 | 20:00 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
39 | 2002-05-09 | 20:00 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
21 | 2002-05-09 | 20:00 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
22 | 2002-05-09 | 21:00 | 2002-05-09 | 22:00 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Gilbert | Oomed to 21 MW per line
47 | 2002-05-10 | 6:30 | 2002-05-10 | 21:30 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
46 | 2002-05-10 | 6:30 | 2002-05-10 | 21:30 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
45 | 2002-05-10 | 6:30 | 2002-05-10 | 21:30 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
44 | 2002-05-10 | 6:30 | 2002-05-10 | 21:30 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
43 | 2002-05-10 | 6:30 | 2002-05-10 | 21:30 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
42 | 2002-05-10 | 6:30 | 2002-05-10 | 21:30 | Bryan | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
29 | 2002-05-10 | 7:30 | 2002-05-10 | 21:30 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
30 | 2002-05-10 | 7:30 | 2002-05-10 | 21:30 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
32 | 2002-05-10 | 7:30 | 2002-05-10 | 21:30 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
33 | 2002-05-10 | 7:30 | 2002-05-10 | 21:30 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
34 | 2002-05-10 | 7:30 | 2002-05-10 | 21:30 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
35 | 2002-05-10 | 7:30 | 2002-05-10 | 21:30 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
36 | 2002-05-10 | 7:30 | 2002-05-10 | 21:30 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
37 | 2002-05-10 | 7:30 | 2002-05-10 | 21:30 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
38 | 2002-05-10 | 7:30 | 2002-05-10 | 21:30 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
39 | 2002-05-10 | 7:30 | 2002-05-10 | 21:30 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
40 | 2002-05-10 | 7:30 | 2002-05-10 | 21:30 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
41 | 2002-05-10 | 7:30 | 2002-05-10 | 21:30 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
64 | 2002-05-10 | 8:25 | 2002-05-10 | 21:30 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
63 | 2002-05-10 | 8:25 | 2002-05-10 | 21:30 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
65 | 2002-05-10 | 8:25 | 2002-05-10 | 21:30 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
66 | 2002-05-10 | 8:25 | 2002-05-10 | 21:30 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
67 | 2002-05-10 | 9:56 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
68 | 2002-05-10 | 9:56 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
69 | 2002-05-10 | 9:56 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
70 | 2002-05-10 | 9:56 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
71 | 2002-05-10 | 9:56 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
72 | 2002-05-10 | 9:56 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
73 | 2002-05-10 | 9:56 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
74 | 2002-05-10 | 10:00 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
75 | 2002-05-10 | 10:00 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
76 | 2002-05-10 | 10:00 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
77 | 2002-05-10 | 10:00 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
78 | 2002-05-10 | 10:00 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
79 | 2002-05-10 | 10:00 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
80 | 2002-05-10 | 10:00 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
81 | 2002-05-10 | 10:00 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
82 | 2002-05-10 | 10:00 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
83 | 2002-05-10 | 10:00 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
84 | 2002-05-10 | 10:09 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
85 | 2002-05-10 | 10:09 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
86 | 2002-05-10 | 10:09 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
87 | 2002-05-10 | 10:09 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
47 | 2002-05-10 | 10:16 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
50 | 2002-05-10 | 10:16 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
51 | 2002-05-10 | 10:16 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
52 | 2002-05-10 | 10:16 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
88 | 2002-05-10 | 10:16 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
89 | 2002-05-10 | 10:16 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
90 | 2002-05-10 | 10:16 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
55 | 2002-05-10 | 10:19 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
56 | 2002-05-10 | 10:02 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
57 | 2002-05-10 | 10:25 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
58 | 2002-05-10 | 10:26 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
93 | 2002-05-10 | 10:26 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
96 | 2002-05-10 | 10:32 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
59 | 2002-05-10 | 10:35 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
1 | 2002-05-10 | 10:35 | 2002-05-10 | 17:00 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
2 | 2002-05-10 | 10:39 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
3 | 2002-05-10 | 10:39 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
4 | 2002-05-10 | 10:00 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
5 | 2002-05-10 | 11:03 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
7 | 2002-05-10 | 11:08 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
8 | 2002-05-10 | 11:20 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
9 | 2002-05-10 | 11:20 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
13 | 2002-05-10 | 11:20 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
14 | 2002-05-10 | 11:55 | 2002-05-10 | 21:30 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
91 | 2002-05-10 | 12:46 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
93 | 2002-05-10 | 12:46 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
96 | 2002-05-10 | 12:46 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
100 | 2002-05-10 | 12:46 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
102 | 2002-05-10 | 12:46 | 2002-05-10 | 13:18 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
15 | 2002-05-10 | 12:48 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
17 | 2002-05-10 | 12:48 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
103 | 2002-05-10 | 13:05 | 2002-05-10 | 13:12 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
104 | 2002-05-10 | 13:05 | 2002-05-10 | 13:12 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
115 | 2002-05-10 | 13:05 | 2002-05-10 | 21:30 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
114 | 2002-05-10 | 13:05 | 2002-05-10 | 21:30 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
102 | 2002-05-10 | 13:50 | 2002-05-10 | 21:30 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
18 | 2002-05-10 | 13:50 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
103 | 2002-05-10 | 14:05 | 2002-05-10 | 21:30 | Tootie | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
104 | 2002-05-10 | 14:25 | 2002-05-10 | 21:30 | Matt | Gilbert | Oomed to 21 MW per line | Bryan | Buck | Oomed to 21 MW per line
55 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
56 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
57 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
58 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
59 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
1 | 2002-05-10 | 22:00 | 2002-05-12 | 9:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
4 | 2002-05-10 | 22:00 | 2002-05-11 | 1:30 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
5 | 2002-05-10 | 22:00 | 2002-05-12 | 8:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
7 | 2002-05-10 | 22:00 | 2002-05-12 | 8:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
8 | 2002-05-10 | 22:00 | 2002-05-12 | 8:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
9 | 2002-05-10 | 22:00 | 2002-05-12 | 8:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
13 | 2002-05-10 | 22:00 | 2002-05-12 | 8:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
14 | 2002-05-10 | 22:00 | 2002-05-12 | 8:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
15 | 2002-05-10 | 22:00 | 2002-05-12 | 8:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
17 | 2002-05-10 | 22:00 | 2002-05-12 | 8:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
18 | 2002-05-10 | 22:00 | 2002-05-12 | 8:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
19 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
20 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
23 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
24 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
25 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
26 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
27 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
28 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
33 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
34 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
35 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
36 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
37 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
38 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
39 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
41 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
42 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
43 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
44 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
45 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
46 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
47 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
50 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
52 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
54 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
65 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
67 | 2002-05-10 | 22:00 | 2002-05-11 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
69 | 2002-05-10 | 22:00 | 2002-05-11 | 1:30 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
70 | 2002-05-10 | 22:00 | 2002-05-12 | 1:30 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
71 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
72 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
74 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
75 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
76 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
77 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
78 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
82 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
83 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
84 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
85 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
86 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
87 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
89 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
90 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
91 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
93 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
96 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
100 | 2002-05-10 | 22:00 | 2002-05-12 | 10:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
102 | 2002-05-10 | 22:00 | 2002-05-12 | 9:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
103 | 2002-05-10 | 22:00 | 2002-05-12 | 9:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
104 | 2002-05-10 | 22:00 | 2002-05-12 | 9:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
105 | 2002-05-10 | 22:00 | 2002-05-12 | 9:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
106 | 2002-05-10 | 22:00 | 2002-05-12 | 9:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
107 | 2002-05-10 | 22:00 | 2002-05-12 | 9:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
120 | 2002-05-10 | 22:00 | 2002-05-12 | 8:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
117 | 2002-05-10 | 22:00 | 2002-05-12 | 8:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
118 | 2002-05-10 | 22:00 | 2002-05-12 | 8:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
121 | 2002-05-10 | 22:00 | 2002-05-12 | 8:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
122 | 2002-05-10 | 22:00 | 2002-05-12 | 8:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
88 | 2002-05-10 | 22:00 | 2002-05-13 | 8:00 | Bryan | Ben | Oomed to 21 MW per line | John | Ben | Oomed to 21 MW per line
122 | 2002-05-12 | 19:00 | 2002-05-13 | 6:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
121 | 2002-05-12 | 19:00 | 2002-05-13 | 6:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
119 | 2002-05-12 | 19:00 | 2002-05-13 | 6:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
118 | 2002-05-12 | 19:00 | 2002-05-13 | 6:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
117 | 2002-05-12 | 20:00 | 2002-05-13 | 6:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
120 | 2002-05-12 | 20:00 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
109 | 2002-05-12 | 20:00 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
108 | 2002-05-12 | 20:00 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
106 | 2002-05-12 | 20:00 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
105 | 2002-05-12 | 20:00 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
104 | 2002-05-12 | 20:00 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
103 | 2002-05-12 | 20:00 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
102 | 2002-05-12 | 20:00 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
100 | 2002-05-12 | 20:00 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
96 | 2002-05-12 | 20:00 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
93 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
92 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
91 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
90 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
89 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
88 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
87 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
86 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
85 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
84 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
83 | 2002-05-12 | 20:30 | 2002-05-13 | 6:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
82 | 2002-05-12 | 20:30 | 2002-05-13 | 6:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
81 | 2002-05-12 | 20:30 | 2002-05-13 | 6:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
80 | 2002-05-12 | 20:30 | 2002-05-13 | 6:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
79 | 2002-05-12 | 20:30 | 2002-05-13 | 6:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
78 | 2002-05-12 | 20:30 | 2002-05-13 | 6:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
77 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
15 | 2002-05-13 | 2:30 | 2002-05-13 | 5:30 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
1 | 2002-05-12 | 19:00 | 2002-05-13 | 5:30 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
2 | 2002-05-12 | 19:00 | 2002-05-13 | 5:30 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
3 | 2002-05-12 | 19:00 | 2002-05-13 | 6:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
4 | 2002-05-12 | 19:00 | 2002-05-13 | 6:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
5 | 2002-05-12 | 19:00 | 2002-05-13 | 6:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
7 | 2002-05-12 | 19:00 | 2002-05-13 | 4:30 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
8 | 2002-05-12 | 19:00 | 2002-05-13 | 4:30 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
9 | 2002-05-12 | 19:00 | 2002-05-13 | 4:30 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
13 | 2002-05-12 | 19:00 | 2002-05-13 | 6:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
14 | 2002-05-12 | 19:00 | 2002-05-13 | 6:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
15 | 2002-05-12 | 19:00 | 2002-05-13 | 6:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
17 | 2002-05-12 | 19:00 | 2002-05-13 | 6:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
18 | 2002-05-12 | 19:00 | 2002-05-13 | 6:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
19 | 2002-05-12 | 19:00 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
20 | 2002-05-12 | 19:00 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
21 | 2002-05-12 | 19:00 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
22 | 2002-05-12 | 19:00 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
114 | 2002-05-12 | 19:00 | 2002-05-13 | 6:00 | Bryan | Ben | Oomed to 21 MW per line | Bryan | Ben | Oomed to 21 MW per line
23 | 2002-05-12 | 20:00 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
24 | 2002-05-12 | 20:00 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
26 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
25 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
27 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
28 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
29 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
30 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
32 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
33 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
34 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
35 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
36 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
37 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
38 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
39 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
40 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
41 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
42 | 2002-05-12 | 20:30 | 2002-05-13 | 7:20 | Bryan | Ben | Oomed to 21 MW per line | Matt | Ben | Oomed to 21 MW per line
63 | 2002-05-14 | 6:40 | 2002-05-14 | 9:40 | Charlie | Gilbert | Oomed to 21 MW per line | Tootie | Art | Oomed to 21 MW per line
64 | 2002-05-14 | 6:40 | 2002-05-14 | 9:40 | Charlie | Gilbert | Oomed to 21 MW per line | Tootie | Art | Oomed to 21 MW per line
65 | 2002-05-14 | 6:40 | 2002-05-14 | 9:40 | Charlie | Gilbert | Oomed to 21 MW per line | Tootie | Art | Oomed to 21 MW per line
66 | 2002-05-14 | 6:40 | 2002-05-14 | 9:40 | Charlie | Gilbert | Oomed to 21 MW per line | Tootie | Art | Oomed to 21 MW per line
67 | 2002-05-14 | 6:40 | 2002-05-14 | 9:00 | Charlie | Gilbert | Oomed to 21 MW per line | Tootie | Art | Oomed to 21 MW per line
68 | 2002-05-14 | 6:40 | 2002-05-14 | 9:00 | Charlie | Gilbert | Oomed to 21 MW per line | Tootie | Art | Oomed to 21 MW per line
1 | 2002-05-14 | 7:00 | 2002-05-14 | 9:25 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
2 | 2002-05-14 | 7:00 | 2002-05-14 | 9:25 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
3 | 2002-05-14 | 7:00 | 2002-05-14 | 9:25 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
4 | 2002-05-14 | 7:00 | 2002-05-14 | 9:25 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
5 | 2002-05-14 | 7:00 | 2002-05-14 | 9:25 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
38 | 2002-05-14 | 7:00 | 2002-05-14 | 9:14 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
39 | 2002-05-14 | 7:00 | 2002-05-14 | 9:20 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
40 | 2002-05-14 | 7:00 | 2002-05-14 | 9:20 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
41 | 2002-05-14 | 7:00 | 2002-05-14 | 9:20 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
42 | 2002-05-14 | 7:00 | 2002-05-14 | 9:20 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
43 | 2002-05-14 | 7:00 | 2002-05-14 | 9:20 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
44 | 2002-05-14 | 7:00 | 2002-05-14 | 8:25 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
45 | 2002-05-14 | 7:00 | 2002-05-14 | 8:25 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
46 | 2002-05-14 | 7:00 | 2002-05-14 | 8:25 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
47 | 2002-05-14 | 7:00 | 2002-05-14 | 8:25 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
48 | 2002-05-14 | 7:00 | 2002-05-14 | 8:25 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
49 | 2002-05-14 | 7:00 | 2002-05-14 | 8:25 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
50 | 2002-05-14 | 7:00 | 2002-05-14 | 9:01 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
69 | 2002-05-14 | 7:07 | 2002-05-14 | 9:01 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
73 | 2002-05-14 | 7:07 | 2002-05-14 | 9:01 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
74 | 2002-05-14 | 7:07 | 2002-05-14 | 9:01 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
75 | 2002-05-14 | 7:07 | 2002-05-14 | 9:01 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
76 | 2002-05-14 | 7:07 | 2002-05-14 | 8:35 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
77 | 2002-05-14 | 7:07 | 2002-05-14 | 8:35 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
79 | 2002-05-14 | 7:07 | 2002-05-14 | 8:35 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
80 | 2002-05-14 | 7:07 | 2002-05-14 | 8:35 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
81 | 2002-05-14 | 7:07 | 2002-05-14 | 8:35 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
82 | 2002-05-14 | 7:07 | 2002-05-14 | 8:35 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
83 | 2002-05-14 | 7:07 | 2002-05-14 | 8:35 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
84 | 2002-05-14 | 7:07 | 2002-05-14 | 8:33 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
85 | 2002-05-14 | 7:07 | 2002-05-14 | 8:33 | Tootie | Art | OO'med to 10 MW per line | Tootie | Art | OO'med to 10 MW per line
1 | 2002-05-14 | 4:55 | 2002-05-14 | 6:25 | Charlie | Gilbert | OO'med to 21MW per line | Charlie | Gilbert | OO'med to 21MW per line
2 | 2002-05-14 | 4:55 | 2002-05-14 | 6:25 | Charlie | Gilbert | OO'med to 21MW per line | Charlie | Gilbert | OO'med to 21MW per line
3 | 2002-05-14 | 4:55 | 2002-05-14 | 6:25 | Charlie | Gilbert | OO'med to 21MW per line | Charlie | Gilbert | OO'med to 21MW per line
4 | 2002-05-14 | 4:55 | 2002-05-14 | 6:25 | Charlie | Gilbert | OO'med to 21MW per line | Charlie | Gilbert | OO'med to 21MW per line
5 | 2002-05-14 | 4:55 | 2002-05-14 | 6:25 | Charlie | Gilbert | OO'med to 21MW per line | Charlie | Gilbert | OO'med to 21MW per line
7 | 2002-05-14 | 4:55 | 2002-05-14 | 7:15 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
8 | 2002-05-14 | 4:55 | 2002-05-14 | 7:15 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
9 | 2002-05-14 | 4:55 | 2002-05-14 | 7:15 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
13 | 2002-05-14 | 4:55 | 2002-05-14 | 7:15 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
14 | 2002-05-14 | 4:55 | 2002-05-14 | 8:59 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
15 | 2002-05-14 | 4:55 | 2002-05-14 | 8:59 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
17 | 2002-05-14 | 4:55 | 2002-05-14 | 8:59 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
18 | 2002-05-14 | 4:55 | 2002-05-14 | 8:59 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
19 | 2002-05-14 | 4:55 | 2002-05-14 | 8:59 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
20 | 2002-05-14 | 4:55 | 2002-05-14 | 8:59 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
21 | 2002-05-14 | 5:35 | 2002-05-14 | 9:04 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
22 | 2002-05-14 | 5:35 | 2002-05-14 | 9:04 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
23 | 2002-05-14 | 5:35 | 2002-05-14 | 9:04 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
24 | 2002-05-14 | 5:35 | 2002-05-14 | 9:04 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
25 | 2002-05-14 | 5:35 | 2002-05-14 | 9:04 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
26 | 2002-05-14 | 5:55 | 2002-05-14 | 9:04 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
27 | 2002-05-14 | 5:55 | 2002-05-14 | 9:04 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
28 | 2002-05-14 | 5:55 | 2002-05-14 | 9:04 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
29 | 2002-05-14 | 5:55 | 2002-05-14 | 9:09 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
30 | 2002-05-14 | 5:55 | 2002-05-14 | 9:09 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
32 | 2002-05-14 | 6:05 | 2002-05-14 | 9:09 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
33 | 2002-05-14 | 6:05 | 2002-05-14 | 9:09 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
34 | 2002-05-14 | 6:05 | 2002-05-14 | 9:09 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
35 | 2002-05-14 | 6:05 | 2002-05-14 | 9:14 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
36 | 2002-05-14 | 6:40 | 2002-05-14 | 9:14 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
37 | 2002-05-14 | 6:40 | 2002-05-14 | 9:14 | Charlie | Gilbert | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
122 | 2002-05-14 | 8:44 | 2002-05-14 | 9:12 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
121 | 2002-05-14 | 8:44 | 2002-05-14 | 9:12 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
117 | 2002-05-14 | 8:45 | 2002-05-14 | 9:12 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
118 | 2002-05-14 | 8:45 | 2002-05-14 | 9:12 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
119 | 2002-05-14 | 8:45 | 2002-05-14 | 9:12 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
113 | 2002-05-14 | 8:48 | 2002-05-14 | 9:07 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
120 | 2002-05-14 | 8:48 | 2002-05-14 | 9:07 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
109 | 2002-05-14 | 8:48 | 2002-05-14 | 9:07 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
107 | 2002-05-14 | 8:50 | 2002-05-14 | 9:07 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
106 | 2002-05-14 | 8:50 | 2002-05-14 | 9:07 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
105 | 2002-05-14 | 8:50 | 2002-05-14 | 9:07 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
104 | 2002-05-14 | 8:50 | 2002-05-14 | 9:07 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
86 | 2002-05-14 | 7:12 | 2002-05-14 | 8:29 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
87 | 2002-05-14 | 7:12 | 2002-05-14 | 8:29 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
88 | 2002-05-14 | 7:12 | 2002-05-14 | 8:29 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
89 | 2002-05-14 | 7:12 | 2002-05-14 | 8:29 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
90 | 2002-05-14 | 7:12 | 2002-05-14 | 8:23 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
91 | 2002-05-14 | 7:12 | 2002-05-14 | 8:23 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
92 | 2002-05-14 | 7:18 | 2002-05-14 | 8:23 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
93 | 2002-05-14 | 7:18 | 2002-05-14 | 7:37 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
96 | 2002-05-14 | 7:18 | 2002-05-14 | 7:37 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
100 | 2002-05-14 | 7:18 | 2002-05-14 | 7:30 | Tootie | Art | OO'med to 21MW per line | Kevin | Art | OO'med to 21MW per line
102 | 2002-05-14 | 7:18 | 2002-05-14 | 7:30 | Tootie | Art | OO'med to 21MW per line | Kevin | Art | OO'med to 21MW per line
93 | 2002-05-14 | 7:42 | 2002-05-14 | 8:23 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
96 | 2002-05-14 | 7:42 | 2002-05-14 | 8:23 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
100 | 2002-05-14 | 7:42 | 2002-05-14 | 8:23 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
102 | 2002-05-14 | 7:42 | 2002-05-14 | 8:23 | Tootie | Art | OO'med to 21MW per line | Tootie | Art | OO'med to 21MW per line
53 | 2002-05-14 | 9:48 | 2002-05-14 | 9:56 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Maintain 20 MW per line
54 | 2002-05-14 | 9:48 | 2002-05-14 | 9:56 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Maintain 20MW per line
55 | 2002-05-14 | 9:48 | 2002-05-14 | 11:17 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Maintain 20MW per line
56 | 2002-05-14 | 9:48 | 2002-05-14 | 11:17 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Maintain 20MW per line
57 | 2002-05-14 | 9:48 | 2002-05-14 | 11:17 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Maintain 20MW per line
58 | 2002-05-14 | 9:48 | 2002-05-14 | 11:17 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Maintain 20MW per line
59 | 2002-05-14 | 9:48 | 2002-05-14 | 11:17 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Maintain 20MW per line
51 | 2002-05-14 | 9:50 | 2002-05-14 | 11:28 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Maintain 20MW per line
52 | 2002-05-14 | 9:50 | 2002-05-14 | 11:28 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Maintain 20MW per line
49 | 2002-05-14 | 9:58 | 2002-05-14 | 11:28 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Maintain 20MW per line
50 | 2002-05-14 | 9:58 | 2002-05-14 | 11:28 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Maintain 20MW per line
46 | 2002-05-14 | 9:58 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
47 | 2002-05-14 | 9:58 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
49 | 2002-05-14 | 9:58 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
68 | 2002-05-14 | 9:58 | 2002-05-14 | 11:10 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
69 | 2002-05-14 | 9:58 | 2002-05-14 | 10:30 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Maintain 20MW per line
71 | 2002-05-14 | 9:58 | 2002-05-14 | 10:30 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Maintain 20MW per line
73 | 2002-05-14 | 9:58 | 2002-05-14 | 10:30 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Maintain 20MW per line
74 | 2002-05-14 | 9:58 | 2002-05-14 | 11:14 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Maintain 20MW per line
75 | 2002-05-14 | 9:58 | 2002-05-14 | 11:14 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Maintain 20MW per line
76 | 2002-05-14 | 9:58 | 2002-05-14 | 11:14 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Maintain 20MW per line
77 | 2002-05-14 | 9:58 | 2002-05-14 | 11:14 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
41 | 2002-05-14 | 9:58 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
42 | 2002-05-14 | 9:58 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
43 | 2002-05-14 | 9:58 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
44 | 2002-05-14 | 9:58 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
45 | 2002-05-14 | 9:58 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
40 | 2002-05-14 | 9:58 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
78 | 2002-05-14 | 10:04 | 2002-05-14 | 11:14 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
38 | 2002-05-14 | 10:06 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
39 | 2002-05-14 | 10:06 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
34 | 2002-05-14 | 10:11 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
35 | 2002-05-14 | 10:11 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
36 | 2002-05-14 | 10:11 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
37 | 2002-05-14 | 10:11 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
81 | 2002-05-14 | 10:20 | 2002-05-14 | 14:17 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
82 | 2002-05-14 | 10:20 | 2002-05-14 | 14:17 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Curtailment lifted
83 | 2002-05-14 | 10:20 | 2002-05-14 | 14:17 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Curtailment lifted
84 | 2002-05-14 | 10:20 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
85 | 2002-05-14 | 10:20 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
86 | 2002-05-14 | 10:20 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
87 | 2002-05-14 | 10:20 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
88 | 2002-05-14 | 10:20 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
89 | 2002-05-14 | 10:30 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
90 | 2002-05-14 | 10:30 | 2002-05-14 | 11:22 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Curtailment lifted
32 | 2002-05-14 | 10:34 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
33 | 2002-05-14 | 10:34 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
91 | 2002-05-14 | 10:34 | 2002-05-14 | 11:22 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Curtailment lifted
92 | 2002-05-14 | 10:34 | 2002-05-14 | 11:22 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Curtailment lifted
27 | 2002-05-14 | 10:38 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
28 | 2002-05-14 | 10:38 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
29 | 2002-05-14 | 10:38 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
30 | 2002-05-14 | 10:38 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
22 | 2002-05-14 | 10:38 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
25 | 2002-05-14 | 10:38 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
24 | 2002-05-14 | 10:38 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
90 | 2002-05-14 | 12:24 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
91 | 2002-05-14 | 12:24 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
92 | 2002-05-14 | 12:24 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
93 | 2002-05-14 | 12:24 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
96 | 2002-05-14 | 12:24 | 2002-05-14 | 14:17 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Curtailment lifted
100 | 2002-05-14 | 12:24 | 2002-05-14 | 14:17 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Curtailment lifted
102 | 2002-05-14 | 12:24 | 2002-05-14 | 14:17 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Curtailment lifted
103 | 2002-05-14 | 12:24 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
104 | 2002-05-14 | 12:24 | 2002-05-14 | 14:17 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Curtailment lifted
105 | 2002-05-14 | 12:24 | 2002-05-14 | 14:17 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Curtailment lifted
106 | 2002-05-14 | 12:24 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
107 | 2002-05-14 | 12:24 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
17 | 2002-05-14 | 12:24 | 2002-05-14 | 14:33 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Curtailment lifted
18 | 2002-05-14 | 12:24 | 2002-05-14 | 14:33 | Tootie | Art | OO'med to 20 MW per line | Tootie | Art | Curtailment lifted
19 | 2002-05-14 | 12:24 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
20 | 2002-05-14 | 12:24 | 2002-05-14 | 20:00 | Tootie | Art | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
21 | 2002-05-14 | 12:27 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
22 | 2002-05-14 | 12:27 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
23 | 2002-05-14 | 12:27 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Tootie | Ben | Curtailment lifted
109 | 2002-05-14 | 13:15 | 2002-05-14 | 14:17 | Tootie | Ben | OO'med to 20 MW per line | Tootie | Ben | Curtailment lifted
120 | 2002-05-14 | 13:15 | 2002-05-14 | 14:17 | Tootie | Ben | OO'med to 20 MW per line | Tootie | Ben | Curtailment lifted
113 | 2002-05-14 | 13:15 | 2002-05-14 | 14:17 | Tootie | Ben | OO'med to 20 MW per line | Tootie | Ben | Curtailment lifted
117 | 2002-05-14 | 13:21 | 2002-05-14 | 15:25 | Tootie | Ben | OO'med to 20 MW per line | Tootie | Ben | Curtailment lifted
114 | 2002-05-14 | 13:43 | 2002-05-14 | 15:25 | Tootie | Ben | OO'med to 20 MW per line | Tootie | Ben | Curtailment lifted
115 | 2002-05-14 | 13:43 | 2002-05-14 | 15:25 | Tootie | Ben | OO'med to 20 MW per line | Tootie | Ben | Curtailment lifted
119 | 2002-05-14 | 14:20 | 2002-05-14 | 14:26 | Tootie | Ben | OO'med to 20 MW per line | Tootie | Ben | Curtailment lifted
121 | 2002-05-14 | 14:20 | 2002-05-14 | 15:25 | Tootie | Ben | OO'med to 20 MW per line | Tootie | Ben | Curtailment lifted
122 | 2002-05-14 | 14:20 | 2002-05-14 | 15:25 | Tootie | Ben | OO'med to 20 MW per line | Tootie | Ben | Curtailment lifted
68 | 2002-05-14 | 14:20 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
69 | 2002-05-14 | 14:20 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
71 | 2002-05-14 | 14:20 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
73 | 2002-05-14 | 14:20 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
74 | 2002-05-14 | 14:20 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
75 | 2002-05-14 | 14:20 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
76 | 2002-05-14 | 14:20 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
77 | 2002-05-14 | 14:20 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
1 | 2002-05-14 | 14:33 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
3 | 2002-05-14 | 14:33 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
4 | 2002-05-14 | 15:20 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
78 | 2002-05-14 | 15:50 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
79 | 2002-05-14 | 15:50 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
80 | 2002-05-14 | 15:50 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
81 | 2002-05-14 | 16:07 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
82 | 2002-05-14 | 16:07 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
83 | 2002-05-14 | 16:10 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
49 | 2002-05-14 | 16:14 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
50 | 2002-05-14 | 16:14 | 2002-05-14 | 20:00 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Buck | Curtailment lifted
96 | 2002-05-14 | 17:50 | 2002-05-14 | 20:00 | Charlie | Buck | OO'med to 25 MW per line | Charlie | Buck | Curtailment lifted
100 | 2002-05-14 | 17:50 | 2002-05-14 | 20:00 | Charlie | Buck | OO'med to 25 MW per line | Charlie | Buck | Curtailment lifted
102 | 2002-05-14 | 18:30 | 2002-05-14 | 20:00 | Charlie | Buck | OO'med to 25 MW per line | Charlie | Buck | Curtailment lifted
104 | 2002-05-14 | 18:30 | 2002-05-14 | 20:00 | Charlie | Buck | OO'med to 25 MW per line | Charlie | Buck | Curtailment lifted
105 | 2002-05-14 | 18:30 | 2002-05-14 | 20:00 | Charlie | Buck | OO'med to 25 MW per line | Charlie | Buck | Curtailment lifted
1 | 2002-05-15 | 18:45 | 2002-05-15 | 22:20 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | Released to 50 MW per line
2 | 2002-05-15 | 18:45 | 2002-05-15 | 22:20 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | Released to 50 MW per line
3 | 2002-05-15 | 18:45 | 2002-05-15 | 23:00 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | Released to 50 MW per line
4 | 2002-05-15 | 18:45 | 2002-05-15 | 23:00 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | Released to 50 MW per line
5 | 2002-05-15 | 18:45 | 2002-05-15 | 23:00 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | Released to 50 MW per line
7 | 2002-05-15 | 18:45 | 2002-05-15 | 23:00 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | Released to 50 MW per line
8 | 2002-05-15 | 18:45 | 2002-05-15 | 23:00 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | Released to 50 MW per line
9 | 2002-05-15 | 18:45 | 2002-05-15 | 23:00 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | Released to 50 MW per line
13 | 2002-05-15 | 18:45 | 2002-05-15 | 23:00 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | Released to 50 MW per line
14 | 2002-05-15 | 18:45 | 2002-05-15 | 23:00 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | Released to 50 MW per line
15 | 2002-05-15 | 18:45 | 2002-05-15 | 23:00 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | Released to 50 MW per line
17 | 2002-05-15 | 18:45 | 2002-05-15 | 23:00 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | Released to 50 MW per line
18 | 2002-05-15 | 18:45 | 2002-05-15 | 23:00 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | Released to 50 MW per line
19 | 2002-05-15 | 18:45 | 2002-05-16 | 5:35 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | Released to 50 MW per line
20 | 2002-05-15 | 18:45 | 2002-05-16 | 5:35 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | Released to 50 MW per line
21 | 2002-05-15 | 18:45 | 2002-05-16 | 5:35 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
22 | 2002-05-15 | 18:45 | 2002-05-16 | 5:35 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
23 | 2002-05-15 | 18:45 | 2002-05-16 | 5:35 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
24 | 2002-05-15 | 18:45 | 2002-05-16 | 5:35 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
25 | 2002-05-15 | 18:45 | 2002-05-16 | 5:40 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
26 | 2002-05-15 | 18:45 | 2002-05-16 | 5:40 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
27 | 2002-05-15 | 18:45 | 2002-05-16 | 5:40 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
28 | 2002-05-15 | 18:45 | 2002-05-16 | 5:40 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
29 | 2002-05-15 | 18:45 | 2002-05-16 | 5:40 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
30 | 2002-05-15 | 18:45 | 2002-05-16 | 5:40 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
32 | 2002-05-15 | 18:45 | 2002-05-16 | 5:45 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
33 | 2002-05-15 | 18:45 | 2002-05-16 | 5:45 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
34 | 2002-05-15 | 18:45 | 2002-05-16 | 5:45 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
35 | 2002-05-15 | 18:45 | 2002-05-16 | 9:02 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
36 | 2002-05-15 | 18:45 | 2002-05-16 | 9:02 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
37 | 2002-05-15 | 18:45 | 2002-05-16 | 9:02 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
38 | 2002-05-15 | 18:45 | 2002-05-16 | 9:02 | Charlie | Gilbert | OO'med to 30 MW per line | Tootie | Gilbert | OO'med down to 45 MW per line
39 | 2002-05-15 | 19:30 | 2002-05-16 | 9:05 | Charlie | Gilbert | OO'med to 30 MW per line | Tootie | Gilbert | OO'med down to 45 MW per line
40 | 2002-05-15 | 19:30 | 2002-05-16 | 9:05 | Charlie | Gilbert | OO'med to 30 MW per line | Tootie | Gilbert | OO'med down to 45 MW per line
41 | 2002-05-16 | 3:50 | 2002-05-16 | 9:05 | Charlie | Gilbert | OO'med to 30 MW per line | Tootie | Gilbert | OO'med down to 45 MW per line
42 | 2002-05-16 | 3:50 | 2002-05-16 | 9:05 | Charlie | Gilbert | OO'med to 30 MW per line | Tootie | Gilbert | OO'med down to 45 MW per line
63 | 2002-05-15 | 18:50 | 2002-05-15 | 22:20 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
64 | 2002-05-15 | 18:50 | 2002-05-15 | 22:20 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
65 | 2002-05-15 | 18:50 | 2002-05-15 | 23:05 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
66 | 2002-05-15 | 18:50 | 2002-05-15 | 23:05 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
68 | 2002-05-15 | 18:50 | 2002-05-15 | 23:05 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
69 | 2002-05-15 | 18:50 | 2002-05-15 | 23:05 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
71 | 2002-05-15 | 18:50 | 2002-05-15 | 23:05 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
73 | 2002-05-15 | 18:50 | 2002-05-15 | 23:05 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
74 | 2002-05-15 | 18:50 | 2002-05-15 | 23:05 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
75 | 2002-05-15 | 18:50 | 2002-05-15 | 23:05 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
76 | 2002-05-15 | 18:50 | 2002-05-15 | 23:05 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
77 | 2002-05-15 | 18:50 | 2002-05-16 | 5:40 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
78 | 2002-05-15 | 18:50 | 2002-05-16 | 5:40 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
79 | 2002-05-15 | 18:50 | 2002-05-16 | 5:40 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
80 | 2002-05-15 | 18:50 | 2002-05-16 | 5:40 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
81 | 2002-05-15 | 18:50 | 2002-05-16 | 5:40 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
82 | 2002-05-15 | 18:50 | 2002-05-16 | 5:40 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
83 | 2002-05-15 | 18:50 | 2002-05-16 | 5:45 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
84 | 2002-05-15 | 18:50 | 2002-05-16 | 5:45 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
85 | 2002-05-15 | 18:50 | 2002-05-16 | 5:45 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
86 | 2002-05-15 | 18:50 | 2002-05-16 | 5:45 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
87 | 2002-05-15 | 18:50 | 2002-05-16 | 5:45 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
88 | 2002-05-15 | 18:50 | 2002-05-16 | 5:45 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
89 | 2002-05-15 | 18:50 | 2002-05-16 | 5:45 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
90 | 2002-05-16 | 3:50 | 2002-05-16 | 5:45 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
91 | 2002-05-16 | 3:50 | 2002-05-16 | 5:45 | Charlie | Gilbert | OO'med to 30 MW per line | Charlie | Gilbert | OO'med down to 45 MW per line
69 | 2002-05-16 | 6:20 | 2002-05-16 | 8:42 | Matt | Gilbert | OO'med to 30 MW per line | Tootie | Gilbert | OO'med down to 45 MW per line
71 | 2002-05-16 | 6:20 | 2002-05-16 | 8:42 | Matt | Gilbert | OO'med to 45 MW per line | Tootie | Gilbert | OO'med down to 45 MW per line
73 | 2002-05-16 | 6:20 | 2002-05-16 | 9:04 | Matt | Gilbert | OO'med to 45 MW per line | Tootie | Gilbert | OO'med down to 45 MW per line
74 | 2002-05-16 | 6:20 | 2002-05-16 | 9:04 | Matt | Gilbert | OO'med to 45 MW per line | Tootie | Gilbert | OO'med down to 45 MW per line
68 | 2002-05-16 | 6:45 | 2002-05-16 | 8:42 | Matt | Gilbert | OO'med to 45 MW per line | Tootie | Gilbert | OO'med down to 45 MW per line
66 | 2002-05-16 | 6:45 | 2002-05-16 | 7:28 | Matt | Gilbert | OO'med to 45 MW per line | Tootie | Gilbert | OO'med down to 45 MW per line
65 | 2002-05-16 | 6:45 | 2002-05-16 | 7:28 | Matt | Gilbert | OO'med to 45 MW per line | Tootie | Gilbert | OO'med down to 45 MW per line
50 | 2002-05-16 | 7:58 | 2002-05-16 | 9:19 | Charlie | Gilbert | OO'med to 45 MW per line | Tootie | Gilbert | OO'med down to 45 MW per line
51 | 2002-05-16 | 7:58 | 2002-05-16 | 9:19 | Charlie | Gilbert | OO'med to 45 MW per line | Tootie | Gilbert | OO'med down to 45 MW per line
1 | 2002-05-15 | 4:40 | 2002-05-15 | 10:25 | Charlie | Buck | OO'med to 40 MW per line | Tootie | Roger | OOM lifted
2 | 2002-05-15 | 4:40 | 2002-05-15 | 10:25 | Charlie | Buck | OO'med to 40 MW per line | Tootie | Roger | OOM lifted
3 | 2002-05-15 | 4:40 | 2002-05-15 | 17:10 | Charlie | Buck | OO'med to 40 MW per line | Tootie | Roger | OOM lifted
4 | 2002-05-15 | 4:40 | 2002-05-15 | 13:17 | Charlie | Buck | OO'med to 40 MW per line | Tootie | Roger | OOM lifted
5 | 2002-05-15 | 4:40 | 2002-05-15 | 13:17 | Charlie | Buck | OO'med to 40 MW per line | Tootie | Roger | OOM lifted
7 | 2002-05-15 | 4:40 | 2002-05-15 | 13:37 | Charlie | Buck | OO'med to 40 MW per line | Tootie | Roger | OOM lifted
8 | 2002-05-15 | 4:40 | 2002-05-15 | 13:37 | Charlie | Buck | OO'med to 40 MW per line | Tootie | Roger | OOM lifted
9 | 2002-05-15 | 4:40 | 2002-05-15 | 17:10 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
13 | 2002-05-15 | 4:40 | 2002-05-15 | 17:10 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
14 | 2002-05-15 | 4:40 | 2002-05-15 | 17:10 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
15 | 2002-05-15 | 4:40 | 2002-05-15 | 17:10 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
17 | 2002-05-15 | 4:40 | 2002-05-15 | 17:10 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
18 | 2002-05-15 | 4:40 | 2002-05-15 | 17:10 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
19 | 2002-05-15 | 4:40 | 2002-05-15 | 17:10 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
20 | 2002-05-15 | 4:40 | 2002-05-15 | 17:10 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
21 | 2002-05-15 | 4:40 | 2002-05-15 | 17:10 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
22 | 2002-05-15 | 4:40 | 2002-05-15 | 17:10 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
23 | 2002-05-15 | 4:40 | 2002-05-15 | 17:10 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
24 | 2002-05-15 | 4:40 | 2002-05-15 | 17:10 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
25 | 2002-05-15 | 4:40 | 2002-05-15 | 17:10 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
26 | 2002-05-15 | 4:40 | 2002-05-15 | 17:10 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
27 | 2002-05-15 | 4:40 | 2002-05-15 | 17:10 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
28 | 2002-05-15 | 4:40 | 2002-05-15 | 17:10 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
29 | 2002-05-15 | 4:40 | 2002-05-15 | 17:10 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
30 | 2002-05-15 | 4:40 | 2002-05-15 | 17:10 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
32 | 2002-05-15 | 4:40 | 2002-05-15 | 17:10 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
33 | 2002-05-15 | 4:40 | 2002-05-15 | 17:10 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
34 | 2002-05-15 | 7:02 | 2002-05-15 | 15:51 | Tootie | Roger | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
1 | 2002-05-15 | 11:40 | 2002-05-15 | 17:15 | Tootie | Roger | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
35 | 2002-05-15 | 11:45 | 2002-05-15 | 17:15 | Tootie | Roger | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
36 | 2002-05-15 | 13:45 | 2002-05-15 | 17:15 | Tootie | Roger | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
37 | 2002-05-15 | 13:45 | 2002-05-15 | 17:15 | Tootie | Roger | OO'med to 40 MW per line | Charlie | Ben | OOM lifted
38 | 2002-05-15 | 15:52 | 2002-05-15 | 17:15 | Tootie | Roger | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
39 | 2002-05-15 | 15:52 | 2002-05-15 | 17:15 | Tootie | Roger | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
40 | 2002-05-15 | 15:52 | 2002-05-15 | 17:15 | Tootie | Roger | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
41 | 2002-05-15 | 15:52 | 2002-05-15 | 17:15 | Tootie | Roger | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
84 | 2002-05-15 | 14:25 | 2002-05-15 | 17:30 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
85 | 2002-05-15 | 14:25 | 2002-05-15 | 17:30 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
86 | 2002-05-15 | 14:25 | 2002-05-15 | 17:30 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
87 | 2002-05-15 | 14:25 | 2002-05-15 | 17:30 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
88 | 2002-05-15 | 14:25 | 2002-05-15 | 17:30 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
89 | 2002-05-15 | 14:25 | 2002-05-15 | 17:30 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
90 | 2002-05-15 | 14:25 | 2002-05-15 | 17:30 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
91 | 2002-05-15 | 15:02 | 2002-05-15 | 17:30 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
92 | 2002-05-15 | 15:02 | 2002-05-15 | 17:30 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
12 | 2002-05-15 | 15:49 | 2002-05-15 | 17:20 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
14 | 2002-05-15 | 15:49 | 2002-05-15 | 17:20 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
15 | 2002-05-15 | 15:49 | 2002-05-15 | 17:20 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
7 | 2002-05-15 | 15:49 | 2002-05-15 | 17:20 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
8 | 2002-05-15 | 15:49 | 2002-05-15 | 17:20 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
42 | 2002-05-15 | 15:54 | 2002-05-15 | 17:20 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
43 | 2002-05-15 | 15:54 | 2002-05-15 | 17:20 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
44 | 2002-05-15 | 15:54 | 2002-05-15 | 17:20 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
45 | 2002-05-15 | 15:54 | 2002-05-15 | 17:20 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
60 | 2002-05-15 | 15:57 | 2002-05-15 | 17:35 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
61 | 2002-05-15 | 15:57 | 2002-05-15 | 17:35 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
62 | 2002-05-15 | 15:57 | 2002-05-15 | 17:35 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
63 | 2002-05-15 | 15:57 | 2002-05-15 | 17:35 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
64 | 2002-05-15 | 15:57 | 2002-05-15 | 17:35 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
65 | 2002-05-15 | 15:57 | 2002-05-15 | 17:35 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
66 | 2002-05-15 | 15:57 | 2002-05-15 | 17:35 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
68 | 2002-05-15 | 15:57 | 2002-05-15 | 17:35 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
46 | 2002-05-15 | 15:57 | 2002-05-15 | 17:25 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
47 | 2002-05-15 | 15:57 | 2002-05-15 | 17:25 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
69 | 2002-05-15 | 15:57 | 2002-05-15 | 17:30 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
107 | 2002-05-15 | 16:00 | 2002-05-15 | 17:30 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
93 | 2002-05-15 | 16:00 | 2002-05-15 | 17:30 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
119 | 2002-05-15 | 16:03 | 2002-05-15 | 17:30 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
118 | 2002-05-15 | 16:04 | 2002-05-15 | 17:30 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
49 | 2002-05-15 | 16:05 | 2002-05-15 | 17:25 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
50 | 2002-05-15 | 16:05 | 2002-05-15 | 17:25 | Tootie | Ben | OO'med to 20 MW per line | Charlie | Ben | OOM lifted
86 | 2002-05-14 | 18:30 | 2002-05-14 | 20:00 | Charlie | Buck | OO'med to 25 MW per line | Charlie | Buck | OOM lifted
2 | 2002-05-14 | 18:30 | 2002-05-14 | 20:00 | Charlie | Buck | OO'med to 25 MW per line | Charlie | Buck | OOM lifted
8 | 2002-05-14 | 18:30 | 2002-05-14 | 20:00 | Charlie | Buck | OO'med to 25 MW per line | Charlie | Buck | OOM lifted
9 | 2002-05-14 | 18:30 | 2002-05-14 | 20:00 | Charlie | Buck | OO'med to 25 MW per line | Charlie | Buck | OOM lifted
13 | 2002-05-14 | 18:30 | 2002-05-14 | 20:00 | Charlie | Buck | OO'med to 25 MW per line | Charlie | Buck | OOM lifted
14 | 2002-05-14 | 18:30 | 2002-05-14 | 20:00 | Charlie | Buck | OO'med to 25 MW per line | Charlie | Buck | OOM lifted
15 | 2002-05-14 | 18:30 | 2002-05-14 | 20:00 | Charlie | Buck | OO'med to 25 MW per line | Charlie | Buck | OOM lifted
17 | 2002-05-14 | 18:30 | 2002-05-14 | 20:00 | Charlie | Buck | OO'med to 25 MW per line | Charlie | Buck | OOM lifted
109 | 2002-05-14 | 18:30 | 2002-05-14 | 20:00 | Charlie | Buck | OO'med to 25 MW per line | Charlie | Buck | OOM lifted
1 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
2 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
3 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
4 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
5 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
7 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
8 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
9 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
13 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
14 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
15 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
17 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
18 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
19 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
20 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
21 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
22 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
23 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
24 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
25 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
26 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
27 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
28 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
29 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
30 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
32 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
33 | 2002-05-14 | 20:20 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
68 | 2002-05-14 | 20:25 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
69 | 2002-05-14 | 20:25 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
71 | 2002-05-14 | 20:25 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
73 | 2002-05-14 | 20:25 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
74 | 2002-05-14 | 20:25 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
75 | 2002-05-14 | 20:25 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
76 | 2002-05-14 | 20:25 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
77 | 2002-05-14 | 20:25 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
78 | 2002-05-14 | 20:25 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
79 | 2002-05-14 | 20:25 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
80 | 2002-05-14 | 20:25 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
81 | 2002-05-14 | 20:25 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
82 | 2002-05-14 | 20:25 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
83 | 2002-05-14 | 20:25 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
84 | 2002-05-14 | 20:25 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
85 | 2002-05-14 | 20:25 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
86 | 2002-05-14 | 20:25 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
87 | 2002-05-14 | 20:25 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
88 | 2002-05-14 | 20:25 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
89 | 2002-05-14 | 20:25 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
90 | 2002-05-14 | 20:25 | 2002-05-14 | 23:35 | Charlie | Buck | OO'med to 40 MW per line | Charlie | Buck | OOM lifted
63 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
64 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
65 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
66 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
68 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
69 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
71 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
73 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
74 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
75 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
76 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
77 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
78 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
79 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
80 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
81 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
82 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
83 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
84 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
85 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
86 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
87 | 2002-05-15 | 17:50 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
1 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
2 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
3 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
4 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
5 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
7 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
8 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
9 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
13 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
14 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
15 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
17 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
18 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
19 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
20 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
21 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
22 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
23 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
24 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
25 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
26 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
27 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
28 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
29 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
30 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
32 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
33 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
34 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
35 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
36 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
37 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
38 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
39 | 2002-05-15 | 17:40 | 2002-05-15 | 18:10 | Charlie | Ben | OO'med to 30 MW per line | Charlie | Gilbert | OOM lifted
43 | 2002-05-16 | 8:00 | 2002-05-16 | 9:30 | Tootie | Pete | OO'med to 45 MW per line | Charlie | Pete | OO'med to 45 MW per line
44 | 2002-05-16 | 8:00 | 2002-05-16 | 9:30 | Tootie | Pete | OO'med to 45 MW per line | Charlie | Pete | OO'med to 45 MW per line
45 | 2002-05-16 | 8:00 | 2002-05-16 | 9:30 | Tootie | Pete | OO'med to 45 MW per line | Charlie | Pete | OO'med to 45 MW per line
46 | 2002-05-16 | 8:00 | 2002-05-16 | 9:30 | Tootie | Pete | OO'med to 45 MW per line | Charlie | Pete | OO'med to 45 MW per line
47 | 2002-05-16 | 8:00 | 2002-05-16 | 9:30 | Tootie | Pete | OO'med to 45 MW per line | Charlie | Pete | OO'med to 45 MW per line
75 | 2002-05-16 | 8:20 | 2002-05-16 | 9:30 | Tootie | Pete | OO'med to 45 MW per line | Charlie | Pete | OO'med to 45 MW per line
52 | 2002-05-16 | 8:20 | 2002-05-16 | 9:30 | Tootie | Pete | OO'med to 45 MW per line | Charlie | Pete | OO'med to 45 MW per line
76 | 2002-05-16 | 8:20 | 2002-05-16 | 9:30 | Tootie | Pete | OO'med to 45 MW per line | Charlie | Pete | OO'med to 45 MW per line
1 | 2002-05-16 | 9:32 | 2002-05-16 | 13:01 | Tootie | Pete | OO'med to 45 MW per line | Charlie | Pete | OO'med to 45 MW per line
3 | 2002-05-16 | 9:32 | 2002-05-16 | 13:01 | Tootie | Pete | OO'med to 45 MW per line | Charlie | Pete | OO'med to 45 MW per line
1 | 2002-05-16 | 18:30 | 2002-05-16 | 18:40 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
2 | 2002-05-16 | 18:30 | 2002-05-16 | 18:40 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
3 | 2002-05-16 | 18:30 | 2002-05-16 | 18:40 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
4 | 2002-05-16 | 18:30 | 2002-05-16 | 18:40 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
5 | 2002-05-16 | 18:30 | 2002-05-16 | 18:40 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
7 | 2002-05-16 | 18:30 | 2002-05-16 | 18:40 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
8 | 2002-05-16 | 18:30 | 2002-05-16 | 18:40 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
9 | 2002-05-16 | 18:30 | 2002-05-16 | 18:40 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
13 | 2002-05-16 | 18:30 | 2002-05-16 | 18:40 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
14 | 2002-05-16 | 18:30 | 2002-05-16 | 18:40 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
15 | 2002-05-16 | 18:30 | 2002-05-16 | 19:15 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
17 | 2002-05-16 | 18:30 | 2002-05-16 | 19:15 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
18 | 2002-05-16 | 18:30 | 2002-05-16 | 19:15 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
19 | 2002-05-16 | 18:30 | 2002-05-16 | 19:15 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
20 | 2002-05-16 | 18:30 | 2002-05-16 | 19:15 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
21 | 2002-05-16 | 18:30 | 2002-05-16 | 19:15 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
22 | 2002-05-16 | 18:35 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
23 | 2002-05-16 | 18:35 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
24 | 2002-05-16 | 18:35 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
25 | 2002-05-16 | 18:35 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
26 | 2002-05-16 | 18:35 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
27 | 2002-05-16 | 18:35 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
28 | 2002-05-16 | 18:35 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
29 | 2002-05-16 | 18:35 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
30 | 2002-05-16 | 18:35 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OO'med to 45 MW per line
63 | 2002-05-16 | 18:05 | 2002-05-16 | 18:30 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
64 | 2002-05-16 | 18:05 | 2002-05-16 | 18:30 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
65 | 2002-05-16 | 18:05 | 2002-05-16 | 18:45 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
66 | 2002-05-16 | 18:05 | 2002-05-16 | 18:45 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
68 | 2002-05-16 | 18:05 | 2002-05-16 | 18:45 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
69 | 2002-05-16 | 18:05 | 2002-05-16 | 18:45 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
71 | 2002-05-16 | 18:05 | 2002-05-16 | 18:50 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
73 | 2002-05-16 | 18:05 | 2002-05-16 | 18:50 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
74 | 2002-05-16 | 18:05 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
75 | 2002-05-16 | 18:05 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
76 | 2002-05-16 | 18:05 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
77 | 2002-05-16 | 18:05 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
78 | 2002-05-16 | 18:05 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
79 | 2002-05-16 | 18:15 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
80 | 2002-05-16 | 18:15 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
81 | 2002-05-16 | 18:15 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
82 | 2002-05-16 | 18:15 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
83 | 2002-05-16 | 18:15 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
84 | 2002-05-16 | 18:15 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
85 | 2002-05-16 | 18:15 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
86 | 2002-05-16 | 18:15 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
87 | 2002-05-16 | 18:15 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
88 | 2002-05-16 | 18:15 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
89 | 2002-05-16 | 18:15 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
90 | 2002-05-16 | 18:15 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
91 | 2002-05-16 | 18:15 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
92 | 2002-05-16 | 18:15 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
93 | 2002-05-16 | 18:15 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
96 | 2002-05-16 | 18:15 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
100 | 2002-05-16 | 18:15 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
102 | 2002-05-16 | 18:15 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
103 | 2002-05-16 | 18:20 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
104 | 2002-05-16 | 18:20 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
105 | 2002-05-16 | 18:20 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
106 | 2002-05-16 | 18:20 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
107 | 2002-05-16 | 18:20 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OO'med to 10 MW per line
1 | 2002-05-16 | 19:00 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OOM released
2 | 2002-05-16 | 19:00 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OOM released
3 | 2002-05-16 | 19:00 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OOM released
4 | 2002-05-16 | 19:00 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OOM released
5 | 2002-05-16 | 19:00 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OOM released
7 | 2002-05-16 | 19:00 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OOM released
8 | 2002-05-16 | 19:00 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OOM released
9 | 2002-05-16 | 19:00 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OOM released
13 | 2002-05-16 | 19:00 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OOM released
14 | 2002-05-16 | 19:00 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OOM released
1 | 2002-05-16 | 20:55 | 2002-05-17 | 0:15 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
2 | 2002-05-16 | 20:55 | 2002-05-17 | 0:15 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
3 | 2002-05-16 | 20:55 | 2002-05-17 | 0:15 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
4 | 2002-05-16 | 20:55 | 2002-05-17 | 0:15 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
5 | 2002-05-16 | 20:55 | 2002-05-17 | 0:15 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
7 | 2002-05-16 | 20:55 | 2002-05-17 | 0:15 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
8 | 2002-05-16 | 20:55 | 2002-05-17 | 0:15 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
9 | 2002-05-16 | 20:55 | 2002-05-17 | 0:15 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
13 | 2002-05-16 | 20:55 | 2002-05-17 | 0:15 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
14 | 2002-05-16 | 20:55 | 2002-05-17 | 0:15 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
15 | 2002-05-16 | 20:55 | 2002-05-17 | 0:20 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
17 | 2002-05-16 | 20:55 | 2002-05-17 | 0:20 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
18 | 2002-05-16 | 20:55 | 2002-05-17 | 0:20 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
19 | 2002-05-16 | 20:55 | 2002-05-17 | 0:20 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
20 | 2002-05-16 | 20:55 | 2002-05-17 | 0:20 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
21 | 2002-05-16 | 20:55 | 2002-05-17 | 0:35 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
22 | 2002-05-16 | 20:55 | 2002-05-17 | 0:35 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
23 | 2002-05-16 | 20:55 | 2002-05-17 | 2:35 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
24 | 2002-05-16 | 20:55 | 2002-05-17 | 2:35 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
25 | 2002-05-16 | 20:55 | 2002-05-17 | 2:35 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
26 | 2002-05-16 | 20:55 | 2002-05-17 | 3:10 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
27 | 2002-05-16 | 20:55 | 2002-05-17 | 3:10 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
28 | 2002-05-16 | 20:55 | 2002-05-17 | 3:20 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
29 | 2002-05-16 | 20:55 | 2002-05-17 | 3:20 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
30 | 2002-05-16 | 20:55 | 2002-05-17 | 3:20 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
32 | 2002-05-16 | 20:55 | 2002-05-17 | 3:20 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Released to 50 MW per line
109 | 2002-05-16 | 18:20 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OOM released
120 | 2002-05-16 | 18:20 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OOM released
113 | 2002-05-16 | 18:35 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OOM released
117 | 2002-05-16 | 18:35 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OOM released
118 | 2002-05-16 | 19:10 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OOM released
119 | 2002-05-16 | 19:10 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 10 MW per line | Charlie | Pete | OOM released
63 | 2002-05-16 | 21:00 | 2002-05-16 | 19:35 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | OOM released
64 | 2002-05-16 | 21:00 | 2002-05-16 | 19:35 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | OOM released
65 | 2002-05-16 | 21:00 | 2002-05-17 | 0:20 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
66 | 2002-05-16 | 21:00 | 2002-05-17 | 0:20 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
68 | 2002-05-16 | 21:00 | 2002-05-17 | 0:20 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
69 | 2002-05-16 | 21:00 | 2002-05-17 | 0:20 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
71 | 2002-05-16 | 21:00 | 2002-05-17 | 0:20 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
73 | 2002-05-16 | 21:00 | 2002-05-17 | 0:20 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
74 | 2002-05-16 | 21:00 | 2002-05-17 | 0:20 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
75 | 2002-05-16 | 21:00 | 2002-05-17 | 0:20 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
76 | 2002-05-16 | 21:00 | 2002-05-17 | 0:20 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
77 | 2002-05-16 | 21:00 | 2002-05-17 | 0:20 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
78 | 2002-05-16 | 21:00 | 2002-05-17 | 0:20 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
79 | 2002-05-16 | 21:00 | 2002-05-17 | 0:20 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
80 | 2002-05-16 | 21:00 | 2002-05-17 | 0:35 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
81 | 2002-05-16 | 21:00 | 2002-05-17 | 0:35 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
82 | 2002-05-16 | 21:00 | 2002-05-17 | 0:35 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
83 | 2002-05-16 | 21:00 | 2002-05-17 | 0:35 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
84 | 2002-05-16 | 21:00 | 2002-05-17 | 0:35 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
85 | 2002-05-16 | 21:00 | 2002-05-17 | 2:35 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
86 | 2002-05-16 | 21:00 | 2002-05-17 | 3:30 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
87 | 2002-05-16 | 21:00 | 2002-05-17 | 3:30 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
88 | 2002-05-16 | 21:00 | 2002-05-17 | 4:35 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
89 | 2002-05-16 | 2:20 | 2002-05-17 | 4:35 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
90 | 2002-05-16 | 2:20 | 2002-05-17 | 4:35 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
91 | 2002-05-16 | 2:20 | 2002-05-17 | 4:35 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
92 | 2002-05-16 | 2:20 | 2002-05-17 | 4:35 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
93 | 2002-05-16 | 2:20 | 2002-05-17 | 4:35 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
96 | 2002-05-16 | 4:00 | 2002-05-17 | 4:35 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
100 | 2002-05-16 | 4:00 | 2002-05-17 | 4:35 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Hold at 50 MW per line
32 | 2002-05-16 | 18:35 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OOM released
33 | 2002-05-16 | 18:35 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OOM released
34 | 2002-05-16 | 18:35 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OOM released
35 | 2002-05-16 | 18:35 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OOM released
36 | 2002-05-16 | 19:10 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OOM released
37 | 2002-05-16 | 19:10 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OOM released
38 | 2002-05-16 | 19:10 | 2002-05-16 | 19:20 | Charlie | Pete | OO'med to 25 MW per line | Charlie | Pete | OOM released
33 | 2002-05-16 | 20:55 | 2002-05-17 | 3:30 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Oomed to 40 MW
34 | 2002-05-16 | 20:55 | 2002-05-17 | 3:30 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Oomed to 40 MW
35 | 2002-05-16 | 20:55 | 2002-05-17 | 3:30 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Oomed to 40 MW
36 | 2002-05-16 | 20:55 | 2002-05-17 | 3:30 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Oomed to 40 MW
37 | 2002-05-16 | 20:55 | 2002-05-17 | 3:30 | Charlie | Pete | OO'med to 30 MW per line | Charlie | Pete | Oomed to 40 MW
42 | 2002-05-17 | 2:16 | 2002-05-17 | 4:30 | Charlie | Pete | OO'med to 40 MW per line | Charlie | Pete | OOM released
43 | 2002-05-17 | 2:16 | 2002-05-17 | 4:30 | Charlie | Pete | OO'med to 40 MW per line | Charlie | Pete | OOM released
44 | 2002-05-17 | 2:16 | 2002-05-17 | 4:30 | Charlie | Pete | OO'med to 40 MW per line | Charlie | Pete | OOM released
45 | 2002-05-17 | 2:16 | 2002-05-17 | 4:30 | Charlie | Pete | OO'med to 40 MW per line | Charlie | Pete | OOM released
46 | 2002-05-17 | 2:16 | 2002-05-17 | 4:30 | Charlie | Pete | OO'med to 40 MW per line | Charlie | Pete | OOM released
47 | 2002-05-17 | 2:45 | 2002-05-17 | 4:30 | Charlie | Pete | OO'med to 40 MW per line | Charlie | Pete | OOM released
49 | 2002-05-17 | 2:45 | 2002-05-17 | 4:30 | Charlie | Pete | OO'med to 40 MW per line | Charlie | Pete | OOM released
50 | 2002-05-17 | 2:45 | 2002-05-17 | 4:30 | Charlie | Pete | OO'med to 40 MW per line | Charlie | Pete | OOM released
51 | 2002-05-17 | 2:45 | 2002-05-17 | 4:30 | Charlie | Pete | OO'med to 40 MW per line | Charlie | Pete | OOM released
52 | 2002-05-17 | 4:00 | 2002-05-17 | 4:30 | Charlie | Pete | OO'med to 40 MW per line | Charlie | Pete | OOM released
53 | 2002-05-17 | 4:00 | 2002-05-17 | 4:30 | Charlie | Pete | OO'med to 40 MW per line | Charlie | Pete | OOM released
54 | 2002-05-17 | 4:00 | 2002-05-17 | 4:30 | Charlie | Pete | OO'med to 40 MW per line | Charlie | Pete | OOM released
55 | 2002-05-17 | 4:15 | 2002-05-17 | 4:30 | Charlie | Pete | OO'med to 40 MW per line | Charlie | Pete | OOM released
56 | 2002-05-17 | 4:15 | 2002-05-17 | 4:30 | Charlie | Pete | OO'med to 40 MW per line | Charlie | Pete | OOM released
57 | 2002-05-17 | 4:15 | 2002-05-17 | 4:30 | Charlie | Pete | OO'med to 40 MW per line | Charlie | Pete | OOM released
102 | 2002-05-17 | 4:15 | 2002-05-17 | 4:35 | Bryan | Pete | OO'med to 40 MW per line | Charlie | Pete | OOM released
103 | 2002-05-17 | 4:15 | 2002-05-17 | 4:35 | Bryan | Pete | OO'med to 40 MW per line | Charlie | Pete | OOM released
104 | 2002-05-17 | 4:15 | 2002-05-17 | 4:35 | Bryan | Pete | OO'med to 40 MW per line | Charlie | Pete | OOM released
17 | 2002-05-17 | 18:30 | 2002-05-17 | 21:30 | Bryan | Pete | OO'med to 40 MW per line | Bryan | Pete | OOM released
20 | 2002-05-17 | 18:30 | 2002-05-17 | 21:30 | Bryan | Pete | OO'med to 40 MW per line | Bryan | Pete | OOM released
34 | 2002-05-17 | 18:30 | 2002-05-17 | 21:30 | Bryan | Pete | OO'med to 40 MW per line | Bryan | Pete | OOM released
38 | 2002-05-17 | 18:30 | 2002-05-17 | 21:30 | Bryan | Pete | OO'med to 40 MW per line | Bryan | Pete | OOM released
43 | 2002-05-17 | 18:30 | 2002-05-17 | 21:30 | Bryan | Pete | OO'med to 40 MW per line | Bryan | Pete | OOM released
46 | 2002-05-17 | 18:30 | 2002-05-17 | 21:30 | Bryan | Pete | OO'med to 40 MW per line | Bryan | Pete | OOM released
47 | 2002-05-17 | 18:30 | 2002-05-17 | 21:30 | Bryan | Pete | OO'med to 40 MW per line | Bryan | Pete | OOM released
50 | 2002-05-17 | 18:30 | 2002-05-17 | 21:30 | Bryan | Pete | OO'med to 40 MW per line | Bryan | Pete | OOM released
73 | 2002-05-17 | 18:30 | 2002-05-17 | 21:30 | Bryan | Pete | OO'med to 40 MW per line | Bryan | Pete | OOM released
77 | 2002-05-17 | 18:30 | 2002-05-17 | 21:30 | Bryan | Pete | OO'med to 40 MW per line | Bryan | Pete | OOM released
84 | 2002-05-17 | 18:30 | 2002-05-17 | 21:30 | Bryan | Pete | OO'med to 40 MW per line | Bryan | Pete | OOM released
87 | 2002-05-17 | 18:30 | 2002-05-17 | 21:30 | Bryan | Pete | OO'med to 40 MW per line | Bryan | Pete | OOM released
93 | 2002-05-17 | 18:30 | 2002-05-17 | 21:30 | Bryan | Pete | OO'med to 40 MW per line | Bryan | Pete | OOM released
120 | 2002-05-17 | 18:30 | 2002-05-17 | 21:30 | Bryan | Pete | OO'med to 40 MW per line | Bryan | Pete | OOM released
114 | 2002-05-17 | 18:30 | 2002-05-17 | 21:30 | Bryan | Pete | OO'med to 40 MW per line | Bryan | Pete | OOM released
115 | 2002-05-17 | 18:30 | 2002-05-17 | 21:30 | Bryan | Pete | OO'med to 40 MW per line | Bryan | Pete | OOM released
118 | 2002-05-17 | 18:30 | 2002-05-17 | 21:30 | Bryan | Pete | OO'med to 40 MW per line | Bryan | Pete | OOM released
68 | 2002-05-15 | 6:00 | 2002-05-15 | 13:13 | Charlie | Ben | OO'med to 40 MW per line | Charlie | Ben | OOM released
69 | 2002-05-15 | 6:00 | 2002-05-15 | 13:13 | Charlie | Ben | OO'med to 40 MW per line | Charlie | Ben | OOM released
71 | 2002-05-15 | 6:00 | 2002-05-15 | 17:25 | Charlie | Ben | OO'med to 40 MW per line | Charlie | Ben | OOM released
73 | 2002-05-15 | 6:00 | 2002-05-15 | 17:25 | Charlie | Ben | OO'med to 40 MW per line | Charlie | Ben | OOM released
74 | 2002-05-15 | 6:00 | 2002-05-15 | 17:25 | Charlie | Ben | OO'med to 40 MW per line | Charlie | Ben | OOM released
75 | 2002-05-15 | 6:00 | 2002-05-15 | 17:25 | Charlie | Ben | OO'med to 40 MW per line | Charlie | Ben | OOM released
76 | 2002-05-15 | 6:00 | 2002-05-15 | 17:25 | Charlie | Ben | OO'med to 40 MW per line | Charlie | Ben | OOM released
77 | 2002-05-15 | 6:00 | 2002-05-15 | 17:25 | Charlie | Ben | OO'med to 40 MW per line | Charlie | Ben | OOM released
78 | 2002-05-15 | 6:00 | 2002-05-15 | 8:13 | Charlie | Ben | OO'med to 40 MW per line | Tootie | Ben | OOM released
79 | 2002-05-15 | 6:00 | 2002-05-15 | 8:13 | Charlie | Ben | OO'med to 40 MW per line | Tootie | Ben | OOM released
80 | 2002-05-15 | 6:00 | 2002-05-15 | 8:13 | Charlie | Ben | OO'med to 40 MW per line | Tootie | Ben | OOM released
81 | 2002-05-15 | 6:00 | 2002-05-15 | 8:13 | Charlie | Ben | OO'med to 40 MW per line | Tootie | Ben | OOM released
82 | 2002-05-15 | 6:00 | 2002-05-15 | 8:13 | Charlie | Ben | OO'med to 40 MW per line | Tootie | Ben | OOM released
83 | 2002-05-15 | 6:00 | 2002-05-15 | 8:13 | Charlie | Ben | OO'med to 40 MW per line | Tootie | Ben | OOM released
84 | 2002-05-15 | 6:00 | 2002-05-15 | 13:23 | Charlie | Ben | OO'med to 40 MW per line | Tootie | Roger | OOM released
85 | 2002-05-15 | 6:00 | 2002-05-15 | 13:23 | Charlie | Ben | OO'med to 40 MW per line | Tootie | Roger | OOM released
86 | 2002-05-15 | 6:00 | 2002-05-15 | 13:23 | Charlie | Ben | OO'med to 40 MW per line | Tootie | Roger | OOM released
87 | 2002-05-15 | 7:03 | 2002-05-15 | 10:38 | Tootie | Roger | OO'med to 40 MW per line | Tootie | Roger | OOM released
88 | 2002-05-15 | 7:03 | 2002-05-15 | 10:38 | Tootie | Roger | OO'med to 40 MW per line | Tootie | Roger | OOM released
89 | 2002-05-15 | 8:13 | 2002-05-15 | 10:38 | Tootie | Roger | OO'med to 40 MW per line | Tootie | Roger | OOM released
90 | 2002-05-15 | 8:13 | 2002-05-15 | 10:25 | Tootie | Roger | OO'med to 40 MW per line | Tootie | Roger | OOM released
91 | 2002-05-15 | 8:13 | 2002-05-15 | 8:19 | Tootie | Roger | OO'med to 40 MW per line | Tootie | Roger | OOM released
92 | 2002-05-15 | 8:13 | 2002-05-15 | 10:25 | Tootie | Roger | OO'med to 40 MW per line | Tootie | Roger | OOM released
93 | 2002-05-15 | 8:13 | 2002-05-15 | 10:23 | Tootie | Roger | OO'med to 40 MW per line | Tootie | Roger | OOM released
106 | 2002-05-15 | 8:13 | 2002-05-15 | 17:30 | Tootie | Roger | OO'med to 40 MW per line | Charlie | Ben | OOM released
121 | 2002-05-15 | 10:53 | 2002-05-15 | 17:30 | Tootie | Roger | OO'med to 40 MW per line | Charlie | Ben | OOM released
122 | 2002-05-15 | 10:53 | 2002-05-15 | 17:30 | Tootie | Roger | OO'med to 40 MW per line | Tootie | Roger | OOM released
118 | 2002-05-15 | 11:09 | 2002-05-15 | 11:11 | Tootie | Roger | OO'med to 40 MW per line | Tootie | Roger | OOM released
119 | 2002-05-15 | 11:09 | 2002-05-15 | 11:11 | Tootie | Roger | OO'med to 40 MW per line | Charlie | Ben | OOM released
117 | 2002-05-15 | 11:09 | 2002-05-15 | 17:30 | Tootie | Roger | OO'med to 40 MW per line | Charlie | Ben | OOM released
87 | 2002-05-15 | 11:11 | 2002-05-15 | 13:23 | Tootie | Roger | OO'med to 40 MW per line | Charlie | Ben | OOM released
88 | 2002-05-15 | 11:11 | 2002-05-15 | 13:23 | Tootie | Roger | OO'med to 40 MW per line | Charlie | Ben | OOM released
89 | 2002-05-15 | 11:11 | 2002-05-15 | 13:23 | Tootie | Roger | OO'med to 40 MW per line | Charlie | Ben | OOM released
90 | 2002-05-15 | 11:58 | 2002-05-15 | 13:23 | Tootie | Roger | OO'med to 40 MW per line | Charlie | Ben | OOM released
91 | 2002-05-15 | 12:02 | 2002-05-15 | 13:39 | Tootie | Roger | OO'med to 40 MW per line | Charlie | Ben | OOM released
1 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
2 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
3 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
4 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
5 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
7 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
8 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
9 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
13 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
15 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
17 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
18 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
19 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
20 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
21 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
22 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
23 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
24 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
25 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
26 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
27 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
28 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
29 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
30 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
32 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
33 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
34 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
35 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
36 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
37 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
38 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
39 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
40 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
41 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
42 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
43 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
44 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
45 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
46 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
47 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
49 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
51 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
52 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
55 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
63 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
65 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
68 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
69 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
71 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
72 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
73 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
74 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
75 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
76 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
77 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
79 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
80 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
82 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
84 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
85 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
86 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
88 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
89 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
90 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
91 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
92 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
93 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
96 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
102 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
103 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
105 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
107 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
78 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
87 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
66 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
67 | 2002-05-18 | 19:30 | 2002-05-18 | 21:30 | Bryan | Pete | OO'med to 10 MW per line | Bryan | Pete | Switched to curtailment software
2 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
8 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
9 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
13 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
14 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
17 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
19 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
24 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
25 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
26 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
27 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
28 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
31 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
33 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
36 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
44 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
45 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
46 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
49 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
55 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
57 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
58 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
59 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
60 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
1 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
3 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software
4 | 2002-05-25 | 20:00 | 2002-05-25 | 21:30 | Bryan | Johnny | Curtailed turbines for CPS OOM level unknown | Bryan | Johnny | Switched to curtailment software

## PROJECTS
Desert Sky
SPECIAL PROJECTS
Month: | May '02
1. Completed punch list
2. Cleaned laydown yard
3. Inspected all VEM generators for vibration
4. Inspected all pitch encoders.
5. Curtailment software was installed
6. Inspected all blades with spotter scopes
7. Dedicated site
8. Changed generator on WTG #116