## Performance
UAE Lowell Power Expansion |  | Single LM6000 Unit
Equipment Performance |  | Ambient vs. Front End Simple Cycle Technology
5 - GE/S&S LM6000 Units
|  | 0 oF |  |  | 60 oF |  |  | 90 oF
|  | DLE | Spr. w/ WI | Spr. w/ SI | DLE | Spr. w/ WI | Spr. w/ SI | DLE | Spr. w/ WI | Spr. w/ SI
General Plant Performance Data
Generator Power, MW |  | S | 48.76 | 48.76 | 44.28 | 46.13 | 47.35 | 44.32 | 46.04 | 47.25
Gross Heat Rate, Btu/kWh (LHV) |  | & | 8338 | 8338 | 8261 | 8557 | 7934 | 8260 | 8555 | 7938
Gross Heat Rate, Btu/kWh (HHV) (3) |  | S | 9264.4352 | 9264.4352 | 9178.8797 | 9507.7683 | 8815.5467 | 9177.7686 | 9505.5461 | 8819.9912
Gross Heat Rate Adjusted for Steam Use, Btu/kWh (HHV) |  |  | na | 10132.1649 | na | na | 9665.9845 | na | na | 9664.0761
Fuel Flow, mmBtu/hr (LHV) |  |  | 406.5609 | 406.5609 | 365.7971 | 394.7344 | 375.6749 | 366.0832 | 393.8722 | 375.0705
Fuel Flow, mmBtu/hr (HHV) |  |  | 451.2826 | 451.2826 | 406.0348 | 438.1552 | 416.9991 | 406.3524 | 437.1981 | 416.3283
Chilling Requirements, tons |  | R | 0 | 0 | 210 | 208 | 212 | 1892 | 1590 | 1905
Water Injection Flow, pph |  | u | 20548 | 0 | 0 | 20835 | 0 | 0 | 20593 | 0
Steam Injection Flow, pph |  | n | 0 | 33500 | 0 | 0 | 31883 | 0 | 0 | 31578
Sprint Water Injection Flow, pph |  | s | 0 | 0 | 0 | 2445 | 2445 | 0 | 2445 | 2445
Aux Load (kW) (2) |  |  | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200
Chiller Aux. Load (kW) |  |  | 0 | 0 | 272 | 270.6 | 273.4 | 1449.4 | 1238 | 1458.5
Net Power Output, MW |  | @ | 47.56 | 47.56 | 42.808 | 44.6594 | 45.8766 | 41.6706 | 43.602 | 44.5915
NOx, ppm |  | 2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
NOx, pph |  | 0 | 41 | 41 | 37 | 40 | 38 | 37 | 40 | 38
CO, ppm |  | oF | 80 | 80 | 25 | 29 | 23 | 25 | 28 | 23
CO, pph |  |  | 80 | 80 | 22 | 28 | 22 | 22 | 27 | 21
Expected DEP NOx Emission Rate, ppm |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Reduction Required |  |  | 92% | 92% | 92% | 92% | 92% | 92% | 92% | 92%
Expected DEP NOx Emission Rate, lb/mmBtu |  |  | 0.0073729 | 0.0073729 | 0.0073729 | 0.0073729 | 0.0073729 | 0.0073729 | 0.0073729 | 0.0073729
Expected DEP NOx Emission Rate, lb/hr |  |  | 2.9937 | 2.996 | 3.3273 | 3.2305 | 3.2234 | 3.3273 | 3.0745 | 3.0696
Expected DEP CO Reduction Rate, % |  |  | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90%
Expected DEP CO Emission Rate, ppm |  |  | 8 | 8 | 2.5 | 2.9 | 2.3 | 2.5 | 2.8 | 2.3
Notes:
1 | Spray Intercooling (Sprint) is not currently available with DLE combustors.
2 | Auxiliary load includes fuel compression, misc. GT auxiliaries, and transformer losses
3 | Gross heat rate as a function of the HHV of the fuel plus degradation

## Sheet2
UAE Lowell Power Expansion
Technology Comparison
5 - GE/S&S LM6000 Units | Yearly Revenue/Cost Variances per Unit
| DLE Combustor | Sprint w/ Water Injection | Sprint w/ Steam Injection (3)
| w/ Inlet Chilling | w/ Inlet Chilling | w/ Inlet Chilling
DLE Capital Recovery ($1.1m over 15 yr. @ 11%) (1) | 121000.0008 | 0 | 0
Chiller Cost (90 oF, electric @ $0.03/kw-hr, 2500 hrs) | 108705 | 92850 | 109387.5
Sprint Water Injection (@100 oF & $1.40/100 cu. ft.) | 0 | 1377.7575 | 1377.7575
Water Injection (@100 oF & $1.40/100 cu. ft.) | 0 | 11740.5225 | 0
Steam Injection (550 psig, 75 oF sprht, 1263 Btu/lb) | 0 | 0 | 358947.126
Major Maintenance | 264650 | 224871.0977 | 231000
Water Treatment Capital Recovery ($200,000 over 15 yr. @ 11%) | 0 | 22000.0002 | 22000.0002
Water Treatment Variable Cost ($0.0025/gal for chemical, 2500 hrs.) | 0 | 15432.4041 | 23664.5683
Fuel Cost ($3/mmBtu & 2500 hrs.) | 3047642.64 | 3278986.065 | 3122461.9125
Capacity Payment ($6/kw-mo w/ DLE Unit as datum) | 0 | -133300.8 | -220939.2
Total First Year Cost | 3541997.6408 | 3513957.0469 | 3647899.6645
Operating Hours | 2500
(1) Price differential between machines equipped with a DLE Combustor and those with the Sprint Technology is $1.1 m ($1.4 m for DLE, $0.3 for Sprint)
(2) General assumption of 2500 hrs. operating
(3) Steam injection rates of over 30,000 lbs/hr can not be handled by existing systems