## Capital Budget
UAE Lowell Power Expansion |  | PRELIMINARY DATA; ENGINEERING STUDY UNDERWAY TO CONFIRM ASSUMPTIONS
Capital Cost Breakdown ($ = 000's)
| 5x GE LM 6000 Base Package - Simple Cycle | DLE Combustor | 0 | (1=yes, 0=no)
Feb 23 Meeting with Enron Capital and Trade
|  | Lowell Expansion |  |  |  | GT Pro
Gas Turbine Package |  | Equipment | Installation | Total | Per Unit
| Gas Turbine Generator | 69000 | 1000 | 70000 | 14000 | 70000 | 0
| Sprint Package Adder (unavail w/DLE) | 1500 | 0 | 1500 | 300 |  | 1500
| Inlet Air Chiller | 3800 | 250 | 4050 | 810 | 4278 | -228
| Switchgear/MCC/Relays/Breaker Set | 1000 | 250 | 1250 | 250 | 770 | 480
| Stack(s)/Noise Attenuation/Buildings | 1250 | 250 | 1500 | 300 |  | 1500
| Water Tube Oil Cooler | 0 | 0 | 0 | 0 |  | 0
| Freight | 500 | 0 | 500 | 100 |  | 500
| Spare Parts Inventory | 350 | 0 | 350 | 70 | 250 | 100
Total Base Package |  | 77400 | 1750 | 79150 | 15830 | 75298 | 3852
Emissions Controls
| Vanadium-Titanium SCR (to 2 ppm NOX) | 4600 | 250 | 4850 | 970
| CO Oxidation Catalyst (to 10ppm CO) | 1000 | 100 | 1100 | 220
| Dry Low Emissions (DLE) Combustor Adder | 0 | 200 | 200 | 40
|  | 5600 | 550 | 6150 | 1230
Balance Of Plant
| Pads and Grading | 1200 | 400 | 1600 | 320
| Fuel Gas Compressors | 1000 | 250 | 1250 | 250
| Control Room (upgrade to existing unit) | 250 | 100 | 350 | 70
| Controls For Remote Operation | 50 | 50 | 100 | 20
| Demin Water Treatment (for Sprint/Water Inj) | 500 | 100 | 600 | 120
| Fire Protection | 300 | 100 | 400 | 80
| Cooling Tower for Chiller | 1200 | 350 | 1550 | 310
| Ammonia System (Tanks, Unldg./Fwdg. Pumps) | 250 | 50 | 300 | 60
| Step-Up Transformer(s) | 1500 | 300 | 1800 | 360
| Piping | 300 | 120 | 420 | 84
| Wiring | 700 | 450 | 1150 | 230
| Continuous Emissions Monitoring | 550 | 150 | 700 | 140
| Other | 0 | 0 | 0 | 0
Total Emissions and BOP |  | 13400 | 2970 | 16370 | 3274
Total EPC |  |  |  | 95520 | 19104
Owner's Cost
| Air Permitting | 500 |  |  | 100
| Air Permit Fees | 25 |  |  | 5
| Boston Gas Upgrades | 2000 |  |  | 400
| Utility Connection Cost (NEP) | 750 |  |  | 150
| Interconnect Study (NEP) | 250 |  |  | 50
| Property Purchase | 1000 |  |  | 200
| Water/Sewer Connect | 200 |  |  | 40
| Phase I/Phase II Environmental Review | 35 |  |  | 7
| Engineering Plant Specification | 50 |  |  | 10
| Engineering (Studies/Services/Conceptual) | 75 |  |  | 15
| Development/Construction Management | 600 |  |  | 120
| Interest During Construction | 3220 |  |  | 644
| Misc. Permits/Fees |  |  |  | 0
| Legal Fees | 500 |  |  | 100
| Bank Fees | 500 |  |  | 100
| Emissions Offsets | 350 |  |  | 70
| Working Capital | 2500 |  |  | 500
| Miscellaneous Consultants | 100 |  |  | 20
| Owner's Contingency (3% of EPC) | 2865.6 |  |  | 573.12
Total Owner's |  | 15520.6 |  |  | 3104.12
Commissioning
| Site Infrastructure (roads, landscape, neighbors) | 250 |  |  | 50
| Start Up | 500 |  |  | 100
Total Commissioning |  | 750 |  |  | 150
Total
| Base Package | 79150 |  |  | 15830
| BOP | 16370 |  |  | 3274
| Sales Tax (5.0%) | 4540 |  |  | 908
| Owner's Cost | 15520.6 |  |  | 3104.12
| Other Costs | 750 |  |  | 150
Total Capital Cost |  | 116330.6 |  |  | 23266.12
ISO Output (MW) |  | 227.5 |  |  | 45.5
$/kW |  | 511.3433 |  |  | 511.3433
| DLE Estimated Output at 90 deg F | 221.6
| Sprint/Water Inj Estimated Output at 90 deg F | 227.5

## Fixed and Variable Costs
United American Energy | PRELIMINARY ECONOMIC ANALYSIS
Lowell Power Expansion
Feb 23 Meeting with Enron Capital and Trade
Operations Summary
FIXED COSTS
Labor |  | 100 | add one+ maintenance
Annual Inspection of Gas Turbines |  | 100
Fixed - maint & consum |  | 193.75 | per S&S
Operator Fee |  | 100
G&A
Property & BI Insurance |  | 400
Replacement Power Insurance |  | discuss
Real Property Taxes |  | 500 | same as existing PILOT
Water Supply/Discharge |  | 100 | cooling tower
Interconnect and NEPOOL Fees |  | 150
Audit/Miscellaneous |  | 50
NOx Budget |  | 75
Asset Mgt. Cost |  | 100
1868.75
VARIABLE COSTS | $/mwhr | Cost | Energy | hrs/yr | Capacity
LM6000 | 2.3187 | 1258.9348 | 542942.5855 | 2450.1019 | 221.6
Consumables | 0.15418 | 83.7091 | 542942.5855