## Construction Costs
Project Orion
Summary of Project Costs (Plant 1)
Summary
Source |  | Paul Steinway | Land | 5000000
Date |  | 1999-10-28 | EPC | 209193073
|  |  | Management's Costs | 38316704
|  |  | Total Project Cost | 252509777
EPC
Major Equipment |  |  | Construction Services (Cont.)
| Gas Turbines | 88200000 | Structural Steel | 184352
| Heat Recovery Boilers | 16500000 | Building and Erection | 1469386
| Steam Turbines | 13044000 | Equipment Installation - Mechanical | 2267166
| Freight | 1385424 | Process Piping | 2924272
| Total Major Equipment | 119129424 | Equipment Installation - Electrical | 1252755
Balance of Plant Equipment and Materials |  |  | Electrical - Wire, Cable & Terminati | 1857267
| Electrical Xfrmrs and Swgr | 9149264 | Testing, Calibration | 558253
| Instrumentation and Controls | 2504816 | Site Interconnections Eng. & Construction | 3000000
| Conduit, Wire and Cable | 1629954 | Total Construction Services | 47197234
| Metal Building | 1072154
| Pumps | 1703479 | Change Orders/Contingency | 9200000
| Misc. Equipment | 2561965
| Condeners | 1541818 | Engineering | 6699886
| Natural Gas Sample and Meter | 1284351 | Total EPC | 209193073
| Cooling Tower | 1226330
| Piping | 2825306 | Managment's Costs
| Valves | 1467092
| Total Plant Equipment and Materials | 26966529 | Project Management, Expenses and Devel't Fees | 20816248
Construction Services |  |  | O&M Start Up Personnel and Expenses | 5146668
| General Conditions Incl. O.H. And Pro. | 12787938 | Spare Parts | 4000000
| Field Office Expenses | 1010152 | Insurance | 2167996
| Field Office Personnel | 2377536 | Allowance for Sales and Use Tax | 6185792
| Misc. General Field Conditions | 920640 | Total Management's Costs | 38316704
| Electrical Subcontractor Indirects | 6181618
| Construction Equipment | 2962547 | Total Plant Costs | 247509777
| Mobilization | 1004000
| Site Development | 2043358 | Land | 5000000
| Foundations | 4395994
Note on F22: Authorized User: Added at B. Bierenkoven's request

## Cost Basis
Summary of Actual Project Costs |  | Fort |  |  |  | Orion | Orion
|  | Lupton |  | Greeley |  | 6LM x 6 x 3 | 1EA x 1 x 1 |  | Orion
|  | 5 x 5 x 2 |  | 1 x 1 x 0 |  | Component | Component |  | Notes
Major Equipment
| Gas Turbines | 54894142 |  | 12293100 |  | 66750000 | 17500000 |  | LMs at $11m each plus $125K shipping…7EA at $17m plus $500K shipping & misc.
| Heat Recovery Boilers | 8040650 |  | 1604162 |  | 11096097 | 2875000 |  | LMs at 6 5ths Fort Lupton times 1.15 for altitude/capacity adjust…EA swag.
| Steam Turbines | 11839276 |  |  |  | 16338200.88 | 4570126.1203 | 119129424.0003 | LMs at 6 5ths Fort Lupton times 1.15 for altitude/capacity adjust…EA at ST MW ratio.
Balance of Plant Equipment & Materials
| Electrical Xfrmrs & Swgr | 5120122 |  |  |  | 7065768.36 | 2083495.7985 |  | LMs at 6 5ths Fort Lupton times 1.15 for altitude/capacity adjust…EA at ST MW ratio.
| Instrumentation & Controls | 1401748 |  |  |  | 1934412.24 | 570403.6092 |  | LMs at 6 5ths Fort Lupton times 1.15 for altitude/capacity adjust…EA at ST MW ratio.
| Conduit, Wire & Cable | 912157 |  |  |  | 1258776.66 | 371177.7331 |  | LMs at 6 5ths Fort Lupton times 1.15 for altitude/capacity adjust…EA at ST MW ratio.
| Metal Building | 600000 |  |  |  | 828000 | 244153.8462 |  | LMs at 6 5ths Fort Lupton times 1.15 for altitude/capacity adjust…EA at ST MW ratio.
| Pumps | 953303 |  |  |  | 1315558.14 | 387920.99 |  | LMs at 6 5ths Fort Lupton times 1.15 for altitude/capacity adjust…EA at ST MW ratio.
| Misc. Equipment | 1433730 |  |  |  | 1978547.4 | 583417.8231 |  | LMs at 6 5ths Fort Lupton times 1.15 for altitude/capacity adjust…EA at ST MW ratio.
| Condensers | 862834 |  |  |  | 1190710.92 | 351107.0662 |  | LMs at 6 5ths Fort Lupton times 1.15 for altitude/capacity adjust…EA at ST MW ratio.
| Natural Gas Sample & Meter | 718750 |  |  |  | 991875 | 292475.9615 |  | LMs at 6 5ths Fort Lupton times 1.15 for altitude/capacity adjust…EA at ST MW ratio.
| Cooling Tower | 686280 |  |  |  | 947066.4 | 279263.1692 |  | LMs at 6 5ths Fort Lupton times 1.15 for altitude/capacity adjust…EA at ST MW ratio.
| Piping | 1581101 |  |  |  | 2181919.38 | 643386.4838 |  | LMs at 6 5ths Fort Lupton times 1.15 for altitude/capacity adjust…EA at ST MW ratio.
| Valves | 821016 |  |  |  | 1133002.08 | 334090.3569 |  | LMs at 6 5ths Fort Lupton times 1.15 for altitude/capacity adjust…EA at ST MW ratio.
| All Electrical Equipment |  |  | 1042359 |  | 0
| All Mechanical Equipment |  |  | 1313177 |  | 0 |  | 26966529.4177
Construction Services
| General Conditions Incl. O.H. & Profit | 7992461 |  | 876363 |  | 12787937.6 |  |  | 1.6 times Fort Lup;ton
| Field Office Expenses | 631345 |  | 115668 |  | 1010152 |  |  | 1.6 times Fort Lup;ton
| Field Office Personnel | 1485960 |  | 528209 |  | 2377536 |  |  | 1.6 times Fort Lup;ton
| Misc General Field Conditions | 575400 |  | 91400 |  | 920640 |  |  | 1.6 times Fort Lup;ton
| Electrical Subcontractor Indirects | 3863511 |  |  |  | 6181617.6 |  |  | 1.6 times Fort Lup;ton
| Construction Equipment | 1851592 |  | 323144 |  | 2962547.2 |  |  | 1.6 times Fort Lup;ton
| Mobilization | 627500 |  | 85930 |  | 1004000 |  |  | 1.6 times Fort Lup;ton
| Site Development | 1277099 |  | 132804 |  | 2043358.4 |  |  | 1.6 times Fort Lup;ton
| Foundations | 2197997 |  | 292038 |  | 4395994 |  |  | 2.0 times Fort Lupton due to foundations on EA
| Structural Steel | 115220 |  | 52169 |  | 184352 |  |  | 1.6 times Fort Lup;ton
| Building & Erection | 918366 |  | 137100 |  | 1469385.6 |  |  | 1.6 times Fort Lup;ton
| Equipment Installation - Mechanical | 1416979 |  | 328482 |  | 2267166.4 |  |  | 1.6 times Fort Lup;ton
| Process Piping | 1827670 |  | 509235 |  | 2924272 |  |  | 1.6 times Fort Lup;ton
| Equipment Installation - Electrical | 782972 |  | 92717 |  | 1252755.2 |  |  | 1.6 times Fort Lup;ton
| Electrical - Wire, Cable & Terminations | 1160792 |  | 268021 |  | 1857267.2 |  |  | 1.6 times Fort Lup;ton
| Testing, Calibration | 348908 |  | 205653 |  | 558252.8 |  |  | 1.6 times Fort Lup;ton
Change Orders & Contingency |  | 3273375 |  |  |  | 9200000 |  |  | 5% of subtotal
SUB TOTAL
| PROCUREMENT & CONST | 120212256 |  | 20291731 |  | 199493187.418
Engineering |  | 3349943 |  | 510482 |  | 6699886 |  |  | 2.0 times Fort Lupton
| SUB TOTAL "EPC" | 123562199 |  | 20802213 |  | 206193073.418 |  |  |  | 280415943.998
| POWER GENERATION @ SEA LEVEL | 304000 | kW | 40000 | kW | 510000 | kW
|  | 406.4546 | $/KW | 520.0553 | $/KW | 404.3001 | $/KW
Other Internal Costs
| Project Management, Expenses & Consultants | 2908124 |  | 152624 |  | 5816248 |  |  | 2.0 times Fort Lupton
| O & M Start Up Personnel & Expenses | 2573334 |  | 159520 |  | 5146668 |  |  | 2.0 times Fort Lupton
| Spare Parts | 1200000 |  | 128194 |  | 4000000 |  |  | Includes cost of spare LM shared amoung 2.5 sites
| Insurance | 1083998 |  | 52565 |  | 2167996 |  |  | 2.0 times Fort Lupton
| Allowanced for Sales & Use Taxes |  |  |  |  | 6185792.2025
| SUB TOTAL OTHER COSTS | 7765456 |  | 492903 |  | 23316704.2025
GRAND TOTAL POWER PLANT |  | 131327655 |  | 21295116 |  | 229509777.6205
[6 empty] | 450.0192 | $/KW

## Fixed O&M
STANDARD 1EA + 6 LM
SUMMARY OF ANNUAL OPERATION & MAINTENANCE
Prepared by P. Steinway
(Amounts in US$ Actual)
|  |  | Average |  | Total
Personnel Expenses |  |  | Annual | Positions | Annual
|  | Wages Manager | 90000 | 1 | 90000
|  | Wages Supervisors | 65000 | 2 | 130000
|  | Wage Administration | 28000 | 1 | 28000
|  | Wages Operations | 50000 | 12 | 600000
|  | Wages Maintenance | 60000 | 6 | 360000
|  | Wages Subtotal |  | 22 | 1208000
|  | Burden Expenses @ 45% |  |  | 543600
|  | Burdened Wages |  |  | 1751600
|  | G&A @ 15% |  |  | 262740
|  | Fees |  |  | 250000
|  |  | Sub Total Personnel |  | 2264340
Operation & Maintenance
Semi Variable (Values assume a 50% Capacity Factor) 1
|  | Equipment Parts |  |  | 750000
|  | Expendables |  |  | 250000
|  |  | Sub Total Semi Variable O&M |  | 1000000
Fixed
|  | Outside Services |  |  | 125000
|  | Water Treatment |  |  | 550000
|  | Office |  |  | 72000
|  | Training |  |  | 25000
|  | Other |  |  | 125000
|  |  | Sub Total Fixed O&M |  | 897000
|  |  | Total |  | 4161340
| 1 | Can alter for capacity factor as follows: Cost *(1 - ((50% - CF) * .6)) Not currently implemented.

## Performance
Orion Performance Summary 10/12/99: (Expect Update to this by 10/29/99)
|  |  |  | No Chilling |  | with Chilling |  | with Chilling
|  |  |  | No STG Upgrade |  | No STG Upgrade |  | with STG Upgrade
|  |  |  | Estd Net | Estd Net | Estd Net | Estd Net | Estd Net | Estd Net
| Ambient | RH | Config | Output * | Heat Rate | Output * | Heat Rate | Output * | Heat Rate
Load | Temp (F) | (%) | 7/LM/Stg | (mwe) | (btu/kwe) | (mwe) | (btu/kwe) | (mwe) | (btu/kwe)
Peak | -20 | 60 | 162 F | 541.7509 | 8445.5044 | 541.7509 | 8445.5044 | 556.9078 | 8607.9512
Peak | 20 | 60 | 162 F | 542.4057 | 8199.7301 | 542.4057 | 8199.7301 | 557.758 | 8378.6945
Peak | 60 | 60 | 162 F | 504.6358 | 8288.987 | 516.7818 | 8253.0728 | 533.6472 | 8456.2312
Peak | 80 | 40 | 162 F | 466.9868 | 8471.0747 | 513.3952 | 8248.4694 | 530.4359 | 8453.624
Peak | 95 | 34.5 | 162 F | 432.0566 | 8637.8612 | 502.4226 | 8323.7711 | 519.1389 | 8530.7247
Peak | 105 | 27 | 162 F | 406.134 | 8567.0411 | 488.5098 | 8475.9503 | 503.1484 | 8827.237
Swing | 20 | 60 | 162 N | 444.3509 | 7229.826 | 444.3509 | 7229.826 | 444.3509 | 7229.826
Swing | 40 | 60 | 162 N | 438.7698 | 7220.0501 | 438.7698 | 7220.2096 | 438.7698 | 7220.2096
Swing | 60 | 60 | 162 N | 407.1453 | 7284.6724 | 419.449 | 7271.3388 | 419.449 | 7271.3388
Swing | 80 | 40 | 162 N | 367.7774 | 7394.6368 | 415.9993 | 7285.5879 | 415.9993 | 7285.5879
Swing | 95 | 34.5 | 162 N | 332.8132 | 7560.8177 | 405.8435 | 7326.9345 | 405.8435 | 7326.9345
Min | -20 | 60 | 101 N | 75.7255 | 7370.5715 | 75.7255 | 8672.115 | 75.7255 | 8672.115
Min | 20 | 60 | 101 N | 70.7311 | 8635.5185 | 70.7311 | 8635.5185 | 70.7311 | 8635.5185
Min | 60 | 60 | 101 N | 62.8311 | 8919.1454 | 62.7443 | 9060.5907 | 62.7443 | 9060.5907
Min | 80 | 40 | 101 N | 59.7264 | 8937.419 | 61.1329 | 9080.2152 | 61.1329 | 9080.2152
Min | 95 | 34.5 | 101 N | 56.9123 | 9040.2307 | 60.1653 | 9026.7996 | 60.1653 | 9026.7996
* Includes 6% for general parasitic and transformer losses plus chiller parasitic loads depending on the amount of chilling being done.

## Variable O&M
Variable O&M Costs
(Amounts in US$ Actual)
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
|  |  | 2001-12-31 | 2002-12-31 | 2003-12-31 | 2004-12-31 | 2005-12-31 | 2006-12-31 | 2007-12-31 | 2008-12-31 | 2009-12-31 | 2010-12-31 | 2011-12-31 | 2012-12-31 | 2013-12-31 | 2014-12-31 | 2015-12-31 | 2016-12-31 | 2017-12-31 | 2018-12-31 | 2019-12-31 | 2020-12-31 | 2021-12-31 | 2022-12-31 | 2023-12-31 | 2024-12-31 | 2025-12-31
Total MWh |  |  | 327832.4689 | 1049265.6765 | 1200037.3398 | 1350809.0031 | 1501580.6664 | 1614700.8439 | 1727821.0213 | 1840941.1988 | 1954061.3763 | 2067181.5537 | 2163865.0516 | 2260548.5494 | 2357232.0472 | 2453915.5451 | 2550599.0429 | 2647282.5407 | 2743966.0386 | 2743966.0386 | 2743966.0386 | 2743966.0386 | 2743966.0386 | 2743966.0386 | 2743966.0386 | 2743966.0386 | 2743966.0386
Raw Water |  | 0.72 | 2001-12-31: thousand gals per MWh
| Gallons Used ('000s) |  | 236039.3776 | 755471.2871 | 864026.8847 | 972582.4822 | 1081138.0798 | 1162584.6076 | 1244031.1354 | 1325477.6631 | 1406924.1909 | 1488370.7187 | 1557982.8371 | 1627594.9556 | 1697207.074 | 1766819.1925 | 1836431.3109 | 1906043.4293 | 1975655.5478 | 1975655.5478 | 1975655.5478 | 1975655.5478 | 1975655.5478 | 1975655.5478 | 1975655.5478 | 1975655.5478 | 1975655.5478
| Cost per 1,000 gals |  | 1 | 1.025 | 1.0506 | 1.0769 | 1.1038 | 1.1314 | 1.1597 | 1.1887 | 1.2184 | 1.2489 | 1.2801 | 1.3121 | 1.3449 | 1.3785 | 1.413 | 1.4483 | 1.4845 | 1.5216 | 1.5597 | 1.5987 | 1.6386 | 1.6796 | 1.7216 | 1.7646 | 1.8087
| Inflation Factor | 2.5%
| Raw Water Total Cost |  | 236039.3776 | 774358.0693 | 907768.2457 | 1047364.9572 | 1193374.149 | 1315357.7732 | 1442694.7197 | 1575576.415 | 1714200.5108 | 1858771.0761 | 1994349.7499 | 2135545.6255 | 2282554.8263 | 2435579.7711 | 2594829.3663 | 2760519.204 | 2932871.7652 | 3006193.5593 | 3081348.3983 | 3158382.1082 | 3237341.6609 | 3318275.2025 | 3401232.0825 | 3486262.8846 | 3573419.4567
Demineralized Water |  | 0.06 | 2001-12-31: thousand gals per MWh
| Gallons Used ('000s) |  | 19669.9481 | 62955.9406 | 72002.2404 | 81048.5402 | 90094.84 | 96882.0506 | 103669.2613 | 110456.4719 | 117243.6826 | 124030.8932 | 129831.9031 | 135632.913 | 141433.9228 | 147234.9327 | 153035.9426 | 158836.9524 | 164637.9623 | 164637.9623 | 164637.9623 | 164637.9623 | 164637.9623 | 164637.9623 | 164637.9623 | 164637.9623 | 164637.9623
| Cost per 1,000 gals |  | 1 | 1.025 | 1.0506 | 1.0769 | 1.1038 | 1.1314 | 1.1597 | 1.1887 | 1.2184 | 1.2489 | 1.2801 | 1.3121 | 1.3449 | 1.3785 | 1.413 | 1.4483 | 1.4845 | 1.5216 | 1.5597 | 1.5987 | 1.6386 | 1.6796 | 1.7216 | 1.7646 | 1.8087
| Inflation Factor | 2.5%
| Demineralized Water Total Cost |  | 19669.9481 | 64529.8391 | 75647.3538 | 87280.4131 | 99447.8458 | 109613.1478 | 120224.56 | 131298.0346 | 142850.0426 | 154897.5897 | 166195.8125 | 177962.1355 | 190212.9022 | 202964.9809 | 216235.7805 | 230043.267 | 244405.9804 | 250516.1299 | 256779.0332 | 263198.509 | 269778.4717 | 276522.9335 | 283436.0069 | 290521.907 | 297784.9547
Sewer |  | 0.09 | 2001-12-31: thousand gals per MWh
| Gallons Used ('000s) |  | 29504.9222 | 94433.9109 | 108003.3606 | 121572.8103 | 135142.26 | 145323.0759 | 155503.8919 | 165684.7079 | 175865.5239 | 186046.3398 | 194747.8546 | 203449.3694 | 212150.8843 | 220852.3991 | 229553.9139 | 238255.4287 | 246956.9435 | 246956.9435 | 246956.9435 | 246956.9435 | 246956.9435 | 246956.9435 | 246956.9435 | 246956.9435 | 246956.9435
| Cost per 1,000 gals |  | 0.5 | 0.5125 | 0.52531 | 0.53845 | 0.55191 | 0.5657 | 0.57985 | 0.59434 | 0.6092 | 0.62443 | 0.64004 | 0.65604 | 0.67244 | 0.68926 | 0.70649 | 0.72415 | 0.74225 | 0.76081 | 0.77983 | 0.79933 | 0.81931 | 0.83979 | 0.86079 | 0.88231 | 0.90436
| Inflation Factor | 2.5%
| Sewer Total Cost |  | 14752.4611 | 48397.3793 | 56735.5154 | 65460.3098 | 74585.8843 | 82209.8608 | 90168.42 | 98473.5259 | 107137.5319 | 116173.1923 | 124646.8594 | 133471.6016 | 142659.6766 | 152223.7357 | 162176.8354 | 172532.4502 | 183304.4853 | 187887.0975 | 192584.2749 | 197398.8818 | 202333.8538 | 207392.2002 | 212577.0052 | 217891.4303 | 223338.716
Total Variable O&M |  |  | 270461.7869 | 887285.2877 | 1040151.1149 | 1200105.6801 | 1367407.8791 | 1507180.7818 | 1653087.6997 | 1805347.9755 | 1964188.0853 | 2129841.8581 | 2285192.4218 | 2446979.3626 | 2615427.4051 | 2790768.4877 | 2973241.9822 | 3163094.9212 | 3360582.2309 | 3444596.7867 | 3530711.7064 | 3618979.499 | 3709453.9865 | 3802190.3362 | 3897245.0946 | 3994676.2219 | 4094543.1275
$/MWh |  |  | 0.825 | 0.84562 | 0.86677 | 0.88843 | 0.91065 | 0.93341 | 0.95675 | 0.98067 | 1.0052 | 1.0303 | 1.0561 | 1.0825 | 1.1095 | 1.1373 | 1.1657 | 1.1948 | 1.2247 | 1.2553 | 1.2867 | 1.3189 | 1.3519 | 1.3857 | 1.4203 | 1.4558 | 1.4922
Misc. Expendables ($.MWh) |  |  | 0.17 | 0.17425 | 0.17861 | 0.18307 | 0.18765 | 0.19234 | 0.19715 | 0.20208 | 0.20713 | 0.21231 | 0.21761 | 0.22305 | 0.22863 | 0.23435 | 0.24021 | 0.24621 | 0.25237 | 0.25868 | 0.26514 | 0.27177 | 0.27856 | 0.28553 | 0.29267 | 0.29998 | 0.30748
Water, Sewer, Demin and Misc. Variable O&M ($/MWh) |  |  | 0.995 | 1.0199 | 1.0454 | 1.0715 | 1.0983 | 1.1258 | 1.1539 | 1.1827 | 1.2123 | 1.2426 | 1.2737 | 1.3055 | 1.3382 | 1.3716 | 1.4059 | 1.4411 | 1.4771 | 1.514 | 1.5519 | 1.5907 | 1.6304 | 1.6712 | 1.713 | 1.7558 | 1.7997