## Wallingford
Project: Wallingford Fuel Cells Power Project (10 Cells) | [10 empty] | Date: October 26, 2000
Wage Rate: (Union Labor - Loaded) | 80
Plant Capacity | 21.2 | MW | [7 empty] | REV.No.1
|  |  |  | LABOR COST |  |  |  | MATERIAL COST |  | S/C & OTHER COST
DESCRIPTION | QUANTITY | UOM | TOTAL COST | UNIT MH | MH | WAGE RATE | TOTAL | UNIT | TOTAL | UNIT | TOTAL
FCE Scope
Fuel Cells - $68,772K | 10 | EA | 0 |  |  | 80 | 0 |  | 0 |  | 0
Fuel Cell Installation -$275K | 10 | EA | 0 |  |  | 80 | 0 |  | 0 |  | 0
Fuel Cell Interconnects - $2,438K | 10 | EA | 0 |  |  | 80 | 0 |  | 0 |  | 0
Fuel Cell Equipment Foundations; includes excavation & backfill - $1,700K | 2000 | CY | 0 |  |  | 80 | 0 |  | 0 |  | 0
Electrical Equipment
125V DC Station Service Battery including Batttery Charger & Switch Board | 1 | EA | 83600 | 170 | 170 | 80 | 13600 | 70000 | 70000 |  | 0
115 KV Switch yard (Brkrs, Disconnects,PT,CTS etc.) | 1 | EA | 194000 | 300 | 300 | 80 | 24000 | 170000 | 170000 |  | 0
Low Voltage MCC; 480V, 1200A, 3 Phase | 1 | EA | 116000 | 200 | 200 | 80 | 16000 | 100000 | 100000 |  | 0
Medium Voltage Switchgear w/ 1200A Breakers | 1 | EA | 516000 | 200 | 200 | 80 | 16000 | 500000 | 500000 |  | 0
Protective Relay Panel; HV Circuit Breaker & Disconnects | 1 | EA | 83000 | 100 | 100 | 80 | 8000 | 75000 | 75000 |  | 0
Dual Revenue Metering System | 2 | EA | 176000 | 100 | 200 | 80 | 16000 | 80000 | 160000 |  | 0
Fuel Cell Generator Step-up Transformer; 3750 kVA, 480V-13.8kV, 3 Phase, 60 Hz | 10 | EA | 596000 | 120 | 1200 | 80 | 96000 | 50000 | 500000 |  | 0
Distribution Transformer; 1000 kVA, 13.8kV-480V, 3 Phase, 60 Hz | 1 | EA | 28000 | 100 | 100 | 80 | 8000 | 20000 | 20000 |  | 0
Main Step-up Transformer | 1 | EA | 428000 | 350 | 350 | 80 | 28000 | 400000 | 400000 |  | 0
A-Frame Twr w/115kV | 1 | EA | 32000 | 150 | 150 | 80 | 12000 | 20000 | 20000 |  | 0
Uninterruptible Power System | 1 | EA | 38000 | 100 | 100 | 80 | 8000 | 30000 | 30000 |  | 0
Bus Duct | 750 | LF | 191250 | 1 | 750 | 80 | 60000 | 175 | 131250 |  | 0
Subtotal Electrical Equipment |  |  | 2481850 |  | 3820 |  | 305600 |  | 2176250 |  | 0
Electircal Bulks
Wire & Cable
THHN 125A (To Switchgear Bldg) | 3000 | LF | 92400 | 0.135 | 405 | 80 | 32400 | 20 | 60000 |  | 0
MV Cable / 2000 Amp | 200 | LF | 43200 | 0.2 | 40 | 80 | 3200 | 200 | 40000 |  | 0
HV Cable | 200 | LF | 43200 | 0.2 | 40 | 80 | 3200 | 200 | 40000 |  | 0
Instrument Cable | 3000 | LF | 10200 | 0.03 | 90 | 80 | 7200 | 1 | 3000
Grounding Grid | 1 | LS | 100000 | 840 | 840 | 80 | 67200 | 32800 | 32800 |  | 0
Exterior Lighting | 1 | LS | 156000 | 1200 | 1200 | 80 | 96000 | 60000 | 60000 |  | 0
Electric Heat Tracing | 3300 | LF | 21780 | 0.02 | 66 | 80 | 5280 | 5 | 16500 |  | 0
Grid Interconnect | 1 | LS | 250000 |  |  | 80 | 0 |  | 0 | 250000 | 250000
Cathodic Protection Allowance | 1 | LS | 40000 |  |  | 80 | 0 |  | 0 | 40000 | 40000
Subtotal Electrical Bulks |  |  | 756780 |  | 2681 |  | 214480 |  | 252300 |  | 290000
CIVIL/STRUCTURAL
Sitework, Scarfiy & Recompact | 2000 | CY | 32000 | 0.2 | 400 | 80 | 32000 | 0 | 0 |  | 0
Excavation/Backfill Foundations | 350 | CY | 5600 | 0.2 | 70 | 80 | 5600 |  | 0 |  | 0
Pipe Trenching (for Gas & Utility U / G Piping) | 3600 | LF | 86400 | 0.3 | 1080 | 80 | 86400 |  | 0 |  | 0
Fence | 1400 | LF | 55720 | 0.3 | 420 | 80 | 33600 | 15.8 | 22120 |  | 0
Plant Road | 6000 | SY | 108000 | 0.1 | 600 | 80 | 48000 | 10 | 60000 |  | 0
Piling; 12" Precast, Prestressed, 50' long | 10000 | LF | 300000 | 0 | 0 | 80 | 0 |  | 0 | 30 | 300000
Concrete
Electrical Trench 6 Feet Wide | 170 | CY | 197200 | 12 | 2040 | 80 | 163200 | 200 | 34000 |  | 0
Main Step-up Transformer Foundation | 20 | CY | 16800 | 8 | 160 | 80 | 12800 | 200 | 4000 |  | 0
Fuel Cell Step-up Transformer Foundations (10 Each) | 100 | CY | 100000 | 10 | 1000 | 80 | 80000 | 200 | 20000 |  | 0
A-Frame Twr Foundation | 40 | CY | 27200 | 6 | 240 | 80 | 19200 | 200 | 8000 |  | 0
Misc. Electrical Fdns | 50 | CY | 42000 | 8 | 400 | 80 | 32000 | 200 | 10000 |  | 0
Slab @ Grade | 500 | CY | 315000 | 6 | 3000 | 80 | 240000 | 150 | 75000 |  | 0
Ductbank, Sand Fill | 300 | CY | 9300 | 0.2 | 60 | 80 | 4800 | 15 | 4500 |  | 0
Subtotal Civil/Structural |  |  | 1295220 |  | 9470 |  | 757600 |  | 237620 |  | 300000
UTILITIES
Fuel Gas Pipeline Tie-in (6") | 2800 | LF | 526400 | 2 | 5600 | 80 | 448000 | 28 | 78400 |  | 0
Gas Metering Stations | 10 | EA | 130000 | 100 | 1000 | 80 | 80000 | 5000 | 50000 |  | 0
City Water Connections (3") | 400 | LF | 43200 | 1.2 | 480 | 80 | 38400 | 12 | 4800 |  | 0
Municiple Waste Water Connection (4") | 400 | LF | 52000 | 1.4 | 560 | 80 | 44800 | 18 | 7200 |  | 0
Utility Distribution (<2") | 3300 | LF | 214500 | 0.75 | 2475 | 80 | 198000 | 5 | 16500 |  | 0
Subtotal Utilities |  |  | 966100 |  | 10115 |  | 809200 |  | 156900 |  | 0
BUILDINGS
Switchgear Building; 20'x60'; Lighting & HVAC | 1200 | SF | 180000 |  |  |  | 0 |  | 0 | 150 | 180000
Control Room/Shop/Admin Facility; 20'x30'; Lighting & HVAC | 600 | SF | 120000 |  |  |  | 0 |  | 0 | 200 | 120000
Subtotal Buildings |  |  | 300000 |  | 0 |  | 0 |  | 0 |  | 300000
Labor Productivity Adjustment(New England Union vs Gulf Coast) | 20% |  | 417376 |  | 5217.2 | 80 | 417376
Subtotal Direct Costs |  |  | 6217326 |  | 26086 |  | 2086880 |  | 2823070 |  | 890000
Engineering (Provided by Engineering & Adjusted to include Piling Design) | 1 LS |  | 450000
Indirect Costs
Project Management | 7.5% | of Direct | 466299.45
Construction Indirects | 6% | of Direct | 373039.56
Startup & Commissioning |  |  | 50000
Warranty Allowance |  |  | 50000
Subtotal Indirect Costs |  |  | 939339.01
Subtotal Project Costs |  |  | 7606665.01
Escalation | 10.5% | of Direct | 608994.75 |  |  |  | 219122.4 |  | 296422.35 |  | 93450
Contingency (Recommended 15 %) | 10% | of Direct | 821565.976
Profit ( Recommended 8 %) | 5% | of Direct | 451861.2868
Total Project Costs |  |  | 9489087.0228
|  |  | 447.5984 | /KW

## Midcon
Project: Midcon Fuel Cells Power Project (12 Cells) | [10 empty] | Date: October 26, 2000
Wage Rate: (Union Labor - Loaded) | 80
Plant Capacity | 28.8 | MW | [7 empty] | REV No.1
DESCRIPTION | QUANTITY | UOM | TOTAL COST | LABOR COST |  |  |  | MATERIAL COST |  | S/C & OTHER COST
|  |  |  | UNIT MH | MH | WAGE RATE | TOTAL | UNIT | TOTAL | UNIT | TOTAL
FCE Scope
Fuel Cells - $70,728K | 12 | EA | 0 |  |  |  | 0 |  | 0 |  | 0
Fuel Cell Installation - $330K | 12 | EA | 0 |  |  |  | 0 |  | 0 |  | 0
Fuel Cell Interconnects - $2,925K | 12 | EA | 0 |  |  |  | 0 |  | 0 |  | 0
Fuel Cell Equipment Foundations; includes excavation & backfill - $2040K | 2400 | CY | 0 |  |  | 80 | 0 |  | 0 |  | 0
Electrical Equipment
125V DC Station Service Battery including Batttery Charger & Switch Board | 1 | EA | 83600 | 170 | 170 | 80 | 13600 | 70000 | 70000 |  | 0
115 KV Switch yard (Brkrs, Disconnects,PT,CTS etc.) | 1 | EA | 194000 | 300 | 300 | 80 | 24000 | 170000 | 170000 |  | 0
Low Voltage MCC; 480V, 1200A, 3 Phase | 1 | EA | 116000 | 200 | 200 | 80 | 16000 | 100000 | 100000 |  | 0
Medium Voltage Switchgear w/ 1200A Breakers | 1 | EA | 516000 | 200 | 200 | 80 | 16000 | 500000 | 500000 |  | 0
Protective Relay Panel; HV Circuit Breaker & Disconnects | 1 | EA | 83000 | 100 | 100 | 80 | 8000 | 75000 | 75000 |  | 0
Dual Revenue Metering System | 2 | EA | 176000 | 100 | 200 | 80 | 16000 | 80000 | 160000 |  | 0
Fuel Cell Generator Step-up Transformer; 3750 kVA, 480V-13.8kV, 3 Phase, 60 Hz | 12 | EA | 715200 | 120 | 1440 | 80 | 115200 | 50000 | 600000 |  | 0
Distribution Transformer; 1000 kVA, 13.8kV-480V, 3 Phase, 60 Hz | 1 | EA | 29600 | 120 | 120 | 80 | 9600 | 20000 | 20000 |  | 0
Main Step-up Transformer | 1 | EA | 428000 | 350 | 350 | 80 | 28000 | 400000 | 400000 |  | 0
A-Frame Twr w/115kV | 1 | EA | 32000 | 150 | 150 | 80 | 12000 | 20000 | 20000 |  | 0
Uninterruptible Power System | 1 | EA | 38000 | 100 | 100 | 80 | 8000 | 30000 | 30000 |  | 0
Bus Duct | 900 | LF | 229500 | 1 | 900 | 80 | 72000 | 175 | 157500 |  | 0
Subtotal Electrical Equipment |  |  | 2640900 |  | 4230 |  | 338400 |  | 2302500 |  | 0
Electircal Bulks
Wire & Cable
THHN 125A (To Switchgear Bldg) | 3040 | LF | 93632 | 0.135 |  | 80 | 32832 | 20 | 60800 |  | 0
MV Cable / 2000 Amp | 200 | LF | 43200 | 0.2 |  | 80 | 3200 | 200 | 40000 |  | 0
HV Cable | 200 | LF | 43200 | 0.2 |  | 80 | 3200 | 200 | 40000 |  | 0
Instrument Cable | 3040 | LF | 10336 | 0.03 | 91.2 | 80 | 7296 | 1 | 3040
Grounding Grid ( $10,000 per Cell for 12 Cells) | 1 | LS | 120000 | 1000 | 1000 | 80 | 80000 | 32800 | 40000 |  | 0
Exterior Lighting | 1 | LS | 187200 | 1440 | 1440 | 80 | 115200 | 72000 | 72000 |  | 0
Electric Heat Tracing | 3500 | LF | 23100 | 0.02 | 70 | 80 | 5600 | 5 | 17500 |  | 0
Grid Interconnect | 1 | LS | 250000 |  |  | 80 | 0 |  | 0 | 250000 | 250000
Cathodic Protection Allowance | 1 | LS | 40000 |  |  | 80 | 0 |  | 0 | 40000 | 40000
Subtotal Electrical Bulks |  |  | 810668 |  | 2601.2 |  | 247328 |  | 273340 |  | 290000
CIVIL/STRUCTURAL
Sitework, Scarfiy & Recompact | 2600 | CY | 41600 | 0.2 | 520 | 80 | 41600 | 0 | 0 |  | 0
Excavation/Backfill Foundations | 400 | CY | 6400 | 0.2 | 80 | 80 | 6400 |  | 0 |  | 0
Pipe Trenching (for Gas & Utility U / G Piping) | 2900 | LF | 69600 | 0.3 | 870 | 80 | 69600 |  | 0 |  | 0
Fence | 1500 | LF | 59700 | 0.3 | 450 | 80 | 36000 | 15.8 | 23700 |  | 0
Plant Road | 6000 | SY | 108000 | 0.1 | 600 | 80 | 48000 | 10 | 60000 |  | 0
Concrete
Electrical Trench 6 Feet Wide | 280 | CY | 324800 | 12 | 3360 | 80 | 268800 | 200 | 56000 |  | 0
Main Step-up Transformer Foundation | 20 | CY | 16800 | 8 | 160 | 80 | 12800 | 200 | 4000 |  | 0
Fuel Cell Step-up Transformer Foundations (12 Each) | 120 | CY | 120000 | 10 | 1200 | 80 | 96000 | 200 | 24000 |  | 0
A-Frame Twr Foundation | 40 | CY | 27200 | 6 | 240 | 80 | 19200 | 200 | 8000 |  | 0
Misc. Electrical Fdns | 60 | CY | 50400 | 8 | 480 | 80 | 38400 | 200 | 12000 |  | 0
Slab @ Grade | 600 | CY | 378000 | 6 | 3600 | 80 | 288000 | 150 | 90000 |  | 0
Ductbank, Sand Fill | 290 | CY | 8990 | 0.2 | 58 | 80 | 4640 | 15 | 4350 |  | 0
Subtotal Civil/Structural |  |  | 1211490 |  | 11618 |  | 929440 |  | 282050 |  | 0
UTILITIES
Fuel Gas Pipeline Tie-in (6") | 980 | LF | 184240 | 2 | 1960 | 80 | 156800 | 28 | 27440 |  | 0
Gas Metering Stations | 12 | EA | 156000 | 100 | 1200 | 80 | 96000 | 5000 | 60000 |  | 0
City Water Connections (3") | 980 | LF | 105840 | 1.2 | 1176 | 80 | 94080 | 12 | 11760 |  | 0
Municiple Waste Water Connection (4") | 980 | LF | 127400 | 1.4 | 1372 | 80 | 109760 | 18 | 17640 |  | 0
Utility Distribution (<2") | 3500 | LF | 227500 | 0.75 | 2625 | 80 | 210000 | 5 | 17500 |  | 0
Subtotal Utilities |  |  | 800980 |  | 8333 |  | 666640 |  | 134340 |  | 0
BUILDINGS
Switchgear Building; 20'x80'; Lighting & HVAC | 1600 | SF | 240000 |  |  |  | 0 |  | 0 | 150 | 240000
Control Room/Shop/Admin Facility; 20'x30'; Lighting & HVAC | 600 | SF | 120000 |  |  |  | 0 |  | 0 | 200 | 120000
Subtotal Buildings |  |  | 360000 |  | 0 |  | 0 |  | 0 |  | 360000
Labor Productivity Adjustment(New England Union vs Gulf Coast) | 20% |  | 428515.2 |  | 5356.44 | 80 | 428515.2
Subtotal Direct Costs |  |  | 6252553.2 |  | 26782.2 |  | 2181808 |  | 2992230 |  | 650000
Engineering (Provided by Engineering)) | 1 LS |  | 450000
Indirect Costs
Project Management | 7.5% | of Direct | 468941.49
Construction Indirects | 6% | of Direct | 375153.192
Startup & Commissioning |  |  | 60000
Warranty Allowance |  |  | 50000
Subtotal Indirect Costs |  |  | 954094.682
Subtotal Project Costs |  |  | 7656647.882
Escalation | 10.5% | of Direct | 611523.99 |  |  |  | 229089.84 |  | 314184.15 |  | 68250
Contingency (Recommended 15 %) | 10% | of Direct | 826817.1872
Profit ( Recommended 8 %) | 5% | of Direct | 454749.453
Total Project Costs |  |  | 9549738.5122
|  |  | 331.5881 | /KW