## Fuel Oil Spec
1
MHI & CMI Minimum Requirements
Property | Value | Units | ASTM Test Method | This Fuel Oil Specification is based on:
Density (max) |  |  |  |  | * MHI input
Density (min) |  |  |  |  | * Engineering Input
API Gravity (max) | 32.1 |  |  |  | * Air Permit Requirements
API Gravity (min)
Specific Gravity (max)
Specific Gravity (min)
Kinematic Viscosity (max) | 5.8 | Cst | D445
Kinematic Viscosity (min) | 1.8 | Cst | D445
Flash Point (min) | 140 | deg F | D93
Pour Point (max) | 12 | deg F | D97
Reid Vapor Pressure (max) | 2 | psia
Water & Sediment (max) | 0.05 | % vol
Ash (max) | 0 | % weight
Sulfer (max) | 0.05 | % weight | D4294
Vanadium (max) | 0.05 | ppm (wt) | D3605
Sodium+Potassium (max from fuel+air+water) | 0.5 | ppm (wt) | D3605
Calcium (max) | 10 | ppm (wt) | D3605
Lead (max) | 1 | ppm (wt) | D3605
Barium, Manganese, and Phosphorus (max) | 2 | ppm (wt) | D3605
10% Carbon Residue (max) | 0.35 | % | D524 of D86
C/H Ratio | <6.6
Lower Heating Value (min) | 17460 | Btu/lbm | D4809-95
Higher Heating Value (min) | 18720 | Btu/lbm | D4809-95

## Comparison Specs
|  | 2 |  |  | 3 |  |  | 4
|  | Minimum Requirements w/ Adjusted Vanadium |  |  | Minimum Requirements w/ Adjusted Ash |  | Minimum Requirements w/ Adjusted Ash & Vanadium
Property | Value | Units | ASTM Test Method | Value | Units | ASTM Test Method | Value | Units | ASTM Test Method
Density (max)
Density (min)
API Gravity (max) | 32.1 |  |  | 32.1 |  |  | 32.1
API Gravity (min)
Specific Gravity (max)
Specific Gravity (min)
Kinematic Viscosity (max) | 5.8 | Cst | D445 | 5.8 | Cst | D445 | 5.8 | Cst | D445
Kinematic Viscosity (min) | 1.8 | Cst | D445 | 1.8 | Cst | D445 | 1.8 | Cst | D445
Flash Point (min) | 140 | deg F | D93 | 140 | deg F | D93 | 140 | deg F | D93
Pour Point (max) | 12 | deg F | D97 | 12 | deg F | D97 | 12 | deg F | D97
Reid Vapor Pressure (max) | 2 | psia |  | 2 | psia |  | 2 | psia
Water & Sediment (max) | 0.05 | % vol |  | 0.05 | % vol |  | 0.05 | % vol
Ash (max) | 0 | % weight |  | 0.01 | % weight |  | 0.01 | % weight
Sulfer (max) | 0.05 | % weight | D4294 | 0.05 | % weight | D4294 | 0.05 | % weight | D4294
Vanadium (max) | 0.5 | ppm (wt) | D3605 | 0.05 | ppm (wt) | D3605 | 0.5 | ppm (wt) | D3605
Sodium+Potassium (max from fuel+air+water) | 0.5 | ppm (wt) | D3605 | 0.5 | ppm (wt) | D3605 | 0.5 | ppm (wt) | D3605
Calcium (max) | 10 | ppm (wt) | D3605 | 10 | ppm (wt) | D3605 | 10 | ppm (wt) | D3605
Lead (max) | 1 | ppm (wt) | D3605 | 1 | ppm (wt) | D3605 | 1 | ppm (wt) | D3605
Barium, Manganese, and Phosphorus (max) | 2 | ppm (wt) | D3605 | 2 | ppm (wt) | D3605 | 2 | ppm (wt) | D3605
10% Carbon Residue (max) | 0.35 | % | D524 of D86 | 0.35 | % | D524 of D86 | 0.35 | % | D524 of D86
C/H Ratio | <6.6 |  |  | <6.6 |  |  | <6.6
Lower Heating Value (min) | 17460 | Btu/lbm | D4809-95 | 17460 | Btu/lbm | D4809-95 | 17460 | Btu/lbm | D4809-95
Higher Heating Value (min) | 18720 | Btu/lbm | D4809-95 | 18720 | Btu/lbm | D4809-95 | 18720 | Btu/lbm | D4809-95
Column 2 represents MHI requirements
Column 3 represents CMI requirements
Column 4 represents Air Permit requirements