## Sheet1
Date | Participants | Discussion
1999-06-02 | Robert Franson-Citzens John Cogan-Citizens Kenny Malter-Citizens Dale Moore-Citizens Laura Kunkel-Trigon Jeff Fawcett-TW (Mrkt) Earl Chandler-TW Ron Matthews-TW Ben Tanner- TW 3 Griffith Representatives | A preliminary design had been prepared by TW and it was discussed along with the general design criteria. Most of the discussion was on: if both pipelines needed to be tapped, Powerplant EIS and schedule, delivery pressure, volumes, site condition-proposed new 230 Kv overhead electric line, easements, need for a control valve to prevent over-pulls, if the valve would be set on flow control or pressure control, pressure drop through the proposed 6" control valve, if Citizens could get a pulse from the meter, gas odorization (sulfur content), and site security.
2000-01-04 | Robert Franson-Citzens Laura Kunkel-Trigon TW (names not documented) | Minimum flow rates were not understood in the original conference call. When Griffith provided the low flow requirements of 1,424 SCFH TW presented a strategy of handling without the additional runs. The estimate and maximum reimbursement amount in the executed Delivery Point Agreement were based on a single 10" meter run. Franson indicated that he would allow as long as operational difficulties were not encountered.
2000-01-06 | Draft Letter (Attached) | The low-flow strategy was reviewed internally by TW.
2000-02-01 | TW | Bid Drawing of the Station were plotted and soon after sent to Citizens for a custody review and for coordination with the proposed Citizens Facilities.
Start-Up Period | Citizens and TW Operations personnel | The TW Interconnect station came on line with a flow control valve along with a pressure override valve. The pressure settings were roughly 650psig to 950 psig, producing erratic swings in the delivery pressure.
Start-Up Period | Citizens, Trigon and TW Operations personnel | Per a request from Bobby Faulkner (Trigon), Citizens, request the tightening of the pressure swing that the TW Interconnect Station operated between. The new operational pressures were about 750 psig to 950 psig, but I don't think the station never operated under these conditions, because the plant was down.
Start-Up Period | Citizens and TW Operations personnel | Citizens' Brian Herzog requested that the pressure override be removed from the station, which it was for a while.
Start-Up Period | Citizens, Trigon and TW Operations personnel | After TW, Trigon, and Citizens observed Citizens Station controlling erratically, TW put the pressure override back into service due to concerns of over-pressuring Griffith's "customer owned piping"
August 17, 2001 | Citizens and TW Operations personnel | Citizens then requested TW to once again remove the pressure override from the station, and that is how the station operates today.
Early Nov. 2001 | Robert Franson talked to David Roensch. | Citizens requested TW to evaluate making a pressure cut at the TW Griffith Interconnect.
Late Nov. to early Dec. 2001 | Robert Franson, David Roensch. | Robert Franson left several messages inquiring if TW would honor the requested pressure cut.
2001-12-12 | Robert Franson, Sean Breen, Mark McConnell | Citizens made this pressure cut request to TW Marketing.
2001-12-13 | Robert Franson, Darrell Schoolcraft | Discussed the history of the design and operation of the station. Franson emailed a copy of the preliminary vibration report, Schoolcraft stated that TW would discuss the subject and let Citizens know by December 21, 2001.