## Fuel Cell Alt
6 Macro Runs
Macro Variable(s):
GT power as % of site rating (>=200 for power in kW)
Plant Net Output | 100% | 92.11% | 83.93% | 75.37% | 66.17% | 56.24%
Plant Net Heat Rate | 100% | 101.1% | 102.6% | 104.4% | 107% | 110.7%
Plant Net HHV Heat Rate [Btu / kWh] | 6958.59 | 7037.4 | 7141.74 | 7267.17 | 7443.66 | 7702.29
Plant Summary
Ambient pressure [psia] | 14.43 | 14.43 | 14.43 | 14.43 | 14.43 | 14.43
Ambient temperature [F] | 59 | 59 | 59 | 59 | 59 | 59
Ambient Relative Humidity [%] | 60 | 60 | 60 | 60 | 60 | 60
Plant gross output [kW] | 256905 | 236907 | 216155 | 194438 | 171089 | 145912
Plant net output [kW] | 250649 | 230879 | 210368 | 188912 | 165864 | 140976
Gross LHV heat rate [BTU/kWh] | 6116 | 6179 | 6262 | 6361 | 6501 | 6704
Net LHV heat rate [BTU/kWh] | 6269 | 6340 | 6434 | 6547 | 6706 | 6939
Plant gross elec eff [%] | 55.79 | 55.23 | 54.49 | 53.64 | 52.49 | 50.9
Plant net elec eff [%] | 54.43 | 53.82 | 53.03 | 52.12 | 50.88 | 49.18
PURPA eff [%] | 54.43 | 53.82 | 53.03 | 52.12 | 50.88 | 49.18
CHP eff [%] | 54.43 | 53.82 | 53.03 | 52.12 | 50.88 | 49.18
Power gen. eff on chargeable energy [%] | 54.43 | 53.82 | 53.03 | 52.12 | 50.88 | 49.18
Canadian Class 43 heat rate [BTU/kWh] | 6787 | 6856 | 6949 | 7059 | 7214 | 7439
Plant total fuel HHV input [kBtu/hr] | 1743542 | 1624264 | 1501982 | 1372479 | 1234206 | 1085437 | % Load | GE 7FA (CC) | FCE 2.0 MW Fuel Cell
Plant total fuel LHV input [kBtu/hr] | 1571306 | 1463810 | 1353608 | 1236898 | 1112285 | 978212 | 100% | 6958.59 | 6790
Fuel compressor [kW] | 0 | 0 | 0 | 0 | 0 | 0 | 92.11% | 7037.4 | 6790
Supercharging fan [kW] | 0 | 0 | 0 | 0 | 0 | 0 | 83.93% | 7141.74 | 6790
Electric chiller [kW] | 0 | 0 | 0 | 0 | 0 | 0 | 75.37% | 7267.17 | 6790
Miscellaneous GT aux. [kW] | 870 | 870 | 870 | 870 | 870 | 870 | 66.17% | 7443.66 | 6790
Boiler feedpump [kW] | 1436.1 | 1328.6 | 1212.9 | 1082.7 | 922.9 | 786 | 56% | 7702 | 6790
CW pump [kW] | 625.9 | 626.2 | 626.6 | 627 | 627.6 | 628.4
Cooling tower fan [kW] | 290.4 | 289.6 | 288.7 | 287.6 | 286.2 | 284.2
Miscellaneous ST aux. [kW] | 479.2 | 479.2 | 479.2 | 479.2 | 479.2 | 479.2 | % Load | GE 7FA (SC) | FCE 2.0 MW Fuel Cell
Transformer losses [kW] | 1284.5 | 1184.5 | 1080.8 | 972.2 | 855.4 | 729.6 | 100% | 9500 | 6790
All other auxiliaries [kW] | 601.9 | 581.9 | 561.2 | 539.4 | 516.1 | 490.9 | 90% | 9650 | 6790
Plant total auxiliaries [kW] | 4971 | 4843 | 4706 | 4554 | 4370 | 4207 | 80% | 10000 | 6790
GT fuel HHV/LHV ratio | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 70% | 10600 | 6790
DB fuel HHV/LHV ratio | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 60% | 11250 | 6790
GT Cycle Summary
GT shaft power [kW] | 168814 | 152723 | 136384 | 119763 | 102896 | 85773
GT shaft LHV eff [%] | 36.66 | 35.6 | 34.38 | 33.04 | 31.57 | 29.92
GT shaft heat rate [BTU/kWh] | 9308 | 9585 | 9925 | 10328 | 10810 | 11405
Compressor inlet massflow [lb/s] | 957.6 | 878.8 | 803.7 | 743.3 | 704.3 | 704.3
Compressor inlet temperature [F] | 59 | 59 | 59 | 59 | 59 | 59
Turbine inlet massflow [lb/s] | 845.7 | 776.4 | 710.2 | 656.6 | 621.4 | 619.7
Turbine inlet temperature [F] | 2420.9 | 2425.6 | 2423.1 | 2386.2 | 2292 | 2101.9
Turbine exhaust massflow [lb/s] | 977.9 | 897.7 | 821.2 | 759.3 | 718.7 | 716.9
Turbine exhaust temperature [F] | 1131.4 | 1161.9 | 1191.6 | 1200.4 | 1171 | 1073.5
GT fuel HHV input [kBtu/hr] | 1743542 | 1624264 | 1501982 | 1372479 | 1234206 | 1085437
GT fuel LHV input [kBtu/hr] | 1571306 | 1463810 | 1353608 | 1236898 | 1112285 | 978212
Exhaust gas molecular weight | 28.38 | 28.38 | 28.37 | 28.38 | 28.4 | 28.45
Exhaust gas N2+Ar mole percentage [%] | 75.34 | 75.29 | 75.26 | 75.3 | 75.44 | 75.76
Exhaust gas O2 mole percentage [%] | 12.63 | 12.51 | 12.43 | 12.52 | 12.93 | 13.84
Exhaust gas CO2 mole percentage [%] | 3.7 | 3.75 | 3.79 | 3.75 | 3.57 | 3.15
Exhaust gas H2O mole percentage [%] | 8.33 | 8.44 | 8.52 | 8.43 | 8.07 | 7.25
GT fuel flow [lb/s] | 20.28 | 18.9 | 17.47 | 15.97 | 14.36 | 12.63
Combustor steam injection [lb/s] | 0 | 0 | 0 | 0 | 0 | 0
Combustor water injection [lb/s] | 0 | 0 | 0 | 0 | 0 | 0
Inlet filter pressure loss [inch H2O] | 4 | 3.613 | 3.254 | 2.97 | 2.79 | 2.79
Total exhaust pressure loss [inch H2O] | 14 | 12 | 10.21 | 8.846 | 7.945 | 7.801
Fogging water massflow [lb/s] | 0 | 0 | 0 | 0 | 0 | 0
Number of chillers in plant
Nameplate capacity at standard conditions [ton]
Nameplate COP at standard conditions
Capacity at current heat balance [ton]
COP at current heat balance
Chilled water temperature [F]
Chilled water range [F]
Chilled water massflow [lb/s]
Desired air temperature drop [F]
Actual air temperature drop [F]
Coolant temperature [F]
Steam Cycle Summary
Gas temperature reaching HRSG [F] | 1129.4 | 1159.9 | 1189.6 | 1198.4 | 1169 | 1071.5
Stack temperature [F] | 213.1 | 207.2 | 200.9 | 195 | 190.6 | 189.7
Stack massflow [lb/s] | 977.9 | 897.7 | 821.2 | 759.3 | 718.7 | 716.9
ST shaft power [kW] | 91162 | 87115 | 82579 | 77359 | 70749 | 62585
Steam cycle gross eff [%] | 31.12 | 31.41 | 31.63 | 31.8 | 31.66 | 31.12
Net process heat output [kBtu/hr] | 0 | 0 | 0 | 0 | 0 | 0
HRSG eff [%] | 85.69 | 86.63 | 87.5 | 88.09 | 88.14 | 87.04
Total duct burner fuel flow [lb/s] | 0 | 0 | 0 | 0 | 0 | 0
Fuel HHV to duct burner(s) [kBtu/hr] | 0 | 0 | 0 | 0 | 0 | 0
Fuel LHV to duct burner(s) [kBtu/hr] | 0 | 0 | 0 | 0 | 0 | 0
HPT pressure before stop valve [psia] | 2101.1 | 1967.4 | 1829 | 1714.1 | 1575 | 1575
HPT temperature before stop valve [F] | 997.6 | 1000 | 1000 | 1000 | 1000 | 983.4
HPT massflow before stop valve [lb/s] | 101.7 | 94.77 | 87.75 | 82.01 | 74.87 | 69.56
HP superheater steam pressure [psia] | 2143.3 | 2006.4 | 1865.7 | 1748.2 | 1606.3 | 1601.6
HP superheater steam temperature [F] | 1001.3 | 1003.6 | 1003.5 | 1003.4 | 1003.3 | 986.5
HP superheater steam massflow [lb/s] | 101.7 | 94.77 | 87.75 | 82.01 | 74.87 | 69.56
HPB pinch temperature difference [F] | 36.19 | 34.11 | 31.78 | 29.88 | 28.24 | 26.94
Cold reheat pressure [psia] | 171.6 | 165.3 | 158.2 | 148.5 | 135.8 | 118.9
Cold reheat temperature [F] | 421.5 | 429.6 | 436.9 | 438.7 | 440.4 | 417
Cold reheat massflow [lb/s] | 100.7 | 93.83 | 86.88 | 81.19 | 74.12 | 68.86
Hot reheat admission pressure [psia] | 150 | 145 | 139.3 | 130.7 | 119.4 | 103.6
Hot reheat admission temperature [F] | 998.3 | 999.9 | 999.9 | 1006.9 | 999.9 | 980.2
Hot reheat admission massflow [lb/s] | 136.6 | 132.2 | 127.1 | 118.9 | 108.9 | 94.87
IP superheater steam pressure [psia] | 165.3 | 159.6 | 153 | 143.6 | 131.4 | 114.5
IP superheater steam temperature [F] | 845.1 | 845.3 | 843.8 | 843.2 | 835.1 | 824.8
IP superheater steam massflow [lb/s] | 35.95 | 32.06 | 28.47 | 25.82 | 24.46 | 26.01
IPB pinch temperature difference [F] | 36.12 | 32.36 | 28.84 | 26.2 | 24.83 | 26.33
LPB steam production rate [lb/s] | 14 | 12.31 | 10.75 | 9.564 | 8.901 | 9.143
LPB pinch temperature difference [F] | 18.02 | 16.03 | 14.16 | 12.72 | 11.91 | 12.22
Deaerator pressure [psia] | 17.19 | 17.19 | 16.76 | 15.69 | 14.4 | 12.75
Deaerator temperature [F] | 220 | 220 | 218.7 | 215.3 | 211 | 204.9
Condenser pressure [psia] | 1.121 | 1.068 | 1.013 | 0.9458 | 0.8681 | 0.7733
Condenser saturation temp [F] | 105.6 | 103.9 | 102.2 | 99.88 | 97.05 | 93.28
LPT exhaust mass flow [lb/s] | 146.6 | 140.3 | 133.6 | 125 | 114.8 | 102.2
Condenser coolant supply temp [F] | 69.43 | 69.29 | 69.12 | 68.85 | 68.45 | 67.79
Condenser coolant discharge temp [F] | 99.46 | 98.07 | 96.56 | 94.62 | 92.19 | 88.94
Condenser coolant massflow [lb/s] | 4967 | 4967 | 4967 | 4967 | 4967 | 4967
Stack gas molecular weight | 28.38 | 28.38 | 28.37 | 28.38 | 28.4 | 28.45
Stack gas N2+Ar mole percentage [%] | 75.34 | 75.29 | 75.26 | 75.3 | 75.44 | 75.76
Stack gas O2 mole percentage [%] | 12.63 | 12.51 | 12.43 | 12.52 | 12.93 | 13.84
Stack gas CO2 mole percentage [%] | 3.7 | 3.75 | 3.79 | 3.75 | 3.57 | 3.15
Stack gas H2O mole percentage [%] | 8.33 | 8.44 | 8.52 | 8.43 | 8.07 | 7.25
Duct burner exit temperature [F] | 1129.4 | 1159.9 | 1189.6 | 1198.4 | 1169 | 1071.5
Exhaust DT across main duct burner [F] | 0 | 0 | 0 | 0 | 0 | 0
Exhaust DT across HPB2 burner [F] | 0 | 0 | 0 | 0 | 0 | 0
Process Streams
Main HP process pressure [psia] | 2100 | 2006.4 | 1865.7 | 1748.2 | 1606.3 | 1601.6
Main HP process temperature [F] | 642.8 | 636.3 | 626 | 617 | 605.4 | 605
Main HP process massflow [lb/s] | 0 | 0 | 0 | 0 | 0 | 0
1st HP substream pressure [psia] | 650 | 650 | 650 | 650 | 650 | 650
1st HP substream temperature [F] | 494.9 | 494.9 | 494.9 | 494.9 | 494.9 | 494.9
1st HP substream massflow [lb/s] | 0 | 0 | 0 | 0 | 0 | 0
2nd HP substream pressure [psia] | 650 | 650 | 650 | 650 | 650 | 650
2nd HP substream temperature [F] | 494.9 | 494.9 | 494.9 | 494.9 | 494.9 | 494.9
2nd HP substream massflow [lb/s] | 0 | 0 | 0 | 0 | 0 | 0
Main IP process pressure [psia] | 159 | 159 | 159 | 159 | 159 | 159
Main IP process temperature [F] | 444.6 | 444.6 | 444.6 | 444.6 | 444.6 | 444.6
Main IP process massflow [lb/s] | 0 | 0 | 0 | 0 | 0 | 0
1st IP substream pressure [psia] | 50 | 50 | 50 | 50 | 50 | 50
1st IP substream temperature [F] | 281 | 281 | 281 | 281 | 281 | 281
1st IP substream massflow [lb/s] | 0 | 0 | 0 | 0 | 0 | 0
2nd IP substream pressure [psia] | 50 | 50 | 50 | 50 | 50 | 50
2nd IP substream temperature [F] | 281 | 281 | 281 | 281 | 281 | 281
2nd IP substream massflow [lb/s] | 0 | 0 | 0 | 0 | 0 | 0
LP process pressure [psia] | 57.32 | 57.32 | 55.27 | 51.46 | 47.22 | 42.39
LP process temperature [F] | 300 | 300 | 300 | 300 | 300 | 300
LP process massflow [lb/s] | 0 | 0 | 0 | 0 | 0 | 0
Main HPT bleed pressure [psia] | 615.4 | 615.4 | 615.4 | 615.4 | 615.4 | 615.4
Main HPT bleed temperature [F] | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
Main HPT bleed massflow [lb/s] | 0 | 0 | 0 | 0 | 0 | 0
1st HPT substream pressure [psia] | 615.4 | 615.4 | 615.4 | 615.4 | 615.4 | 615.4
1st HPT substream temperature [F] | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
1st HPT substream massflow [lb/s] | 0 | 0 | 0 | 0 | 0 | 0
2nd HPT substream pressure [psia] | 615.4 | 615.4 | 615.4 | 615.4 | 615.4 | 615.4
2nd HPT substream temperature [F] | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
2nd HPT substream massflow [lb/s] | 0 | 0 | 0 | 0 | 0 | 0
HPT addition pressure [psia] | 0 | 0 | 0 | 0 | 0 | 0
HPT addition temperature [F] | 0 | 0 | 0 | 0 | 0 | 0
HPT addition massflow [lb/s] | 0 | 0 | 0 | 0 | 0 | 0
Main LPT bleed pressure [psia] | 100 | 100 | 100 | 100 | 100 | 100
Main LPT bleed temperature [F] | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
Main LPT bleed massflow [lb/s] | 0 | 0 | 0 | 0 | 0 | 0
1st LPT substream pressure [psia] | 100 | 100 | 100 | 100 | 100 | 100
1st LPT substream temperature [F] | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
1st LPT substream massflow [lb/s] | 0 | 0 | 0 | 0 | 0 | 0
2nd LPT substream pressure [psia] | 100 | 100 | 100 | 100 | 100 | 100
2nd LPT substream temperature [F] | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
2nd LPT substream massflow [lb/s] | 0 | 0 | 0 | 0 | 0 | 0
LPT addition pressure [psia] | 0 | 0 | 0 | 0 | 0 | 0
LPT addition temperature [F] | 0 | 0 | 0 | 0 | 0 | 0
LPT addition massflow [lb/s] | 0 | 0 | 0 | 0 | 0 | 0
Financial Summary
Specialized Equipment Cost [kUSD] | 59944 | 59944 | 59944 | 59944 | 59944 | 59944
Other Equipment Cost [kUSD] | 3923 | 3923 | 3923 | 3923 | 3923 | 3923
Civil Cost [kUSD] | 3261 | 3261 | 3261 | 3261 | 3261 | 3261
Mechanical Cost [kUSD] | 6666 | 6666 | 6666 | 6666 | 6666 | 6666
Electrical Cost [kUSD] | 667 | 667 | 667 | 667 | 667 | 667
Buildings & Structures Cost [kUSD] | 2808 | 2808 | 2808 | 2808 | 2808 | 2808
Engineering & Plant Startup Cost [kUSD] | 5966 | 5966 | 5966 | 5966 | 5966 | 5966
SUBTOTAL - Contractor's Internal Cost [kUSD] | 83237 | 83237 | 83237 | 83237 | 83237 | 83237
Contractors's Soft & Miscellaneous Costs [kUSD] | 8217 | 8217 | 8217 | 8217 | 8217 | 8217
SUBTOTAL - Contractors Price [kUSD] | 91455 | 91455 | 91455 | 91455 | 91455 | 91455
Owner's Soft & Miscellaneous Costs [kUSD] | 3658 | 3658 | 3658 | 3658 | 3658 | 3658
TOTAL - Owner's Cost [kUSD] | 95113 | 95113 | 95113 | 95113 | 95113 | 95113
Contractor's Specific Cost [USD per kW] | 364 | 364 | 364 | 364 | 364 | 364
Owner's Specific Cost [USD per kW] | 378 | 378 | 378 | 378 | 378 | 378
Operating Hours per Year | 8100 | 8100 | 8100 | 8100 | 8100 | 8100
Initial Equity [kUSD] | 28534 | 28534 | 28534 | 28534 | 28534 | 28534
Cummulative Net Cash Flow [kUSD] | 622292 | 622292 | 622292 | 622292 | 622292 | 622292
Internal Rate of Return on Investment (ROI) [%] | 29.2 | 29.2 | 29.2 | 29.2 | 29.2 | 29.2
Internal Rate of Return on Equity (ROE) [%] | 68.2 | 68.2 | 68.2 | 68.2 | 68.2 | 68.2
Years for Equity Payback | 1.554 | 1.554 | 1.554 | 1.554 | 1.554 | 1.554
Net Present Value [kUSD] | 124646 | 124646 | 124646 | 124646 | 124646 | 124646
Annual Electricity Export [E6 kWh] | 2035.5 | 2035.5 | 2035.5 | 2035.5 | 2035.5 | 2035.5
Annual Heat Export [E9 BTU] | 0 | 0 | 0 | 0 | 0 | 0
Annual Fuel Import, LHV [E9 BTU] | 12728 | 12728 | 12728 | 12728 | 12728 | 12728
Break-even electricity price [USD per kWh] | 0.0284 | 0.0284 | 0.0284 | 0.0284 | 0.0284 | 0.0284
Break-even fuel LHV price [USD per E6 BTU] | 4.855 | 4.855 | 4.855 | 4.855 | 4.855 | 4.855
Cost Report
SPECIALIZED EQUIPMENT:
GT-ST-Generator Package [kUSD] | 44131 | 44131 | 44131 | 44131 | 44131 | 44131
Steam Turbine Package [kUSD]
Heat Recovery Boiler [kUSD] | 9190 | 9190 | 9190 | 9190 | 9190 | 9190
Water-cooled Condenser [kUSD] | 803.8 | 803.8 | 803.8 | 803.8 | 803.8 | 803.8
Air-cooled Condenser [kUSD]
Inlet Air Chilling / Heating System [kUSD]
Fuel Gas Compressor [kUSD] | 1088.1 | 1088.1 | 1088.1 | 1088.1 | 1088.1 | 1088.1
Continuous Emissions Monitoring System [kUSD] | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4
Distributed Control System [kUSD] | 588.5 | 588.5 | 588.5 | 588.5 | 588.5 | 588.5
Transmission Voltage Equipment [kUSD] | 1272.7 | 1272.7 | 1272.7 | 1272.7 | 1272.7 | 1272.7
Generating Voltage Equipment [kUSD] | 2651.7 | 2651.7 | 2651.7 | 2651.7 | 2651.7 | 2651.7
User-defined [kUSD] | 0 | 0 | 0 | 0 | 0 | 0
OTHER EQUIPMENT:
Pumps [kUSD] | 861.2 | 861.2 | 861.2 | 861.2 | 861.2 | 861.2
Tanks [kUSD] | 91.42 | 91.42 | 91.42 | 91.42 | 91.42 | 91.42
Cooling Tower [kUSD] | 1262.8 | 1262.8 | 1262.8 | 1262.8 | 1262.8 | 1262.8
Auxiliary Heat Exchangers [kUSD] | 41.74 | 41.74 | 41.74 | 41.74 | 41.74 | 41.74
Feedwater Heater(s) [kUSD]
Auxiliary Boiler [kUSD]
Makeup Water Treatment System [kUSD]
Waste Water Treatment System [kUSD]
Bridge Crane(s) [kUSD] | 270.3 | 270.3 | 270.3 | 270.3 | 270.3 | 270.3
Station/Instrument Air Compressors [kUSD] | 55.14 | 55.14 | 55.14 | 55.14 | 55.14 | 55.14
Recip Engine Genset(s) [kUSD]
General Plant Instrumentation [kUSD] | 152.6 | 152.6 | 152.6 | 152.6 | 152.6 | 152.6
Medium Voltage Equipment [kUSD] | 452.9 | 452.9 | 452.9 | 452.9 | 452.9 | 452.9
Low Voltage Equipment [kUSD] | 548.9 | 548.9 | 548.9 | 548.9 | 548.9 | 548.9
Miscellaneous Equipment [kUSD] | 186.8 | 186.8 | 186.8 | 186.8 | 186.8 | 186.8
User-defined [kUSD] | 0 | 0 | 0 | 0 | 0 | 0
CIVIL:
Site Work [kUSD] | 1231.5 | 1231.5 | 1231.5 | 1231.5 | 1231.5 | 1231.5
Excavation & Backfill [kUSD] | 87.7 | 87.7 | 87.7 | 87.7 | 87.7 | 87.7
Concrete [kUSD] | 1801.8 | 1801.8 | 1801.8 | 1801.8 | 1801.8 | 1801.8
Roads, Parking, Walkways [kUSD] | 140.8 | 140.8 | 140.8 | 140.8 | 140.8 | 140.8
User-defined [kUSD] | 0 | 0 | 0 | 0 | 0 | 0
MECHANICAL:
On-Site Transportation & Rigging [kUSD] | 944 | 944 | 944 | 944 | 944 | 944
Equipment Erection & Assembly [kUSD] | 2951.7 | 2951.7 | 2951.7 | 2951.7 | 2951.7 | 2951.7
Piping [kUSD] | 2323.6 | 2323.6 | 2323.6 | 2323.6 | 2323.6 | 2323.6
Steel [kUSD] | 446.9 | 446.9 | 446.9 | 446.9 | 446.9 | 446.9
User-defined [kUSD] | 0 | 0 | 0 | 0 | 0 | 0
ELECTRICAL:
Assembly & Wiring [kUSD] | 667.1 | 667.1 | 667.1 | 667.1 | 667.1 | 667.1
User-defined [kUSD] | 0 | 0 | 0 | 0 | 0 | 0
BUILDINGS:
Turbine Hall [kUSD] | 2078 | 2078 | 2078 | 2078 | 2078 | 2078
Administration, Control Room, Machine Shop / Warehouse [kUSD] | 718.8 | 718.8 | 718.8 | 718.8 | 718.8 | 718.8
Water Treatment System [kUSD]
Guard House [kUSD] | 11.73 | 11.73 | 11.73 | 11.73 | 11.73 | 11.73
User-defined [kUSD] | 0 | 0 | 0 | 0 | 0 | 0
ENGINEERING & PLANT STARTUP:
Engineering [kUSD] | 5343 | 5343 | 5343 | 5343 | 5343 | 5343
Start-Up [kUSD] | 623.2 | 623.2 | 623.2 | 623.2 | 623.2 | 623.2
User-defined [kUSD] | 0 | 0 | 0 | 0 | 0 | 0
SOFT & MISCELLANEOUS COSTS:
Contractor's Soft Costs [kUSD] | 8218 | 8218 | 8218 | 8218 | 8218 | 8218
Owner's Soft Costs [kUSD] | 3658 | 3658 | 3658 | 3658 | 3658 | 3658
Total User-defined Costs [kUSD] | 0 | 0 | 0 | 0 | 0 | 0
Major Equipment Data
Estimated Site Plot Plan
Site Length [ft] | 722.9 | 722.9 | 722.9 | 722.9 | 722.9 | 722.9
Site Width [ft] | 366.1 | 366.1 | 366.1 | 366.1 | 366.1 | 366.1
Site Area [acre] | 6.075 | 6.075 | 6.075 | 6.075 | 6.075 | 6.075
Estimated GT System Weights & Dimensions (per unit)
Number of Units | 1 | 1 | 1 | 1 | 1 | 1
Engine Weight [lb] | 302065 | 302065 | 302065 | 302065 | 302065 | 302065
Generator Weight [lb] | 685779 | 685779 | 685779 | 685779 | 685779 | 685779
Genset Foundation Length [ft] | 134.3 | 134.3 | 134.3 | 134.3 | 134.3 | 134.3
Genset Foundation Width [ft] | 18 | 18 | 18 | 18 | 18 | 18
Estimated ST System Weights & Dimensions (per unit)
Number of Units | 1 | 1 | 1 | 1 | 1 | 1
Rated Shaft Output MW
Nameplate Throttle Pressure [psia] | 2205 | 2205 | 2205 | 2205 | 2205 | 2205
Nameplate Throttle temperature [F] | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
Nameplate Throttle massflow [lb/s] | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
Steam Turbine Length [ft]
Steam Turbine Width [ft]
Steam Turbine Weight [lb]
Generator Length (Including Exciter) [ft]
Generator Width [ft]
Generator Weight [lb]
Overall ST and Generator Length [ft]
Overall ST and Generator Width [ft]
Overall ST and Generator Weight [lb]
Estimated HRSG Weights & Dimensions (per unit)
Number of Units | 1 | 1 | 1 | 1 | 1 | 1
HRSG Heat Transfer Area [ft²] | 1470025 | 1470025 | 1470025 | 1470025 | 1470025 | 1470025
Overall HRSG Length [ft] | 149.9 | 149.9 | 149.9 | 149.9 | 149.9 | 149.9
Overall HRSG Width [ft] | 28.63 | 28.63 | 28.63 | 28.63 | 28.63 | 28.63
Overall HRSG Height [ft] | 59.97 | 59.97 | 59.97 | 59.97 | 59.97 | 59.97
Overall HRSG Dry Weight [lb] | 4032785 | 4032785 | 4032785 | 4032785 | 4032785 | 4032785
Duct Burner Nameplate LHV Capacity [kBTU/hr] | 254208 | 254208 | 254208 | 254208 | 254208 | 254208
Radiant Burner Nameplate LHV Capacity [kBTU/hr] | 0 | 0 | 0 | 0 | 0 | 0
Pumps [kUSD] | 861.2 | 861.2 | 861.2 | 861.2 | 861.2 | 861.2
HP Feedwater Pump [kUSD] | 341.8 | 341.8 | 341.8 | 341.8 | 341.8 | 341.8
IP Feedwater Pump [kUSD] | 49.7 | 49.7 | 49.7 | 49.7 | 49.7 | 49.7
LP Feedwater Pump [kUSD] | 39.02 | 39.02 | 39.02 | 39.02 | 39.02 | 39.02
Condensate Forwarding Pump [kUSD] | 27.61 | 27.61 | 27.61 | 27.61 | 27.61 | 27.61
Condenser C.W. Pump [kUSD] | 208.4 | 208.4 | 208.4 | 208.4 | 208.4 | 208.4
Condenser Vacuum Pump [kUSD] | 65.31 | 65.31 | 65.31 | 65.31 | 65.31 | 65.31
Treated Water Pump [kUSD] | 2.818 | 2.818 | 2.818 | 2.818 | 2.818 | 2.818
Demin Water Pump [kUSD]
Raw Water Pump 1 [kUSD] | 2.818 | 2.818 | 2.818 | 2.818 | 2.818 | 2.818
Raw Water Pump 2 [kUSD] | 2.818 | 2.818 | 2.818 | 2.818 | 2.818 | 2.818
Raw Water Pump 3 [kUSD]
GT Water Injection Pump [kUSD]
GT Evap Cooler Water Pump [kUSD]
Auxiliary Boiler Feedwater Pump [kUSD]
Fuel Oil Unloading Pump [kUSD]
Fuel Oil Forwarding Pump [kUSD]
Auxiliary Cooling Water Pump [kUSD] | 19.78 | 19.78 | 19.78 | 19.78 | 19.78 | 19.78
Diesel Fire Pump [kUSD] | 98.22 | 98.22 | 98.22 | 98.22 | 98.22 | 98.22
Electric Fire Pump [kUSD]
Jockey Fire Pump [kUSD] | 2.848 | 2.848 | 2.848 | 2.848 | 2.848 | 2.848
GT Inlet Air Chiller Water Pump [kUSD]
GT+ST+Gen Lube Oil Coolant Pump [kUSD]
GT Generator Lube Oil Coolant Pump [kUSD]
GT Generator Coolant Pump [kUSD]
GT Chiller Coolant Pump [kUSD]
Fuel Compressor Coolant Pump [kUSD]
ST+Generator Lube Oil Coolant Pump [kUSD]
Generator Coolant Pump [kUSD]
Tanks [kUSD] | 91.42 | 91.42 | 91.42 | 91.42 | 91.42 | 91.42
Fuel Oil [kUSD]
Hydrous Ammonia [kUSD]
Demineralized Water [kUSD] | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22
Raw Water [kUSD] | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22
Neutralized Water [kUSD] | 17.05 | 17.05 | 17.05 | 17.05 | 17.05 | 17.05
Acid Storage [kUSD] | 2.965 | 2.965 | 2.965 | 2.965 | 2.965 | 2.965
Caustic Storage [kUSD] | 2.965 | 2.965 | 2.965 | 2.965 | 2.965 | 2.965
Waste Water [kUSD]
Dedicated Fire Protection Water Storage [kUSD]
Equipment Erection & Assembly [kUSD] | 2951.7 | 2951.7 | 2951.7 | 2951.7 | 2951.7 | 2951.7
Gas Turbine Package [kUSD] | 680.8 | 680.8 | 680.8 | 680.8 | 680.8 | 680.8
Steam Turbine Package [kUSD] | 357.5 | 357.5 | 357.5 | 357.5 | 357.5 | 357.5
HRSG [kUSD] | 1257.2 | 1257.2 | 1257.2 | 1257.2 | 1257.2 | 1257.2
Condenser [kUSD] | 245.2 | 245.2 | 245.2 | 245.2 | 245.2 | 245.2
Cooling Tower [kUSD]
Makeup Water Treatment System [kUSD]
Auxiliary Boiler [kUSD]
Electrical Power Equipment [kUSD] | 111.2 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2
Inlet Chilling System [kUSD]
Fuel Gas Compressor [kUSD] | 17.12 | 17.12 | 17.12 | 17.12 | 17.12 | 17.12
Pumps [kUSD] | 66.97 | 66.97 | 66.97 | 66.97 | 66.97 | 66.97
Auxiliary Heat Exchangers [kUSD] | 2.121 | 2.121 | 2.121 | 2.121 | 2.121 | 2.121
Feedwater Heater(s) [kUSD]
Station/Instrument Air Compressors [kUSD] | 5.355 | 5.355 | 5.355 | 5.355 | 5.355 | 5.355
Bridge Crane(s) [kUSD] | 17.66 | 17.66 | 17.66 | 17.66 | 17.66 | 17.66
Recip Engine Genset(s) [kUSD]
Miscellaneous [kUSD] | 190.6 | 190.6 | 190.6 | 190.6 | 190.6 | 190.6
Piping [kUSD] | 2323.6 | 2323.6 | 2323.6 | 2323.6 | 2323.6 | 2323.6
High Pressure Steam [kUSD] | 85.43 | 85.43 | 85.43 | 85.43 | 85.43 | 85.43
Cold Reheat Steam [kUSD] | 43.07 | 43.07 | 43.07 | 43.07 | 43.07 | 43.07
Hot Reheat Steam [kUSD] | 146 | 146 | 146 | 146 | 146 | 146
Intermediate Pressure Steam [kUSD]
Low Pressure Steam [kUSD] | 36.29 | 36.29 | 36.29 | 36.29 | 36.29 | 36.29
Other Steam [kUSD] | 85.68 | 85.68 | 85.68 | 85.68 | 85.68 | 85.68
Circulating Water [kUSD] | 412 | 412 | 412 | 412 | 412 | 412
Auxiliary Cooling Water [kUSD] | 256.7 | 256.7 | 256.7 | 256.7 | 256.7 | 256.7
Feedwater [kUSD] | 251.6 | 251.6 | 251.6 | 251.6 | 251.6 | 251.6
Other Water [kUSD] | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12
GT Inlet Chilling/Heating System [kUSD]
Raw Water [kUSD] | 20.51 | 20.51 | 20.51 | 20.51 | 20.51 | 20.51
Service Water [kUSD] | 55.45 | 55.45 | 55.45 | 55.45 | 55.45 | 55.45
Waste Water [kUSD]
Steam/Water Sampling [kUSD]
Sanitary Water [kUSD]
Vents [kUSD]
Fuel Gas [kUSD] | 313.3 | 313.3 | 313.3 | 313.3 | 313.3 | 313.3
Fuel Oil [kUSD]
Lube Oil [kUSD] | 105.4 | 105.4 | 105.4 | 105.4 | 105.4 | 105.4
Compressed Air [kUSD]
GT Air Bleed [kUSD]
Service Air [kUSD] | 55.68 | 55.68 | 55.68 | 55.68 | 55.68 | 55.68
Vacuum Air [kUSD] | 35.05 | 35.05 | 35.05 | 35.05 | 35.05 | 35.05
Trim [kUSD]
Chemical Feed [kUSD]
Nitrogen [kUSD]
Oxygen [kUSD]
Carbon Dioxide [kUSD]
Ammonia [kUSD]
Caustic [kUSD]
Acid [kUSD]
Boiler & Equipment Drain [kUSD] | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1
Boiler Blowdown [kUSD] | 34.47 | 34.47 | 34.47 | 34.47 | 34.47 | 34.47
Air Blowoff [kUSD]
Steam Blowoff [kUSD] | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9
Chemical Cleaning [kUSD]
Heat Tracing [kUSD]
Fire Protection [kUSD] | 79.69 | 79.69 | 79.69 | 79.69 | 79.69 | 79.69
Miscellaneous [kUSD] | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1
Assembly & Wiring [kUSD] | 667.1 | 667.1 | 667.1 | 667.1 | 667.1 | 667.1
Switchgear [kUSD] | 5.907 | 5.907 | 5.907 | 5.907 | 5.907 | 5.907
Motor Control Centers [kUSD] | 32.96 | 32.96 | 32.96 | 32.96 | 32.96 | 32.96
Feeders [kUSD] | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6
Medium/Low Voltage Cable Bus [kUSD] | 422.8 | 422.8 | 422.8 | 422.8 | 422.8 | 422.8
General Plant Instrumentation [kUSD] | 66.98 | 66.98 | 66.98 | 66.98 | 66.98 | 66.98
Miscellaneous [kUSD] | 31.77 | 31.77 | 31.77 | 31.77 | 31.77 | 31.77
Contractor's Soft Costs [kUSD] | 8218 | 8218 | 8218 | 8218 | 8218 | 8218
Contingency: [kUSD] | 2579.3 | 2579.3 | 2579.3 | 2579.3 | 2579.3 | 2579.3
Labor [kUSD] | 1049.6 | 1049.6 | 1049.6 | 1049.6 | 1049.6 | 1049.6
Specialized Equipment [kUSD] | 1198.9 | 1198.9 | 1198.9 | 1198.9 | 1198.9 | 1198.9
Other Equipment [kUSD] | 117.7 | 117.7 | 117.7 | 117.7 | 117.7 | 117.7
Commodity [kUSD] | 213.1 | 213.1 | 213.1 | 213.1 | 213.1 | 213.1
Profit: [kUSD] | 4806 | 4806 | 4806 | 4806 | 4806 | 4806
Labor [kUSD] | 1399.5 | 1399.5 | 1399.5 | 1399.5 | 1399.5 | 1399.5
Specialized Equipment [kUSD] | 2997.2 | 2997.2 | 2997.2 | 2997.2 | 2997.2 | 2997.2
Other Equipment [kUSD] | 196.2 | 196.2 | 196.2 | 196.2 | 196.2 | 196.2
Commodity [kUSD] | 213.1 | 213.1 | 213.1 | 213.1 | 213.1 | 213.1
Permits, Licenses, Fees, Miscellaneous [kUSD] | 0 | 0 | 0 | 0 | 0 | 0
Bonds and Insurance [kUSD] | 832.4 | 832.4 | 832.4 | 832.4 | 832.4 | 832.4
Spare Parts & Materials [kUSD] | 0 | 0 | 0 | 0 | 0 | 0
Contractor's Fee [kUSD] | 0 | 0 | 0 | 0 | 0 | 0
Owner's Soft Costs [kUSD] | 3658 | 3658 | 3658 | 3658 | 3658 | 3658
Permits, Licenses, Fees, Miscellaneous [kUSD] | 0 | 0 | 0 | 0 | 0 | 0
Land Cost [kUSD] | 0 | 0 | 0 | 0 | 0 | 0
Utility Connection Cost [kUSD] | 0 | 0 | 0 | 0 | 0 | 0
Legal & Financial Costs [kUSD] | 0 | 0 | 0 | 0 | 0 | 0
Interest During Construction [kUSD] | 3658 | 3658 | 3658 | 3658 | 3658 | 3658
Spare Parts & Materials [kUSD] | 0 | 0 | 0 | 0 | 0 | 0
Project Administration & Developer's Fee [kUSD] | 0 | 0 | 0 | 0 | 0 | 0