## Sheet1
Comparison of Solutions to Inverter Burnout Problem
Cost per Turbine (in Thousands of Dollars), over 20-Year Period
| Note: This table includes preliminary -- guessti- mated -- data | relia- bility | safty risk vs. other systems | crowbar -related injuries | lost genera- tion | equipme- nt repla- cement | system upgrade costs | C/B re-building (4x) | loss due to no main disc | TOTAL per turbine | notes
|  |  |  | $K | $K | $K | $K | $K | $K | $K
1 | Present Configuration | low | super high | 10 | 1.7 | 5 | 0 | 8 | 0.5 | 25.2
2 | Upgraded Present Configuration -- Now Cond. | high | same | 0.1 if 20 yrs
2 | Upgraded Present Configu- ration before C/B cont. repl. | low | very high | 2 if 20 yrs
2 | Upgraded Present Configu- ration -- 20-yr period | med | high | 0.4 | 1.1 | 0.7 | 0.2 | 8 | 0.5 | 10.9
3 | Upgraded Present Configu- ration w/Series Contactor | high | same | 0.1 | 0 | 0.1 | 2 |  | 0.5 | 2.7
4 | Proposed Configuration -- 20-year period | high | same | 0.1 | 1 | 0.1 | 7.5 | 8 |  | 16.7 | previously proposed solution
5 | Proposed Configuration w/Temp. Fuses | high | same | 0.1 | 1 | 0.1 | 5.5 | 8 |  | 14.7 | prev. proposal, but w/temp fuses
6 | Proposed Config. w/ Temp. Fuses & Series Contractor | very high | low | 0 | 0 | 0 | 7.5 |  |  | 7.5 | prev. props'l, but w/ contctr, temp fuses
7 | Contactor, Blowout Panel; No New C/B | high | same | 0.1 | 0 | 0.1 | 2.5 |  | 0.5 | 3.2
8 | Contactor, Blowout Panel; New C/B | super high | very low | 0 | 0 | 0 | 5 |  |  | 5 | earliest commiss'g recomm'd choice
9 | Remotely Mounted Crow- bar, New C/B, Contactor | super high | super low | 0 | 0 | 0 | 7.5 |  |  | 7.5 | the safetest recom- mended choice
10 | Remotely Mtd. Crowbar, Contactor, No New C/B | high + | lower | 0 | 0 | 0 | 3 |  | 0.5 | 3.5 | The least expensive recomm'd choice
11 | Cont'r, Remote Crowbar add. Cooling, No New C/B | very high | low | 0 | 0 | 0 | 3.5 |  | 0.5 | 4 | Best Buy -- good reliability & safety
12 | Cont'r, Remote Crowbar add. Cooling, New C/B | high- est | lowest | 0 | 0 | 0 | 8 |  |  | 8