## Turbine
TRANSWESTERN PIPELINE COMPANY
RED ROCK EXPANSION PROJECT
KINGMAN COMPRESSOR STATION
Table 1
TURBINE INFORMATION
Manufacturer: | GE LM2500
Fuel Type: | Sweet Natural Gas
HHV: | 1020 | Btu/scf
Site Elevation: | 5063
Inlet Loss: | 4 | in H2O
Exhaust Loss: | 4 | in H2O
Shaft Power: | 40916 | hp @ 12.8oF (Base Load)
| 33526 | hp @ 60oF (Base Load)
Max Heat Rate: | 9429 | Btu/hp-hr @95oF (50% Load)
| 385.797 | MMBtu/hr | (Max Heat Rate x shp@12.8oF)
Avg Heat Rate: | 6298 | Btu/hp-hr @60oF (Base Load)
| 211.1467 | MMBtu/hr | (Avg Heat Rate x shp@60oF)
Speed: | 6100 | rpm
Max Hourly Fuel: | 0.37823 | MMscf/hr | (Max Heat Rate/HHV)
Avg Hourly Fuel: | 0.20701 | MMscf/hr | (Avg Heat Rate/HHV)
Annual Fuel: | 1813.378 | MMscf/yr | (Avg Fuel x 8760)
Potential Emissions
Temp | Turbine | NOx (as NO2) |  | CO |  | THC
(oF) | Load (%) | (lb/hr) | (tpy) | (lb/hr) | (tpy) | (lb/hr) | (tpy)
0 | Base | 24.6 | 107.748 | 15 | 65.7 | 5.1 | 22.338
0 | 64 | 27.8 | 121.764 | 16.9 | 74.022 | 5.9 | 25.842
0 | 50 | 25.2 | 110.376 | 15.3 | 67.014 | 5.4 | 23.652
12.8 | Base | 24.9 | 109.062 | 15.2 | 66.576 | 5.1 | 22.338
12.8 | 50 | 24.7 | 108.186 | 15 | 65.7 | 5.3 | 23.214
40 | Base | 22.8 | 99.864 | 13.8 | 60.444 | 4.7 | 20.586
40 | 50 | 22.5 | 98.55 | 13.7 | 60.006 | 4.8 | 21.024
60 | Base | 21.2 | 92.856 | 12.9 | 56.502 | 4.4 | 19.272
60 | 50 | 14.5 | 63.51 | 8.8 | 38.544 | 3 | 13.14
95 | Base | 18.5 | 81.03 | 11.3 | 49.494 | 3.8 | 16.644
95 | 50 | 13.1 | 57.378 | 8 | 35.04 | 2.7 | 11.826
| Max Hourly | 27.8 | 121.764 | 16.9 | 74.022 | 5.9 | 25.842
| Base Load Max | 24.9 | 109.062 | 15.2 | 66.576 | 5.1 | 22.338
AP-42 Emission Factors (04/00)
PM | 0.0066 | lb/MMBtu
SO2 | 0.0034 | lb/MMBtu
Formaldehyde | 0.00071 | lb/MMBtu
Proposed Turbine Emissions
| Maximum | Annual
Pollutant | (lb/hr) | (tpy)
NOX | 27.8 | 111.6024 | @base load 80% of time, 64% load 20% of time
CO | 16.9 | 68.0652 | @base load 80% of time, 64% load 20% of time
VOC | 0.59 | 2.3039 | @base load 80% of time, 64% load 20% of time; assume 10% NMHC.
PM | 2.5463 | 6.1038 | @max hourly based on max heat rate, annuals based on avg heat rate
SO2 | 1.3117 | 3.1444 | @max hourly based on max heat rate, annuals based on avg heat rate
Formaldehyde | 0.27392 | 0.65662 | @max hourly based on max heat rate, annuals based on avg heat rate
Proposed Turbine Emissions with 15% Safety Factor
| Maximum | Annual
Pollutant | (lb/hr) | (tpy)
NOX | 31.97 | 128.3428
CO | 19.435 | 78.275
VOC | 0.6785 | 2.6495
PM | 2.9282 | 7.0194
SO2 | 1.5085 | 3.6161
Formaldehyde | 0.315 | 0.75512

## Gen Engines
TRANSWESTERN PIPELINE COMPANY
RED ROCK EXPANSION PROJECT
KINGMAN COMPRESSOR STATION
Table 2
GENERATOR ENGINE INFORMATION
Manufacturer: | Caterpillar 3406B
Fuel Type: | Diesel
Site Elevation: | 5063
Rated Power: | 519 | hp @100% Load
Fuel Flow Rate: | 26.4 | gal/hr
| 191.5531 | lb/hr @s.g. 0.87
Diesel Heat: | 19300 | Btu/lb
Heat Rate: | 3.697 | MMBtu/hr
| 7123.2663 | Btu/hp-hr
Speed: | 1800 | rpm
Operating Schedule: | 2000 | hours/yr
Emission Factors
Pollutant | Rate | Units | Source
NOx | 9.23 | lb/hr | Mfr
CO | 9.65 | lb/hr | Mfr
THC | 0.12 | lb/hr | Mfr
PM | 2.82 | lb/hr | Mfr
SO2 | 0.29 | lb/MMBtu | AP-42
Proposed Generator Engine Emissions
| Maximum | Annual
Pollutant | (lb/hr) | (tpy)
NOX | 9.23 | 9.23
CO | 9.65 | 9.65
VOC | 0.12 | 0.12
PM | 2.82 | 2.82
SO2 | 1.0721 | 1.0721

## Netting
TRANSWESTERN PIPELINE COMPANY
RED ROCK EXPANSION PROJECT
KINGMAN COMPRESSOR STATION
Table 3
NETTING CALCULATIONS
Existing Compressor Engines
|  |  |  | Heat Rate | Max Input
Unit | Model | hp Rating | Type | Btu/hp-hr | MMBtu/hr
101 | Ingersoll Rand 616KVT | 4000 | 4 Cycle Rich Burns | 8500 | 34
102 | Ingersoll Rand 616KVT | 4000 | 4 Cycle Rich Burns | 8500 | 34
103 | Ingersoll Rand 616KVT | 4000 | 4 Cycle Rich Burns | 8500 | 34
121 | Waukesha | 451 | 4 Cycle Rich Burns | 8500 | 3.8335
122 | Waukesha | 451 | 4 Cycle Rich Burns | 8500 | 3.38
AP-42 Emissions Factors (07/00) for 4-Cycle Rich <90% Load
Nox | 2.27 | lb/MMBtu
CO | 3.51 | lb/MMBtu
VOC | 0.0296 | lb/MMBtu
PM | 0.0194 | lb/MMBtu
SO2 | 0.000588 | lb/MMBtu
Historical Operating Hours
| Year | 101 | 102 | 103 | 121 | 122
| 2000 | 8549 | 7212 | 6540 | 1600 | 0
| 1999 | 2426 | 2242 | 2723 | 0 | 0
| 1998 | 6702 | 6252 | 6449
| 1997 | 122 | 263 | 191
| 1996 | 325 | 331 | 242
| 1995 | 94 | 89 | 42
| 1994 | 1068 | 253 | 1119
| 1993 | 1413 | 1801 | 1671
| 1992 | 3737 | 3292 | 2945
| 1991 | 7545 | 7147 | 7437
2000-1999 Average |  | 5487.5 | 4727 | 4631.5 | 800 | 0
Last 2-Year Emissions Average (from this worksheet)
Unit | Nox (tpy) | CO (tpy) | VOC (tpy) | PM | SO2
101 | 211.7626 | 327.4391 | 2.7613 | 1.559 | 0.046296
102 | 182.4149 | 282.0601 | 2.3786 | 1.5275 | 0.046296
103 | 178.7296 | 276.3616 | 2.3306 | 1.5275 | 0.046296
121 | 3.4808 | 5.3822 | 0.045389 | 0.029748 | 0.00090164
122 | 0 | 0 | 0 | 0 | 0
Total | 576.388 | 891.2431 | 7.5159 | 4.6436 | 0.13979
Contemporaneous Emission Increases (tpy) (from this worksheet)
Turbine | 128.3428 | 78.275 | 2.6495 | 7.0194 | 3.6161
Gen Eng 1 | 9.23 | 9.65 | 0.12 | 2.82 | 1.0721
TOTAL | 137.5728 | 87.925 | 2.7695 | 9.8394 | 4.6882
Contemporaneous Emission Decreases (tpy) (from this worksheet)
| 576.388 | 891.2431 | 7.5159 | 4.6436 | 0.13979
Net Change (Increase - Decrease) (tpy) (from this worksheet)
| -438.8152 | -803.3181 | -4.7464 | 5.1958 | 4.5484
Assumptions
1. Turbine PM and SO2 emission factors from AP-42 (04/00).
2. Proposed NOx, CO, and VOC emissions based on 80/20 split. Turbine will operate at 100% load 80% of the time
and 64% load 20% of the time.
3. Contemporaneous increases are from proposed turbine and generator engine.
4. Contemporaneous decreases are from permanent shutdown of Units 101, 102, 103, 121 and 122.

## Netting 2
TRANSWESTERN PIPELINE COMPANY
RED ROCK EXPANSION PROJECT
KINGMAN COMPRESSOR STATION
1999 Emissions Reported to ADEQ (from EI)
Unit | Nox (tpy) | CO (tpy) | VOC (tpy)
101 | 106.98 | 92 | 1.5
102 | 98.83 | 85 | 1.38
103 | 120.08 | 103.27 | 1.68
121 | 0 | 0 | 0
122 | 0 | 0 | 0
Total | 325.89 | 280.27 | 4.56
2000 Emissions Reported to ADEQ (from EI)
Unit | Nox (tpy) | CO (tpy) | VOC (tpy)
101 | 280.87 | 472.77 | 3.76
102 | 236.95 | 398.84 | 3.17
103 | 214.98 | 361.87 | 2.88
121 | 5.26 | 8.85 | 0.07
122 | 0 | 0 | 0
Total | 738.06 | 1242.33 | 9.88
Last 2-Year Emissions Average (from EIs)
Unit | Nox (tpy) | CO (tpy) | VOC (tpy)
101 | 193.925 | 282.385 | 2.63
102 | 167.89 | 241.92 | 2.275
103 | 167.53 | 232.57 | 2.28
121 | 2.63 | 4.425 | 0.035
122 | 0 | 0 | 0
Total | 531.975 | 761.3 | 7.22
Proposed Emission Increases (tpy)
Turbine | 128.34 | 78.27 | 2.65
Gen Engines | 9.23 | 9.65 | 0.12
TOTAL | 137.57 | 87.92 | 2.77
Contemporaneous Emission Decreases (tpy)
| 531.975 | 761.3 | 7.22
Net Change (Increase - Decrease) (tpy)
| -394.405 | -673.38 | -4.45
Notes:
(1) Proposed NOx, CO, and VOC emissions based on 80/20 split. Turbine will operate at 100% load 80% of the time
and 64% load 20% of the time.
(2) Proposed increases are from proposed turbine and generator engines.
Only one generator engine will be run at a time.
(3) Contemporaneous decreases are from permanent shutdown of Units 101, 102, 103, 121, and 122.

## Alternative
TRANSWESTERN PIPELINE COMPANY
RED ROCK EXPANSION PROJECT
KINGMAN COMPRESSOR STATION
Table 4
ALTERNATIVE OPERATING SCENARIO EMISSIONS
Engine Data
Operating Hours: |  | 4380 | hours
Comp Rated hp: |  | 4000 | hp
Gen Rate hp: |  | 451
Heat Rate: |  | 7500 | Btu/hp-hr
AP-42 Emissions Factors (07/00) for 4-Cycle Rich <90% Load
Nox | 2.27 | lb/MMBtu
CO | 3.51 | lb/MMBtu
VOC | 0.0296 | lb/MMBtu
PM | 0.0194 | lb/MMBtu
SO2 | 0.000588 | lb/MMBtu
Proposed Emissions (tpy)
Unit | NOx | CO | VOC | PM | SO2
101 | 149.139 | 230.607 | 1.9447 | 1.2746 | 0.038632
102 | 149.139 | 230.607 | 1.9447 | 1.2746 | 0.038632
103 | 149.139 | 230.607 | 1.9447 | 1.2746 | 0.038632
121 | 0 | 0 | 0 | 0 | 0
122 | 0 | 0 | 0 | 0 | 0
TOTAL | 447.417 | 691.821 | 5.8342 | 3.8237 | 0.11589

## Summary
TRANSWESTERN PIPELINE COMPANY
RED ROCK EXPANSION PROJECT
KINGMAN COMPRESSOR STATION
Table 5
SUMMARY OF STATION EMISSIONS
PRIMARY OPERATING SCENARIO
|  |  | NOx |  | CO |  | VOC |  | PM |  | SO2
Unit | Source Name | Source ID | lb/hr | tpy | lb/hr | tpy | lb/hr | tpy | lb/hr | tpy | lb/hr | tpy
101 | Compressor Engine 1 | P1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | Compressor Engine 2 | P2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | Compressor Engine 3 | P3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | Generator Engine 1 | P4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122 | Generator Engine 2 | P5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | Compressor Turbine | P7 | 31.97 | 128.3428 | 19.435 | 78.275 | 0.6785 | 2.6495 | 2.9282 | 7.0194 | 1.5085 | 3.6161
123 | Diesel Generator Engine | P8 | 9.23 | 9.23 | 9.65 | 9.65 | 0.12 | 0.12 | 2.82 | 2.82 | 1.0721 | 1.0721
|  | TOTAL | 41.2 | 137.5728 | 29.085 | 87.925 | 0.7985 | 2.7695 | 5.7482 | 9.8394 | 2.5806 | 4.6882
ALTERNATIVE OPERATING SCENARIO
|  |  | NOx |  | CO |  | VOC |  | PM |  | SO2
Unit | Source Name | Source ID | lb/hr | tpy | lb/hr | tpy | lb/hr | tpy | lb/hr | tpy | lb/hr | tpy
101 | Compressor Engine 1 | P1 |  | 149.139 |  | 230.607 |  | 1.9447 |  | 1.2746 |  | 0.038632
102 | Compressor Engine 2 | P2 |  | 149.139 |  | 230.607 |  | 1.9447 |  | 1.2746 |  | 0.038632
103 | Compressor Engine 3 | P3 |  | 149.139 |  | 230.607 |  | 1.9447 |  | 1.2746 |  | 0.038632
121 | Generator Engine 1 | P4 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
122 | Generator Engine 2 | P5 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
104 | Compressor Turbine | P7 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
123 | Diesel Generator Engine | P8 |  | 9.23 |  | 9.65 |  | 0.12 |  | 2.82 |  | 1.0721
|  | TOTAL | 0 | 456.647 | 0 | 701.471 | 0 | 5.9542 | 0 | 6.6437 | 0 | 1.188

## Example
TRANSWESTERN PIPELINE COMPANY
RED ROCK EXPANSION PROJECT
KINGMAN COMPRESSOR STATION
Table 6
EXAMPLE EMISSION CALCULATIONS
GE LM2500 TURBINE
NOx Emissions
Maximum Hourly (lb/hr)
31.97 | lb/hr = | maximum hourly emission rate at 64% load at 00F x 1.15
Annual (ton per year)
128.3428 | tpy = | (80% x annual avg emission rate) + (20% x annual emission rate based on maximum hourly) x 1.15
((0.8 x 109.06) + (0.2 x 121.76)) x 1.15
CO Emissions
Maximum Hourly (lb/hr)
19.435 | lb/hr = | maximum hourly emission rate at 64% load at 00F x 1.15
Annual (ton per year)
78.275 | tpy = | (80% x annual avg emission rate) + (20% x annual emission rate based on maximum hourly) x 1.15
((0.8 x 66.58) + (0.2 x 74.02)) x 1.15
VOC Emissions
Maximum Hourly (lb/hr)
0.6785 | lb/hr = | maximum hourly emission rate at 64% load at 0oF x 10% NMHC x 1.15
Annual (ton per year)
2.6495 | tpy = | ((80% x annual avg emission rate) + (20% x annual emission rate based on maximum hourly)) x 10% NMHC x 1.15
((0.8 x 22.34) + (0.2 x 25.84)) x 0.1 x 1.15
Particulate Emissions
Maximum Hourly (lb/hr)
2.9282 | lb/hr = | maximum heat rate at 50% load at 95oF x AP42 factor lb/MMBtu x 1.15
385.80 MMBtu/hr x 6.6E-3 lb/MMBtu x 1.15
Annual (ton per year)
7.0194 | tpy = | avg heat rate at base load at 60oF x AP42 factor lb/MMBtu x 8760 hrs/yr x 1 ton/2000 lbs x 1.15
211.15 MMBtu/hr x 6.6E-3 lb/MMBtu x 8760 / 2000 x 1.15
SO2 Emissions
Maximum Hourly (lb/hr)
1.5085 | lb/hr = | maximum heat rate at 50% load at 95oF x AP42 factor lb/MMBtu x 1.15
385.80 MMBtu/hr x 3.4E-3 lb/MMBtu x 1.15
Annual (ton per year)
3.6161 | tpy = | avg heat rate at base load at 60oF x AP42 factor lb/MMBtu x 8760 hrs/yr x 1 ton/2000 lbs x 1.15
211.15 MMBtu/hr x 3.4E-3 lb/MMBtu x 8760 / 2000 x 1.15
Formaldehyde Emissions
Maximum Hourly (lb/hr)
0.315 | lb/hr = | maximum heat rate at 50% load at 95oF x AP42 factor lb/MMBtu x 1.15
385.80 MMBtu/hr x 7.1E-4 lb/MMBtu
Annual (ton per year)
0.75512 | tpy = | avg heat rate at base load at 60oF x AP42 factor lb/MMBtu x 8760 hrs/yr x 1 ton/2000 lbs x 1.15
211.15 MMBtu/hr x 7.1E-4 lb/MMBtu x 8760 / 2000 x 1.15