## Hinkley District, 2000
LINE | Mile Point | Description | Sample Date | Sample Type | Result (All results as Aroclor 1016 unless otherwise noted) | Comments
300 A | 116.48 A | Pisgah |  | None |  | Tap not inspected or sampled
300 A | 130.37 A | PLS 2XA Insertion Meter | 2000-02-16 | Wipe | ND <0.7 ug/100cm2
300 A | 131.94 A | Newberry Springs Community Tap | 2000-02-09 | Wipe | ND <1ug/wipe | Removed primary regulator; opened it and obtained wipe sample - non quantitative
300 A | 134.00 A | Southwest Gas (Martino) |  | None |  | Tap not inspected or sampled
300 A | 135.98 A | Southwest Gas (Masimini) |  | None |  | Tap not inspected or sampled
300 A | 137.00 A | Southwest Gas |  | None |  | Tap not inspected or sampled
300 A | 137.50 A | Southwest Gas |  | None |  | Tap not inspected or sampled
300 A | 141.03 A | Lucerne Valley - Main #313 XA | 2000-02-11 | None |  | Sample taps located immediately upstream and downstream of orifice plate. Both taps were dry.
300 A | 147.91 A | Barstow B Meter | 2000-02-11 | Liquid | 11 ppm
300 A | 147.91 A | Barstow B Meter | 2000-02-28 | Liquid |  | Insufficient Sample
300 A | 147.91 A | Barstow B Meter | 2000-03-10 | Liquid | 16 ppm
300 A | 147.91 A | Barstow B Meter | 2000-03-21 | Liquid | 13 ppm
300 A | 147.91 A | Barstow B Meter | 2000-04-05 | Liquid | 18 ppm
300 A | 147.91 A | Barstow B Meter | 2000-04-19 | Liquid | 10 ppm
300 A | 147.91 A | Barstow B Meter | 2000-05-01 | Liquid | 11 ppm
300 A | 147.91 A | Barstow B Meter | 2000-05-14 | Liquid | 18 ppm
300 A | 147.91 A | Barstow B Meter | 2000-05-30 | Liquid | 11 ppm
300 A | 147.91 A | Barstow B Meter | 2000-06-14 | Liquid | 24 ppm
300 A | 147.91 A | Barstow B Meter | 2000-06-30 | Liquid | 25 ppm
300 A | 147.91 A | Barstow B Meter | 2000-07-29 | Liquid | 8 ppm
300 A | 147.91 A | Barstow B Meter | 2000-08-18 | Liquid | 10 ppm
300 A | 147.91 A | Barstow B Meter | 2000-09-05 | Liquid | 14 ppm | <10 mls
300 A | 147.91 A | Barstow B Meter | 2000-09-19 | Liquid | 15 ppm | <10 mls (trace)
300 A | 151.05 A | Barstow "A" Filter | 2000-02-17 | Liquid | 6 ppm
300 A | 151.05 A | Barstow "A" Filter | 2000-02-28 | Liquid | 13 ppm
300 A | 151.06 A | Barstow "A" Filter | 2000-03-10 | Liquid | 15 ppm
300 A | 151.06 A | Barstow "A" Filter | 2000-03-21 | Liquid | 15 ppm
300 A | 151.06 A | Barstow "A" Filter | 2000-04-05 | Liquid | 22 ppm
300 A | 151.06 A | Barstow "A" Filter | 2000-04-18 | Liquid | 11 ppm
300 A | 151.06 A | Barstow "A" Filter | 2000-05-01 | Liquid | 7 ppm
300 A | 151.06 A | Barstow "A" Filter | 2000-05-14 | Liquid | 26 ppm
300 A | 151.06 A | Barstow "A" Filter | 2000-05-30 | Liquid | 10 ppm
300 A | 151.06 A | Barstow "A" Filter | 2000-06-14 | Liquid | 18 ppm
300 A | 151.06 A | Barstow "A" Meter | 2000-02-17 | Liquid | 9 ppm
300 A | 151.06 A | Barstow "A" Meter | 2000-02-28 | Liquid | 20 ppm
300 A | 151.06 A | Barstow "A" Meter | 2000-03-10 | Liquid | 16 ppm
300 A | 151.06 A | Barstow "A" Meter | 2000-03-21 | Liquid | 15 ppm
300 A | 151.06 A | Barstow "A" Meter | 2000-04-05 | Liquid | 18 ppm
300 A | 151.06 A | Barstow "A" Meter | 2000-04-18 | Liquid | 8 ppm
300 A | 151.06 A | Barstow "A" Meter | 2000-05-01 | Liquid | 17 ppm
300 A | 151.06 A | Barstow "A" Meter | 2000-05-14 | Liquid | 33 ppm
300 A | 151.06 A | Barstow "A" Meter | 2000-05-30 | Liquid | 5 ppm
300 A | 151.06 A | Barstow "A" Meter | 2000-06-14 | Liquid | 17 ppm
300 A | 151.06 A | Barstow "A" Meter | 2000-06-30 | Liquid | 15 ppm
300 A | 151.06 A | Barstow "A" Meter | 2000-07-29 | Liquid | 16 ppm
300 A | 151.06 A | Barstow "A" Meter | 2000-08-10 | Liquid | 1 ppm
300 A | 151.06 A | Barstow "A" Meter | 2000-08-16 | Liquid | 2 ppm
300 A | 151.06 A | Barstow "A" Meter | 2000-08-18 | Liquid | 9 ppm
300 A | 151.06 A | Barstow "A" Meter | 2000-08-24 | Liquid | 3 ppm
300 A | 151.06 A | Barstow "A" Meter | 2000-08-30 | Liquid | 4 ppm
300 A | 151.06 A | Barstow "A" Meter | 2000-09-05 | Liquid | 15 ppm | < 10 mls
300 A | 151.06 A | Barstow "A" Meter | 2000-09-07 | Liquid | 2 ppm
300 A | 151.06 A | Barstow "A" Meter | 2000-09-19 | Liquid | 14 ppm | ~ 20 mls
300 A | 151.06 A | Barstow "A" Meter | 2000-10-02 | Liquid | 13 ppm | ~ 20 mls
300 A | 154.70 A | Barstow "D" Meter | 2000-02-18 | Liquid | 38 ppm
300 A | 154.70 A | Barstow "D" Meter | 2000-02-28 | Liquid | 39 ppm
300 A | 154.70 A | Barstow "D" Meter | 2000-03-10 | Liquid | 34 ppm
300 A | 154.70 A | Barstow "D" Meter | 2000-03-21 | Liquid | 45 ppm
300 A | 154.70 A | Barstow "D" Meter | 2000-04-05 | Liquid | 29 ppm
300 A | 154.70 A | Barstow "D" Meter | 2000-04-18 | Liquid | 27 ppm
300 A | 154.70 A | Barstow "D" Meter | 2000-05-01 | Liquid | 28 ppm
300 A | 154.70 A | Barstow "D" Meter | 2000-05-14 | Liquid | 33 ppm
300 A | 154.70 A | Barstow "D" Meter | 2000-05-25 | Liquid | 19 ppm
300 A | 154.70 A | Barstow "D" Meter | 2000-06-14 | Liquid | 33 ppm
300 A | 154.70 A | Barstow "D" Meter | 2000-06-30 | Liquid | 22 ppm
300 A | 154.70 A | Barstow "D" Meter | 2000-07-29 | None
300 A | 154.70 A | Barstow "D" Meter | 2000-09-19 | None | 30 ppm | 20 mls
300 A | 154.70 A | Barstow "D" Meter | 2000-10-02 | None | 31 ppm | 20 mls
300 A | 154.70 A | Barstow "D" East Filter | 2000-02-11 | Liquid | ND < 1 ppm
300 A | 154.70 A | Barstow "D" East Filter | 2000-02-28 | Liquid |  | Insufficient Sample
300 A | 154.70 A | Barstow "D" East Filter | 2000-03-21 | Liquid | 0.45
300 A | 154.70 A | Barstow "D" East Filter | 2000-04-05 | Liquid | < 1 ppm
300 A | 154.70 A | Barstow "D" East Filter | 2000-07-29 | None
300 A | 154.70 A | Barstow "D" East Filter | 2000-08-10 | Liquid | 3 ppm
300 A | 154.70 A | Barstow "D" East Filter | 2000-08-16 | Liquid | 2 ppm
300 A | 154.70 A | Barstow "D" East Filter | 2000-08-24 | Liquid | 3 ppm
300 A | 154.70 A | Barstow "D" East Filter | 2000-08-30 | Liquid | 2 ppm
300 A | 154.70 A | Barstow "D" East Filter | 2000-09-07 | Liquid | 2 ppm
300 A | 159.33 A | Emergency Fuel |  | None |  | Tap not inspected or sampled
300 A | 159.33 A | Hinkley, K-11 Crankcase | 2000-05-01 | Liquid | ND < 1 ppm
300 A | 159.33 A | Hinkley, K-11 Compressor | 2000-05-01 | Liquid | 6 ppm
300 A | 159.33 A | Hinkley Compressor Station 300A Suction Drip, Inlet 211 | 2000-01-27 | Liquid | 4 ppm
300 A | 159.33 A | Hinkley Compressor Station 300A Suction Drip, Inlet 211 | 2000-02-10 | Liquid | 3 ppm | Black; liquid obtained. Drip was emptied after sample was obtained Sample tap was plugged and was replaced with metric valve.
300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-02-25 | Liquid | 7 ppm
300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-03-09 | Liquid | 8 ppm
300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-04-06 | Liquid | 7 ppm
300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-05-01 | Liquid | 10 ppm
300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-05-14 | Liquid | 15 ppm
300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-05-14 | Liquid | 15 ppm
300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-05-30 | Liquid | 6 ppm
300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-06-30 | Liquid | 9 ppm
300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-07-29 | Liquid | 9 ppm
300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-09-18 | Liquid | 14 ppm | ~ 40 mls
300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-10-02 | Liquid | 21 ppm | ~ 40 mls
300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2000-05-01 | Liquid | 7 ppm
300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2000-08-10 | Liquid | 2 ppm
300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2000-08-16 | Liquid | 3 ppm
300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2000-08-24 | Liquid | 2 ppm
300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2000-08-30 | Liquid | 3 ppm
300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2000-09-07 | Liquid | 2 ppm
300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2000-10-02 | Liquid | 13 ppm | ~30 mls
300 A | 160.00 A | Southwest Gas 3 Customers (Neirmeirer - McCormack) |  | None |  | Tap not inspected or sampled
300 A | 161.93 A | A Line Drip | 2000-02-10 | Liquid | <1 ppm
300 A | 161.93 A | A Line Drip | 2000-02-24 | Liquid | 2 ppm
300 A | 161.93 A | A Line Drip | 2000-03-09 | Liquid | ND < 1 ppm
300 A | 161.93 A | A Line Drip | 2000-03-23 | Liquid | ND < 1 ppm
300 A | 161.93 A | A Line Drip | 2000-04-06 | Liquid | <1 ppm
300 A | 161.93 A | A Line Drip | 2000-04-19 | Liquid | <1 ppm
300 A | 161.93 A | A Line Drip | 2000-05-01 | Liquid | <1 ppm
300 A | 161.93 A | A Line Drip | 2000-05-14 | Liquid | <1 ppm
300 A | 161.93 A | A Line Drip | 2000-06-01 | Liquid | <1 ppm
300 A | 161.93 A | A Line Drip | 2000-06-14 | Liquid | 1 ppm
300 A | 161.93 A | A Line Drip | 2000-06-29 | None
300 A | 161.93 A | A Line Drip | 2000-06-30 | Liquid | <1 ppm
300 A | 161.93 A | A Line Drip | 2000-07-23 | None
300 A | 161.93 A | A Line Drip | 2000-07-29 | Liquid | 1.7 ppm as Aroclor 1016, 0.5 ppm as Aroclor 1260
300 A | 161.93 A | A Line Drip | 2000-09-06 | Liquid | 1 ppm | ~40 mls
300 A | 161.93 A | A Line Drip | 2000-09-18 | Liquid | 2 ppm | ~20 mls
300 A | 161.93 A | A Line Drip | 2000-10-03 | Liquid | 2 ppm | ~10 mls
300 A | 164.71 A | A Line Drip | 2000-02-10 | Liquid | <1
300 A | 164.71 A | A Line Drip | 2000-02-24 | Liquid | 5 ppm
300 A | 164.71 A | A Line Drip | 2000-03-09 | Liquid | <1 ppm
300 A | 164.71 A | A Line Drip | 2000-03-28 | Liquid | <1 ppm
300 A | 164.71 A | A Line Drip | 2000-04-06 | Liquid | <1 ppm
300 A | 164.71 A | A Line Drip | 2000-04-19 | Liquid | < 1 ppm
300 A | 164.71 A | A Line Drip | 2000-05-14 | Liquid | < 1 ppm
300 A | 164.71 A | A Line Drip | 2000-06-01 | Liquid | < 1 ppm
300 A | 164.71 A | A Line Drip | 2000-06-15 | Liquid | 1 ppm
300 A | 164.71 A | A Line Drip | 2000-06-30 | Liquid | 1 ppm
300 A | 164.71 A | A Line Drip | 2000-07-23 | None
300 A | 164.71 A | A Line Drip | 2000-07-29 | Liquid | 1 ppm
300 A | 164.71 A | A Line Drip | 2000-08-21 | Liquid | 1 ppm
300 A | 164.71 A | A Line Drip | 2000-09-06 | Liquid | 1 ppm | ~ 20 mls
300 A | 164.71 A | A Line Drip | 2000-09-18 | Liquid | 1 ppm | ~ 40 mls
300 A | 164.71 A | A Line Drip | 2000-10-03 | Liquid | 1 ppm | ~ 50 mls
300 A | 167.37 A | A Line Drip | 2000-02-10 | Liquid | <1 ppm
300 A | 167.37 A | A Line Drip | 2000-02-24 | Liquid | 6 ppm
300 A | 167.37 A | A Line Drip | 2000-03-09 | Liquid | <1 ppm
300 A | 167.37 A | A Line Drip | 2000-03-23 | Liquid | ND < 1 ppm
300 A | 167.37 A | A Line Drip | 2000-04-06 | Liquid | < 1 ppm
300 A | 167.37 A | A Line Drip | 2000-04-19 | Liquid | 1 ppm
300 A | 167.37 A | A Line Drip | 2000-05-01 | Liquid | < 1 ppm
300 A | 167.37 A | A Line Drip | 2000-05-14 | Liquid | < 1 ppm
300 A | 167.37 A | A Line Drip | 2000-06-01 | Liquid | < 1 ppm
300 A | 167.37 A | A Line Drip | 2000-06-16 | Liquid | < 1 ppm
300 A | 167.37 A | A Line Drip | 2000-06-30 | Liquid | 1 ppm
300 A | 167.37 A | A Line Drip | 2000-07-29 | Liquid | 1 ppm
300 A | 167.37 A | A Line Drip | 2000-08-21 | Liquid | 1 ppm
300 A | 167.37 A | A Line Drip | 2000-09-06 | Liquid | 1 ppm | ~20 mls
300 A | 167.37 A | A Line Drip | 2000-09-18 | Liquid | 1 ppm | ~20 mls
300 A | 167.37 A | A Line Drip | 2000-10-03 | Liquid | 3 ppm | ~50 mls
300 A | 170.61 A | A Line Drip | 2000-04-06 | Liquid | ND < 1ppm
300 A | 170.61 A | A Line Drip | 2000-04-19 | Liquid | ND < 1ppm
300 A | 170.61 A | A Line Drip | 2000-05-14 | Liquid | ND < 1ppm
300 A | 170.61 A | A Line Drip | 2000-06-01 | Liquid | ND < 1ppm
300 A | 170.61 A | A Line Drip | 2000-06-15 | Liquid | ND < 1ppm
300 A | 170.61 A | A Line Drip | 2000-06-30 | Liquid | ND < 1ppm
300 A | 170.61 A | A Line Drip | 2000-07-23 | None
300 A | 170.61 A | A Line Drip | 2000-08-21 | Liquid | 1 ppm
300 A | 170.61 A | A Line Drip | 2000-09-06 | Liquid | <1 ppm | ~10 mls
300 A | 170.61 A | A Line Drip | 2000-09-19 | Liquid | <1 ppm | <10 mls (trace)
300 A | 170.61 A | A Line Drip | 2000-10-03 | Liquid | <1 ppm | <10 mls (trace)
300 A | 170.62 A | Line 300 A Drip at Victorville Tap | 2000-02-10 | None |  | No liquids in drip
300 A | 175.49 A | Line 300 A Drip | 2000-02-10 | Liquid | ND < 1 ppm
300 A | 175.49 A | Line 300 A Drip | 2000-02-24 | Liquid | 7 ppm
300 A | 175.49 A | Line 300 A Drip | 2000-03-09 | Liquid | 1 ppm
300 A | 175.49 A | Line 300 A Drip | 2000-04-06 | Liquid | < 1 ppm
300 A | 175.49 A | Line 300 A Drip | 2000-04-19 | Liquid | 1 ppm
300 A | 175.49 A | Line 300 A Drip | 2000-05-14 | Liquid | < 1 ppm
300 A | 175.49 A | Line 300 A Drip | 2000-06-01 | Liquid | < 1 ppm
300 A | 175.49 A | Line 300 A Drip | 2000-06-15 | Liquid | 1 ppm
300 A | 175.49 A | Line 300 A Drip | 2000-06-29 | None | 1 ppm
300 A | 175.49 A | Line 300 A Drip | 2000-06-30 | Liquid | 1 ppm
300 A | 175.49 A | Line 300 A Drip | 2000-07-23 | Liquid | 1 ppm
300 A | 175.49 A | Line 300 A Drip | 2000-07-29 | Liquid | 1 ppm
300 A | 175.49 A | Line 300 A Drip | 2000-08-10 | Liquid | 2 ppm
300 A | 175.49 A | Line 300 A Drip | 2000-08-16 | Liquid | 2 ppm
300 A | 175.49 A | Line 300 A Drip | 2000-08-21 | Liquid | 1 ppm
300 A | 175.49 A | Line 300 A Drip | 2000-08-24 | Liquid | 2 ppm
300 A | 175.49 A | Line 300 A Drip | 2000-08-30 | Liquid | 2 ppm
300 A | 175.49 A | Line 300 A Drip | 2000-09-06 | Liquid | 2 ppm | ~20 mls
300 A | 175.49 A | Line 300 A Drip | 2000-09-07 | Liquid | 2 ppm
300 A | 175.49 A | Line 300 A Drip | 2000-09-19 | Liquid | 3 ppm | ~20 mls
300 A | 175.49 A | Line 300 A Drip | 2000-10-03 | Liquid | 3 ppm | ~50 mls
300 A | 180.64 A | Trona - Main # 311 X | 2000-02-10 | None |  | No liquids in filter (east filter tap)
300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-02-10 | Liquid | 4 ppm | Second Stage sample point - good liquid sample obtained
300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-02-24 | Liquid | 5 ppm | Second stage Regulator
300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-03-08 | Liquid | 7 ppm
300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-03-21 | Liquid | 26 ppm
300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-04-05 | Liquid | 11 ppm | Regulator Pit
300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-04-18 | Liquid | 6 ppm
300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-05-03 | Liquid | 12 ppm
300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-05-15 | Liquid | 14 ppm
300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-05-30 | Liquid | 26 ppm
300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-07-25 | None
300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-08-10 | Liquid | 8 ppm
300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-08-21 | None
300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-08-24 | Liquid | 4 ppm
300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-09-06 | Liquid | 9 ppm | <10 mls
300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-09-19 | None |  | Dry
300 A | 188.06 A | Boron Town Site |  | None |  | Tap not inspected or sampled
300 A | 188.06 A | Boron Town Site | 2000-06-01 | Liquid | 1 ppm
300 A | 191.09 A | US Borax and Chem. Co., Hal B Hayes |  | None |  | Tap not inspected or sampled
300 A | 197.63 A | North Edwards - Red Barn | 2000-02-10 | None |  | Didn't sample
300 A | 200.97 A | Clay Mine Road (Muroc Motel) | 2000-02-10 | None |  | Didn't sample
300 A | 203.01 A | PLS 3A Insertion Meter | 2000-02-16 | Wipe | ND <0.7 ug/100cm2
300 A | 203.02 A | Edwards AFB, from PLS #3, elbow | 2000-02-10 | Wipe | 1.3 ug/wipe | East Run - Two Wipe samples taken (semi-quantitative)
300 A | 203.02 A | Edwards AFB, from PLS #3, elbow | 2000-08-10 | Wipe | 3 ppm
300 A | 203.02 A | Edwards AFB, from PLS #3, valve | 2000-02-10 | Wipe | < 1ug/wipe | East Run - Two Wipe samples taken (semi-quantitative)
300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-03-22 | Wipe | 2 ug /wipe as Aroclor 1016, 1 ug/wipe as Aroclor 1254
300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-04-04 | Wipe | 0.8 ug /wipe as Aroclor 1016, 0.8 ug/wipe as Aroclor 1254
300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-05-15 | Liquid | 1 ppm
300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-06-01 | Liquid | 8 ppm
300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-06-13 | Liquid | 3 ppm
300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-07-24 | Liquid | 2.6 ppm as Aroclor 1016, 0.6 ppm as Aroclor 1260 | < 10 mls
300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-08-07 | Liquid
300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-08-22 | Liquid | 2 ppm as Aroclor 1016, 1 ppm as Aroclor 1254 | < 10 mls liquid
300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-09-06 | Liquid | 2 ppm as Aroclor 1016, 2 ppm as Aroclor 1254 | < 10 mls
300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-09-19 | Liquid | 2 ppm | < 10 mls
300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-10-03 | Liquid | 19 ppm
300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-03-22 | Liquid | < 1 ppm
300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-04-04 | Liquid | < 1 ppm
300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-04-19 | Liquid | ND < 1 ppm
300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-05-04 | Liquid | ND < 1 ppm
300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-05-15 | Liquid |  | Insufficient Sample
300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-06-01 | Liquid |  | Insufficient Sample
300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-06-13 | Liquid | ND < 1 ppm
300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-06-27 | Liquid |  | Insufficient Sample
300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-07-24 | None
300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-08-21 | None
300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-09-06 | Liquid |  | Insuffient sample, <10 mls
300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-09-19 | None |  | no liquid
300 A | 210.47 A | All American Pipeline Filter | 2000-02-29 | Liquid | < 1 ppm | Sample from filter (Site shut-in as of 4/00)
300 A | 210.47 A | All American Pipeline Filter | 2000-02-29 | Liquid | 1 ppm | Additional sample obtained from filter (Site shut-in as of 4/00)
300 A | 218.73 A | Mojave Meter and Reg Station, So. Cal Gas |  | None |  | Tap not inspected or sampled
300 A | 225.57 A | California Portland Cement | 2000-02-24 | Liquid | ND < 1ppm | Sample from Old Orifice meter (Left)
300 A | 225.57 A | California Portland Cement | 2000-05-15 | Liquid | 1 ppm | Tap meter
300 A | 225.57 A | California Portland Cement | 2000-06-10 | Liquid | 1 ppm | Tap meter
300 A | 225.57 A | California Portland Cement | 2000-06-26 | Liquid | 1 ppm | Tap meter
300 A | 225.57 A | California Portland Cement | 2000-07-24 | Liquid | 2 ppm | Tap meter, < 10 mls
300 A | 225.57 A | California Portland Cement | 2000-08-07 | Liquid | 2 ppm | Tap meter, < 10 mls
300 A | 225.57 A | California Portland Cement | 2000-08-21 | Liquid | 8 ppm | Tap meter, < 10 mls
300 A | 225.57 A | California Portland Cement | 2000-09-18 | Liquid | 2 ppm | Tap meter, < 10 mls
300 A | 225.91 A | California Portland Cement | 2000-02-24 | Wipe | < 1 ug/100cm2 | Wipe sample from bottom of meter
300 A | 225.91 A | California Portland Cement | 2000-04-05 | Liquid | ND < 1 ppm | Primary, downstream
300 A | 225.91 A | California Portland Cement | 2000-05-04 | Liquid | ND < 1 ppm | Primary, downstream
300 A | 225.91 A | California Portland Cement | 2000-04-05 | Liquid | 4 ppm as Aroclor 1260 | 12 GT Meter, sample taken downstream
300 A | 225.91 A | California Portland Cement Meter | 2000-04-19 | Liquid | ND < 1ppm
300 A | 225.91 A | California Portland Cement Meter | 2000-05-15 | Liquid |  | Insufficient Sample
300 A | 225.91 A | California Portland Cement Meter | 2000-06-10 | Liquid | 1 ppm
300 A | 225.91 A | California Portland Cement Meter | 2000-07-24 | None
300 A | 225.91 A | California Portland Cement Meter | 2000-08-21 | None
300 A | 225.91 A | California Portland Cement Meter | 2000-09-05 | Liquid | 1 ppm | <10 mls
300 A | 225.91 A | California Portland Cement Meter | 2000-09-18 | None |  | no liquid
300 A | 225.91 A | California Portland Cement Meter | 2000-10-02 | Liquid | 2 ppm
300 A | 116.28 B | P.L.G. X-tie (Pisgah) |  | None |  | Tap not inspected or sampled
300 B | 129.92 B | John R. Mason, Newberry (Customer meter) | 2000-02-09 | None |  | No liquid; no wipe
300 B | 129.92 B | John R. Mason, Newberry (TAP) | 2000-02-09 | None |  | No acceptable sampling point
300 B | 130.38 B | Line 300 B insertion meter | 2000-02-11 | Wipe | ND < 0.7 ug/100cm2 | Pulled insertion meter; measured exterior surface area (not including turbine wheel); took wipe sample of measured area
300 B | 130.38 B | PLS 2XA Mist Extractor | 2000-04-12 | Liquid | ND <1ppm
300 B | 131.37 B | RHEOX Chem. Co. | 2000-02-08 | Liquid | 6 ppm | Sample obtained from filter, downstream of regulator. Black thick liquid obtained Good taps before and after meter available for sampling.
300 B | 131.37 B | RHEOX Chem. Co. | 2000-02-24 | Liquid | 14 ppm | Meter Set, Filter
300 B | 131.37 B | RHEOX Chem. Co. | 2000-03-09 | Liquid | 10 ppm | Meter Set, Filter
300 B | 131.37 B | RHEOX Chem. Co. | 2000-03-21 | Liquid | 17 ppm | Meter Set, Filter
300 B | 131.37 B | RHEOX Chem. Co. | 2000-04-05 | Liquid | 13 ppm | Meter Set, Filter
300 B | 131.37 B | RHEOX Chem. Co. | 2000-04-17 | Liquid | 13 ppm | Meter Set, Filter
300 B | 131.37 B | RHEOX Chem. Co. | 2000-04-17 | Liquid | ND < 1ppm | Meter Separator
300 B | 131.37 B | RHEOX Chem. Co. | 2000-05-03 | Liquid | 35 ppm | Meter Set, Filter
300 B | 131.37 B | RHEOX Chem. Co. | 2000-05-16 | Liquid | 12 ppm | Meter Set, Filter
300 B | 131.37 B | RHEOX Chem. Co. | 2000-05-30 | Liquid | 12 ppm | Meter Set, Filter
300 B | 131.37 B | RHEOX Chem. Co. | 2000-06-13 | Liquid | 12 ppm | Meter Set, Filter
300 B | 131.37 B | RHEOX Chem. Co. | 2000-06-27 | Liquid | 12 ppm | Meter Set, Filter
300 B | 131.37 B | RHEOX Chem. Co. | 2000-07-25 | Liquid | 10 ppm | Meter Set, Filter, < 10 mls
300 B | 131.37 B | RHEOX Chem. Co. | 2000-08-22 | None |  | no liquid - new filter separator installed
300 B | 131.37 B | RHEOX Chem. Co. | 2000-09-19 | None |  | no liquid - new filter separator installed
300 B | 131.37 B | Interto Co. Newberry, (American Transel Co.) |  | None |  | Tap not inspected or sampled - Line Abandoned
300 B | 135.65 B | Southwest Gas Corp. (Cirano Farm) |  | None |  | Tap not inspected or sampled
300 B | 137.55 B | SWG, Daggett Airport Tap | 2000-02-11 | None |  | Sample tap available from bottom of filter - No liquids were found.
300 B | 138.67 B | Hell's Acre Ranch |  | None |  | Tap not inspected or sampled - Service Tee and Valve only. Southwest Gas to furnish meter, etc.
300 B | 140.00 B | Kern River Daggett Intertie | 2000-02-10 | None |  | No liquid from #7 Bypass valve next to filter separator. Separator is shut-in.
300 B | 140.65 B | SEGS 1 Meter Set | 2000-02-08 | Wipe | < 1ug/100cm2 | Wipe taken from 2 inches inside meter casing on inlet side
300 B | 140.65 B | SEGS 1 Meter Set | 2000-02-08 | Liquid | 6 ppm | Small amount of clear liquid present at bottom of meter.
300 B | 140.65 B | SEGS 1 Meter Set | 2000-02-23 | Liquid | 2 ppm
300 B | 140.65 B | SEGS 1 Meter Set | 2000-03-21 | Liquid | 4 ppm
300 B | 140.65 B | SEGS 1 Meter Set | 2000-04-05 | Liquid | 6 ppm
300 B | 140.65 B | SEGS 1 Meter Set | 2000-04-17 | Liquid | 4 ppm
300 B | 140.65 B | SEGS 1 Meter Set | 2000-05-03 | Liquid | 5 ppm
| 140.65 B | SEGS 1 Meter Set | 2000-06-13 | Liquid | 6 ppm
300 B | 140.65 B | SEGS 1 Primary drip Pot | 2000-02-08 | Wipe | < 1ug/100cm2 | Wipe sample taken from East filter only filter was degraded
300 B | 140.65 B | SEGS 1 Primary drip Pot | 2000-03-09 | Liquid | 2 ppm
300 B | 140.65 B | SEGS 1 Primary drip Pot | 2000-06-13 | Liquid | 6 ppm
300 B | 140.65 B | SEGS 1 Primary drip Pot | 2000-06-27 | Liquid | 5 ppm
300 B | 140.65 B | SEGS 1 Primary drip Pot | 2000-07-25 | None
300 B | 140.65 B | SEGS 1 Primary drip Pot | 2000-08-21 | None
300 B | 140.65 B | SEGS 1 Primary drip Pot | 2000-09-19 | None |  | Dry
300 B | 140.91 B | SWG, Daggett | 2000-02-10 | None |  | Sample tap available from bottom of filter - No liquids were found.
300 B | 159.33 B | Hinkley Compressor Station K-7, B Outlet | 2000-02-15 | Liquid | ND < 1 ppm
300 B | 159.33 B | Hinkley Compressor Station K-7, B Outlet | 2000-02-15 | Wipe | < 1ug/wipe
300 B | 159.33 B | Hinkley Compressor Station K-7, B Inlet | 2000-02-15 | Liquid | 1 ppm
300 B | 159.33 B | Hinkley Compressor Station 300B Suction Drip | 2000-01-27 | Liquid | 4 ppm
300 B | 159.33 B | Hinkley Compressor Station 300B Suction Drip | 2000-02-10 | Liquid | 4 ppm | Black liquid obtained. Drip was emptied after sample was obtained
300 B | 159.33 B | Hinkley Compressor Station B V-211 Inlet Drip | 2000-04-20 | Liquid | 11 ppm
300 B | 159.33 B | Hinkley Compressor Station B V-211 Inlet Drip | 2000-05-02 | Liquid | 10 ppm
300 B | 159.33 B | Hinkley Compressor Station B V-211 Inlet Drip | 2000-06-15 | Liquid | 8 ppm
300 B | 159.33 B | Hinkley Compressor Station B V-211 Inlet Drip | 2000-08-18 | Liquid | 9 ppm
300 B | 159.33 B | Hinkley Compressor Station B V-211 Inlet Drip | 2000-09-05 | Liquid | 12 ppm | 50 mls
300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-02-25 | Liquid | 7 ppm
300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-03-09 | Liquid | 8 ppm
300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-03-23 | Liquid | 12 ppm
300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-04-06 | Liquid | 7 ppm
300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-04-20 | Liquid | 7 ppm
300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-05-01 | Liquid | 7 ppm
300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-05-14 | Liquid | 11 ppm
300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-05-30 | Liquid | 7 ppm
300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-06-15 | Liquid | 8 ppm
300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-06-30 | Liquid | 8 ppm
300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-08-18 | Liquid | 9 ppm
300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-08-18 | Liquid | 10 ppm | ~40 mls
300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-09-18 | Liquid | 10 ppm | ~40 mls
300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-02-10 | Liquid | 1ppm | Sample obtained from bottom of inlet filter to 8" meter run.
300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-02-25 | Liquid | 2 ppm | Sample obtained from 8" filter
300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-03-09 | Liquid | 1 ppm | Sample obtained from 8" filter
300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-03-23 | Liquid | 2 ppm | Sample obtained from 8" filter
300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-04-23 | Liquid | <1 ppm | Sample obtained from 8" filter
300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-05-01 | Liquid | 1 ppm | Sample obtained from 8" filter
300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-05-14 | Liquid | 1 ppm | Sample obtained from 8" filter
300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-06-01 | Liquid | 1 ppm | Sample obtained from 8" filter
300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-06-15 | Liquid | 2 ppm | Sample obtained from 8" filter
300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-06-30 | Liquid | 1 ppm | Sample obtained from 8" filter
300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-07-29 | Liquid | 1 ppm | Sample obtained from 8" filter
300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-08-21 | Liquid | 2 ppm | Sample obtained from 8" filter
300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-09-05 | Liquid | 2 ppm | Sample obtained from 8" filter, ~10 mls
300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-09-19 | Liquid | 2 ppm | Sample obtained from 8" filter, ~10 mls
300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-10-03 | Liquid | 2 ppm | Sample obtained from 8" filter, < 10 mls
300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-02-25 | Liquid | ND < 1ppm | Sample taken from 10" filter
300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-03-09 | Liquid | ND < 1ppm | Sample taken from 10" filter
300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-03-23 | Liquid |  | Sample container received broken - no analysis
300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-04-18 | Liquid | 2 ppm | Sample taken from 10" filter
300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-07-29 | None |  | Sample taken from 10" filter
300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-02-10 | Liquid | 1 ppm
300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-02-10 | Liquid | 1 ppm | Liquids obtained from drip. Drip completely drained after sampling. Drip was also drained during first week of 2/2000.
300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-03-09 | Liquid | 1 ppm
300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-04-06 | Liquid | 1 ppm
300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-04-19 | Liquid | < 1 ppm
300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-05-01 | Liquid | ND < 1 ppm
300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-05-14 | Liquid | ND < 1 ppm
300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-06-01 | Liquid |  | Insufficient sample
300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-06-15 | Liquid | 1 ppm
300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-06-30 | Liquid | 1 ppm
300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-07-29 | Liquid | 1 ppm
300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-08-21 | Liquid | 1 ppm
300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-09-06 | Liquid | 1 ppm | ~20 mls
300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-09-19 | Liquid | 2 ppm | ~20 mls
300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-10-03 | Liquid | 2 ppm | ~20 mls
300 B | 170.44 B | South West Gas - Harper Lake Meter Station |  | None |  | Tap not inspected or sampled
300 B | 180.11 B | Trona - Main # 311 X |  | None |  | Tap not inspected or sampled
300 B | 182.00 B | John Wiles Co. |  | None |  | Farm tap Reg. Set. Tap. Service tap not inspected or sampled and is abandoned
300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-02-10 | Liquid | 2 ppm | Mist generated during sampling (light coating in bottle only)
300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-02-24 | Liquid | 2 ppm
300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-03-08 | Liquid | 3 ppm
300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-03-22 | Liquid | 3 ppm
300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-04-05 | Liquid | 2 ppm
300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-04-17 | Liquid | 3 ppm
300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-05-04 | Liquid | 2 ppm
300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-05-16 | Liquid | 1 ppm
300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-05-30 | Liquid | 2 ppm
300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-06-13 | Liquid | 2 ppm
300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-06-27 | Liquid | 3 ppm
300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-07-25 | Liquid | 3 ppm | < 10 mls
300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-08-07 | Liquid | 4 ppm | ~10 mls
300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-08-22 | Liquid | 3 ppm | ~50 mls liquid
300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-09-06 | Liquid | 6 ppm as Aroclor 1016, 2 ppm as Aroclor 1254 | ~10 mls
300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-09-18 | Liquid | 6 ppm | ~10 mls
300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-10-04 | Liquid | 4 ppm
300 B | 182.58 B | SEGS 5,6 & 7 Primary | 2000-02-10 | None |  | Filter was dry
300 B | 182.58 B | SEGS 7 Meter Set | 2000-02-10 | None |  | Turbine mater sample - dry
300 B | 187.78 B | Boron Tap | 2000-02-10 | Liquid | 1 ppm | Primary reg. filter, East run; good sample
300 B | 187.78 B | Boron Tap | 2000-02-24 | Liquid | 2 ppm
300 B | 187.78 B | Boron Tap | 2000-03-08 | Liquid | 1 ppm
300 B | 187.78 B | Boron Tap | 2000-04-04 | Liquid | 1 ppm
300 B | 187.78 B | Boron Tap | 2000-04-17 | Liquid | 1 ppm
300 B | 187.78 B | Boron Tap | 2000-05-04 | Liquid | 1 ppm
300 B | 187.78 B | Boron Tap | 2000-05-15 | Liquid | 1 ppm
300 B | 187.78 B | Boron Tap | 2000-06-01 | Liquid | 1 ppm
300 B | 187.78 B | Boron Tap | 2000-06-27 | None |  | Insufficient sample
300 B | 187.78 B | Boron Tap | 2000-08-22 | None |  | no liquids
300 B | 187.78 B | Boron Tap | 2000-09-06 | None |  | no liquids
300 B | 187.78 B | Boron Tap | 2000-09-19 | None |  | no liquids
300 B | 187.78 B | Boron High School Dry Gas Meter No. 32707774 | 2000-03-15 | Wipe | ND < 1ug/wipe | Meter removed and replaced. Non-quantitative wipe taken on drain cover and inside of drain cover opening.
300 B | 187.78 B | Joshua Trailer Park, 26611 Nugent, Boron | 2000-03-13 | Wipe | ND < 1ug/wipe | Non-quantitative wipe inside filter
300 B | 191.14 B | US Borax (Bypass) |  | None |  | Tap not inspected or sampled
300 B | 191.18 B | Desert Lakes US Borax | 2000-02-10 | None |  | Primary reg. filter, North run; dry (Recheck filter)
300 B | 191.18 B | US Borax |  | None |  | Tap not inspected or sampled
300 B | 197.70 B | M. Penn Philips Tract, Gilbert St. |  | None |  | Tap not inspected or sampled; line abandoned
300 B | 198.88 B | Edgemont Road District (West Boron Area) Increase Capacity |  | None |  | San Joaquin Div., original farm tap and reg. Installed second farm tap and reg. in parallel with existing set. Taps not inspected or sampled.
300 B | 199.24 B | Fountain Trailer Court |  | None |  | Tap not inspected or sampled - line abandoned in 1987
300 B | 203.07 B | PLS 3B Insertion Meter | 2000-02-16 | Wipe | ND <0.7 ug/100cm2
300 B | 203.07 B | PLS 3B Mist Extractor | 2000-04-14 | Liquid | ND < 1ppm
300 B | 203.07 B | Emergency Tie-in to Main 300B |  | None |  | Tap not inspected or sampled
300 B | 239.04 B | Tehachapi |  | None |  | Tap not inspected or sampled - line abandoned
311 X | 54.88 | Ridgecrest West End Primary | 2000-02-22 | Wipe | < 1ug/100cm2 | Right Filter
311 X | 54.88 | Ridgecrest West End Primary | 2000-04-06 | Wipe | ND < 1ug/wipe | Right Filter (non-quantitative wipe)
311 X | 54.88 | Ridgecrest West End Primary | 2000-04-19 | Wipe | ND < 1ug/wipe | Right Filter (non-quantitative wipe)
311 X | 54.88 | Ridgecrest West End Primary | 2000-07-24 | None
311 X | 54.88 | Ridgecrest West End Primary | 2000-09-18 | None
311 X | 54.88 | IMC Chemical, Trona | 2000-04-03 | Wipe | 2.6 ug/wipe as Aroclor 1016, 1.2 ug/wipe as Aroclor 1254 | West End Turbine Meter
311 X | 54.88 | Ridgecrest West End Turbine Meter | 2000-04-19 | Liquid | 11 ppm as Aroclor 1016, 12 ppm as Aroclor 1260
311 X | 54.88 | Ridgecrest West End Turbine Meter | 2000-05-04 | Liquid | 11 ppm as Aroclor 1016, 8 ppm as Aroclor 1254
311 X | 54.88 | Ridgecrest West End Turbine Meter | 2000-05-31 | Liquid | 13 ppm as Aroclor 1016, 9 ppm as Aroclor 1254
311 X | 54.88 | Ridgecrest West End Turbine Meter | 2000-06-12 | Liquid | 16 ppm as Aroclor 1016, 7 ppm as Aroclor 1260
311 X | 54.88 | Ridgecrest West End Turbine Meter | 2000-06-26 | Liquid | 11 ppm as Aroclor 1016, 17 ppm as Aroclor 1260
311 X | 54.88 | Ridgecrest West End Turbine Meter | 2000-07-24 | Liquid | 8.4 ppm as Aroclor 1016, 7.9 ppm as Aroclor 1260
311 X | 54.88 | Ridgecrest West End Turbine Meter | 2000-08-08 | Liquid | 29 ppm as Aroclor 1016, 27 ppm as Aroclor 1254 | <10 mls
311 X | 54.88 | Ridgecrest West End Turbine Meter | 2000-09-05 | Liquid | 6 ppm as Aroclor 1016, 9 ppm as Aroclor 1254 | < 10 mls
311 X | 54.88 | Ridgecrest West End Turbine Meter | 2000-09-18 | Liquid | 7 ppm as Aroclor 1016, 9 ppm as Aroclor 1260 | < 10 mls
311 X | 54.88 | Ridgecrest West End Turbine Meter | 2000-09-18 | Liquid |  | < 10 mls (Insufficient sample)
311 X | 54.88 | Ridgecrest West End Process | 2000-05-04 | Liquid | 4 ppm as Aroclor 1016, 4 ppm as Aroclor 1254 | Turbine mater
311 X | 54.88 | Ridgecrest West End Process | 2000-05-16 | Liquid | 4 ppm as Aroclor 1016, 12 ppm as Aroclor 1254
311 X | 54.88 | Ridgecrest West End Process | 2000-05-31 | Liquid | 5 ppm as Aroclor 1016, 8 ppm as Aroclor 1254
311 X | 54.88 | Ridgecrest West End Process | 2000-08-21 | None |  | no liquids found
311 X | 54.88 | Ridgecrest West End Process | 2000-10-02 | Liquid | 10 ppm as Aroclor 1016, 7 ppm as Aroclor 1260 | no liquids found
311 X | 54.44 | West End Plant (old meter set) | 2000-06-12 | Wipe | ND < 1 ug/wipe | Semi-quantitative
311 X | 54.44 | West End Plant (old meter set) | 2000-08-21 | None |  | no liquid found
311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2000-05-31 | Liquid | 4 ppm as Aroclor 1016, 11 ppm as Aroclor 1254 | 12 GT Meter
311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2000-06-12 | Liquid | 6 ppm as Aroclor 1016, 7 ppm as Aroclor 1260
311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2000-06-26 | Liquid | 5 ppm as Aroclor 1016, 9 ppm as Aroclor 1260
311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2000-08-08 | Liquid | 8 ppm as Aroclor 1016, 19 ppm as Aroclor 1254
311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2000-08-21 | Liquid | 8 ppm as Aroclor 1016, 27 ppm as Aroclor 1254 | <10 mls taken from meter drip
311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2000-09-05 | Liquid | 3 ppm as Aroclor 1016, 11 ppm as Aroclor 1254 | < 10 mls
311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2000-09-18 | Liquid | 3 ppm as Aroclor 1016, 12 ppm as Aroclor 1260 | < 10 mls
311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2000-09-18 | Liquid | 2 ppm as Aroclor 1016, 8 ppm as Aroclor 1260 | < 10 mls
313 X | 27.26 | SWG Rabbit Springs Rd. | 2000-02-09 | Liquid | 2 ppm, < 1ppm as Aroclor 1260. Semi quantitative results due to small sample | Obtained small amount of liquid obtained from bottom tap of meter. No liquid from gooseneck pipe on north filter.
313 X | 27.26 | SWG Rabbit Springs Rd. Meter | 2000-02-28 | Liquid | 4 ppm
313 X | 27.26 | SWG Rabbit Springs Rd. Meter | 2000-03-10 | Liquid | 10 ppm
313 X | 27.26 | SWG Rabbit Springs Rd. Meter | 2000-03-22 | Liquid | 5 ppm
313 X | 27.26 | SWG Rabbit Springs Rd. Meter | 2000-04-06 | Liquid | 9 ppm
313 X | 27.26 | SWG Rabbit Springs Rd. Meter | 2000-05-14 | Liquid | 4 ppm
313 X | 27.26 | SWG Rabbit Springs Rd. Meter | 2000-06-14 | Liquid | 11 ppm
313 X | 27.26 | SWG Rabbit Springs Rd. Meter | 2000-06-30 | Liquid | 9 ppm as Aroclor 1016, 2 ppm as Aroclor 1254
313 X | 27.76 | SWG, Rabbit Springs Rd. Meter | 2000-02-09 | None |  | Filter downstream from MP27.26 not accessible
313 X | 27.76 | SWG, Rabbit Springs Rd. Meter | 2000-07-29 | Liquid | 6.8 ppm, as Aroclor 1016, 1.1 ppm, as Aroclor 1260
313 X | 27.76 | SWG, Rabbit Springs Rd. Meter | 2000-09-05 | Liquid |  | <10 mls (insuffiient sample)
313 X | 29.08 | SWG Old Woman Springs | 2000-02-09 | None |  | North filter is dry (no way to sample bypass filter)
313 X | 34.34 | Mitsubishi Cement | 2000-02-09 | Liquid | 2 ppm, 3ppm as Aroclor 1260 | Sample taken from bottom of filter (gas flowing 6 mcf / hour)
313 X | 34.34 | Mitsubishi Cement | 2000-02-23 | None |  | Filter Dry (check location)
313 X | 34.34 | Mitsubishi Cement | 2000-02-24 | Liquid | 3 ppm, 3ppm as Aroclor 1254 | Sample from meter set
313 X | 34.34 | Mitsubishi Cement | 2000-03-08 | Liquid | 4 ppm as Aroclor 1016, 3ppm as Aroclor 1260 | Sample from meter set
313 X | 34.34 | Mitsubishi Cement | 2000-03-20 | Liquid | 2 ppm as Aroclor 1016, 3ppm as Aroclor 1260 | Sample from meter set
313 X | 34.34 | Mitsubishi Cement | 2000-04-05 | Liquid | 3 ppm as Aroclor 1016, 3ppm as Aroclor 1254 | Sample from meter set
313 X | 34.34 | Mitsubishi Cement | 2000-04-05 | Liquid | 1 ppm as Aroclor 1016, 3ppm as Aroclor 1254 | Sample from meter set
313 X | 34.34 | Mitsubishi Cement | 2000-04-27 | Liquid | 7 ppm as Aroclor 1016, 2 ppm as Aroclor 1254 | Sampled Labeled as "Big Bear B" at MP 34.34
313 X | 34.34 | Mitsubishi Cement | 2000-05-01 | Liquid | 1 ppm as Aroclor 1016, 3 ppm as Aroclor 1254
313 X | 34.34 | Mitsubishi Cement | 2000-05-15 | Liquid | 2 ppm as Aroclor 1016, 4 ppm as Aroclor 1254
313 X | 34.34 | Mitsubishi Cement | 2000-05-30 | Liquid | 3 ppm as Aroclor 1016, 3 ppm as Aroclor 1254
313 X | 34.34 | Mitsubishi Cement | 2000-06-13 | Liquid | 4 ppm as Aroclor 1016, 3 ppm as Aroclor 1260
313 X | 34.34 | Mitsubishi Cement | 2000-07-24 | Liquid | 1 ppm as Aroclor 1016, 0.6 ppm as Aroclor 1260 | < 10 mls
313 X | 34.34 | Mitsubishi Cement | 2000-08-08 | None |  | Meter set dry
313 X | 34.34 | Mitsubishi Cement | 2000-08-21 | Liquid | ND < 1 ppm | < 10 mls
313 X | 34.34 | Mitsubishi Cement | 2000-09-05 | Liquid | ND < 1 ppm | < 10 mls
313 X | 34.34 | Mitsubishi Cement | 2000-09-18 | Liquid | ND < 3 ppm | < 10 mls (reporting limit raised because of small sample size)
313 X | 34.34 | Mitsubishi Cement | 2000-10-04 | Liquid | 42 ppm
314 X | 0.02 | Company Use |  |  |  | Tap not Inspected or sampled (Hinkley Tap)
314 X | 0.06 | SW Gas (Hinkley Tap) |  |  |  | Tap not Inspected or sampled
314 X | 8.76 | SW Gas (Zackey Farms) |  |  |  | Tap not inspected or sampled
314 X | 21.76 | SW Gas (La Delta, Helendale) |  |  |  | Tap not Inspected or sampled (San Joaquin Div. job)
314 X | 24.31 | TXI Riverside Cement PLS | 2000-02-09 | None |  | Active filter next to Valve 4. Bottom tap of filter is dry. Note: Clearance reqrd. for filter removal and wipe sampling
314 X | 24.31 | TXI Riverside Cement PLS | 2000-08-21 | None |  | no liquids
314 X | 24.31 | TXI Riverside Cement PLS | 2000-09-06 | None |  | no liquids
314 X | 24.31 | TXI Riverside Cement PLS | 2000-09-18 | None |  | no liquids
314 X | 24.75 | TXI Riverside Tap Meter | 2000-02-09 | Liquid | 16 ppm, 4ppm as Aroclor 1260 | Sample taken from bottom of turbine meter - small amount of liquid
314 X | 24.75 | TXI Riverside Tap Meter | 2000-02-15 | Liquid | 9 ppm
314 X | 24.75 | TXI Riverside Tap Meter | 2000-02-23 | Liquid | 19 ppm as Aroclor 1016, 5 ppm as Aroclor 1254
314 X | 24.75 | TXI Riverside Tap Meter | 2000-03-08 | Liquid | 45 ppm
314 X | 24.75 | TXI Riverside Tap Meter | 2000-03-22 | Liquid | 11 ppm
314 X | 24.75 | TXI Riverside Tap Meter | 2000-04-05 | Liquid | 24 ppm as Aroclor 1016, 7 ppm as Aroclor 1254
314 X | 24.75 | TXI Riverside Tap Meter | 2000-04-18 | Liquid | 22 ppm, 5 ppm as Aroclor 1260
314 X | 24.75 | TXI Riverside Tap Meter | 2000-05-01 | Liquid | 6 ppm
314 X | 24.75 | TXI Riverside Tap Meter | 2000-05-15 | Liquid | 5 ppm, 2 ppm as Aroclor 1254 | Bottom inside Meter
314 X | 24.75 | TXI Riverside Tap Meter | 2000-05-15 | Liquid | < 1 ppm | Top of inside meter
314 X | 24.75 | TXI Riverside Tap Meter | 2000-05-30 | Liquid | 31 ppm, 3 ppm as Aroclor 1254 | Bottom inside Meter
314 X | 24.75 | TXI Riverside Tap Meter | 2000-06-12 | Liquid | 34 ppm, 3 ppm as Aroclor 1254
314 X | 24.75 | TXI Riverside Tap Meter | 2000-06-26 | Liquid | 30 ppm, 3 ppm as Aroclor 1254
314 X | 24.75 | TXI Riverside Tap Meter | 2000-07-24 | Liquid | 26 ppm, 2.5 ppm as Aroclor 1254 | < 10 mls
314 X | 24.75 | TXI Riverside Tap Meter | 2000-08-08 | Liquid | 40 ppm, 12 ppm as Aroclor 1254 | < 10 mls
314 X | 24.75 | TXI Riverside Tap Meter | 2000-08-21 | Liquid | 25 ppm, 14 ppm as Aroclor 1254 | < 10 mls
314 X | 24.75 | TXI Riverside Tap Meter | 2000-09-05 | Liquid | 16 ppm, 6 ppm as Aroclor 1254 | < 10 mls
314 X | 24.75 | TXI Riverside Tap Meter | 2000-09-18 | Liquid | 20 ppm, 3 ppm as Aroclor 1260 | < 10 mls
314 X | 24.75 | TXI Riverside Tap Meter | 2000-10-04 | Liquid | 22 ppm, 4 ppm as Aroclor 1254 | < 10 mls
314 X | 25.2 | SW Gas (Academy Road) |  |  |  | Tap not Inspected or sampled (San Joaquin Div. job)
314 X | 26 | SW Gas (Clanton) |  |  |  | Tap not Inspected or sampled (San Joaquin Div. job)
314 X | 26.8 | None |  |  |  | Tap not inspected or sampled (4" valve installed on original const. for SWG - capped)
314 X | 27.46 | Victorville "B" Meter | 2000-02-15 | Liquid | 5 ppm
314 X | 27.46 | Victorville "B" Meter | 2000-07-15 | Liquid | 3.5 ppm as Aroclor 1016, 0.6 ppm as Aroclor 1260
314 X | 28.76 | Southwest Portland Cement |  |  |  | Tap not inspected or sampled -Original Construction
314 X | 30.5 | Stoddard Wells Tap |  |  |  | Tap not inspected or sampled
314 X | 34.22 | Oro Grande - Victorville F | 2000-05-14 | Liquid | 35 ppm | Feeds Oro Grande Township
314 X | 34.22 | Oro Grande - Victorville F | 2000-05-30 | Liquid | 6 ppm
314 X | 34.22 | Oro Grande - Victorville F | 2000-06-14 | Liquid | 11 ppm
314 X | 34.22 | Oro Grande - Victorville F | 2000-06-29 | Liquid | 10 ppm
314 X | 34.22 | Oro Grande - Victorville F | 2000-07-29 | None |  | Filter was dry
314 X | 34.22 | Oro Grande - Victorville F | 2000-08-21 | Liquid | 16 ppm
314 X | 34.22 | Oro Grande - Victorville F | 2000-10-02 | Liquid | 5 ppm | < 10 mls
314 X | 34.34 | Big Bear "B" | 2000-02-09 | None |  | Two filters; both are dry
314 X | 34.34 | Big Bear "B" | 2000-04-27 | Liquid | 7 ppm as Aroclor 1016, 2 ppm as Aroclor 1254
314 X | 34.34 | Big Bear "B" | 05/14/00. | Liquid | 38 ppm as Aroclor 1016, 3 ppm as Aroclor 1254 | Sample from meter set
314 X | 34.34 | Big Bear "B" | 2000-05-30 | Liquid | 6 ppm as Aroclor 1016, 2 ppm as Aroclor 1254
314 X | 34.34 | Big Bear "B" | 2000-06-14 | Liquid | 16 ppm as Aroclor 1016, 2 ppm as Aroclor 1260
314 X | 34.34 | Big Bear "B" | 2000-06-29 | Liquid | 16 ppm as Aroclor 1016, 3 ppm as Aroclor 1254
314 X | 34.34 | Big Bear "B" | 2000-07-29 | Liquid | 15 ppm as Aroclor 1016, 2 ppm as Aroclor 1254
314 X | 34.34 | Big Bear "B" | 2000-08-18 | Liquid | 16 ppm as Aroclor 1016, 2 ppm as Aroclor 1260
314 X | 34.34 | Big Bear "B" | 2000-09-05 | Liquid | 16 ppm as Aroclor 1016, 3 ppm as Aroclor 1254 | ~20 mls
314 X | 34.34 | Big Bear "B" | 2000-09-18 | Liquid | 17 ppm as Aroclor 1016, 3 ppm as Aroclor 1254 | ~20 mls
314 X | 34.34 | Big Bear "B" | 2000-10-02 | Liquid | 17 ppm as Aroclor 1016, 3 ppm as Aroclor 1254 | ~20 mls
314 X | 38.57 | Victorville "C" SWG | 2000-02-09 | None |  | Two filters; both are dry
314 X | 38.57 | Victorville "C" Meter | 2000-02-17 | Liquid | 5 ppm as Aroclor 1016, 4 ppm, as Aroclor 1254
314 X | 38.57 | Victorville "C" Meter | 2000-03-22 | Liquid | 3 ppm, as Aroclor 1254
314 X | 43.18 | Black Mountain Cement | 2000-02-09 | None |  | Meter tap is dry. Filter on low flow run is dry
314 X | 43.18 | Black Mountain Cement | 2000-03-23 | Liquid | 0.2 ppm as Aroclor 1016, 0.8 ppm, as Aroclor 1254 | Sample from Filter
314 X | 43.18 | Black Mountain Cement | 2000-03-23 | Wipe | 2 ug /wipe as Aroclor 1254 | semi-quantittative wipw inside filter canister
314 X | 43.18 | Black Mountain Cement | 2000-04-05 | Wipe | 2 ug /wipe as Aroclor 1254 | semi-quantittative wipw inside filter canister
314 X | 43.18 | Black Mountain Cement | 2000-03-23 | Liquid | 3 ppm as Aroclor 1254 | Sample from Filter
314 X | 43.18 | Black Mountain Cement | 2000-05-01 | Liquid |  | Insufficient Sample
314 X | 43.18 | Black Mountain Cement | 2000-05-15 | Solid | < 1 ppm | Dust from Filter
314 X | 43.18 | Black Mountain Cement | 2000-07-24 | None |  | Filter
314 X | 43.18 | Black Mountain Cement | 2000-08-21 | Wipe | ND < 1ug/100cm2
314 X | 43.18 | Black Mountain Cement | 2000-09-06 | None |  | No liquids
314 X | 43.18 | Black Mountain Cement | 2000-09-18 | None |  | No liquids
372 X (Line 311 branch) | 3.7 | R.C. Primary Reg. Station | 2000-05-04 | Wipe | ND < 1ug/100cm2 | Ridgecrest primary filter
372 X (Line 311 branch) | 3.7 | R.C. Primary Reg. Station | 2000-05-16 | Wipe | ND < 1ug/100cm2 | Ridgecrest primary filter
372 X (Line 311 branch) | 3.7 | R.C. Primary Reg. Station | 2000-05-16 | Liquid | < 1 ppm | Ridgecrest primary, liquid taken from orifice meter
372 X (Line 311 branch) | 3.7 | R.C. Primary Reg. Station | 2000-08-21 | None |  | Filter Dry

## Kettleman District 2000
LINE | Mile Point | Description | Sample Date | Sample Type | Result (All results as Aroclor 1016 unless otherwise noted) | Comments
142 | 1.2 | Gosford and White Road tap | 2000-05-27 | Liquid | 1 ppm
142 | 1.2 | Gosford and White Road tap | 2000-06-02 | Liquid | 2 ppm
142 | 1.2 | Gosford and White Road tap | 2000-07-13 | Liquid | 2 ppm
142 | 1.2 | Gosford and White Road tap | 2000-07-23 | None |  | Dry
142 | 1.2 | Gosford and White Road tap | 2000-08-10 | None |  | insufficient sample
142 | 1.2 | Gosford and White Road tap | 2000-09-08 | None |  | insufficient sample
142 | 1.2 | Gosford and White Road tap | 2000-09-21 | Liquid | 2 ppm | < 10 ml
142 | 1.2 | Gosford and White Road tap | 2000-10-05 | Liquid | 2 ppm | < 10 ml
142 | 4.3 | White Lane and Wible | 2000-07-23 | None |  | Dry
142 | 4.3 | White Lane and Wible | 2000-08-10 | None |  | Dry
142 | 4.3 | White Lane and Wible | 2000-09-08 | None |  | Dry
142 | 4.3 | White Lane and Wible | 2000-10-05 | None |  | Dry
142 | 11.47 | Bakersfield Tap off Line 300 A | 2000-07-13 | None
142 | 11.47 | Bakersfield Tap | 2000-07-23 | Trace |  | Insufficient sample
142 | 14.05 | Bakersfield Reg. Station | 2000-07-27 | Liquid | 3 ppm
142 | 14.05 | Bakersfield Reg. Station | 2000-08-10 | Trace |  | Insufficient sample
142 | 14.05 | Bakersfield Reg. Station | 2000-09-08 | Liquid | 4 ppm | <10 mls
142 | 14.05 | Bakersfield Reg. Station | 2000-10-05 | None |  | Dry
300 A | 130.37 A | Line 300 A Drip | 2000-03-22 | Liquid | 2 ppm
300 A | 256.21 A | PLS4A Insertion Meter | 2000-02-17 | Wipe | ND < 0.7 ug/100cm2 | Took wipe samples on same surfaces as was done on Line 300 B PLS 2X Insertion Meter (MP 130.39 B)
300 A | 260.50 A | Arvin Cotton Gin |  | None |  | Tap not inspected or sampled
300 A | 267.26 A | Costerisan Farms |  | None |  | Tap not inspected or sampled
300 A | 269.05 A | Shafter School and Others |  | None |  | Tap not inspected or sampled
300 A | 270.74 A | Kern Delta Gin (new) | 2000-02-17 | None |  | Took wipe samples on same surfaces as was done on Line 300 B PLS 2x Insertion Meter (MP 130.39 B). Note: wipe sample accidentally dropped in meter pit.
300 A | 280.58 A | Kern River Intake Header | 2000-03-22 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Intake Header | 2000-04-06 | Liquid | 3 ppm
300 A | 280.58 A | Kern River Intake Header | 2000-04-12 | Liquid | 3 ppm
300 A | 280.58 A | Kern River Intake Header | 2000-04-26 | Liquid | 1 ppm
300 A | 280.58 A | Kern River Intake Header | 2000-05-04 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Intake Header | 2000-05-10 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Intake Header | 2000-05-26 | Liquid | 1 ppm
300 A | 280.58 A | Kern River Intake Header | 2000-05-31 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Intake Header | 2000-06-07 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Intake Header | 2000-06-14 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Intake Header | 2000-06-21 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Intake Header | 2000-06-29 | Liquid | 3 ppm
300 A | 280.58 A | Kern River Intake Header | 2000-07-07 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Intake Header | 2000-07-19 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Intake Header | 2000-07-27 | Liquid | 3 ppm
300 A | 280.58 A | Kern River Intake Header | 2000-08-01 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Intake Header | 2000-08-10 | Liquid | 1 ppm | ~100 mls.
300 A | 280.58 A | Kern River Intake Header | 2000-08-16 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Intake Header | 2000-08-24 | Liquid | 3 ppm | ~75 mls
300 A | 280.58 A | Kern River Intake Header | 2000-08-30 | Liquid | 4 ppm | ~100 mls.
300 A | 280.58 A | Kern River Intake Header | 2000-09-07 | Liquid | 2 ppm | ~125 mls
300 A | 280.58 A | Kern River Intake Header | 2000-09-14 | Liquid | 3 ppm | ~125 mls
300 A | 280.58 A | Kern River Intake Header | 2000-09-20 | Liquid | 2 ppm | ~100 mls.
300 A | 280.58 A | Kern River Intake Header | 2000-09-28 | Liquid | 2 ppm | ~80 mls.
300 A | 280.58 A | Kern River Intake Header | 2000-10-05 | Liquid | 2 ppm | ~125 mls
300 A | 280.58 A | Kern River Discharge Header | 2000-04-06 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Discharge Header | 2000-05-04 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Discharge Header | 2000-05-17 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Discharge Header | 2000-08-10 | None |  | Dry
300 A | 280.58 A | Kern River Discharge Header | 2000-08-24 | None |  | Dry
300 A | 280.58 A | Kern River Discharge Header | 2000-09-20 | None |  | Dry
300 A | 280.58 A | Kern River Discharge Header | 2000-09-28 | None |  | Dry
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-02-16 | Liquid | < 1 ppm
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-03-22 | Liquid | < 1 ppm
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-04-06 | Liquid | 3 ppm
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-04-12 | Liquid | 4 ppm
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-04-19 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-04-26 | Liquid | 1 ppm
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-05-04 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-05-10 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-05-17 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-05-26 | Liquid | 1 ppm
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-05-31 | Liquid | 1 ppm
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-06-07 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-06-14 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-06-21 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-06-29 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-07-07 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-07-19 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-07-27 | Liquid | 3 ppm
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-08-01 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-08-10 | Liquid | 3 ppm | 90 mls (one run in service part of the week)
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-08-16 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-08-24 | Liquid | 3 ppm | ~75 mls
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-08-30 | Liquid | 2 ppm | ~75 mls
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-09-07 | Liquid | 2 ppm | ~ 80 mls
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-09-14 | Liquid | 3 ppm | ~125 mls
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-09-20 | Liquid | 2 ppm | ~100 mls.
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-09-28 | Liquid | 2 ppm | ~70 mls.
300 A | 280.58 A | Kern River Tap Valve 1 | 2000-10-05 | Liquid | 2 ppm | ~60 mls.
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-02-16 | Liquid | ND <1 ppm
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-03-22 | Liquid | <1 ppm
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-06-30 | Liquid | 15 ppm
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-04-06 | Liquid | 1 ppm
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-04-12 | Liquid | 4 ppm
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-04-26 | Liquid | 1 ppm
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-05-04 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-05-10 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-05-17 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-05-31 | Liquid | 1 ppm
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-06-07 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-06-14 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-06-29 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-07-07 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-07-19 | Liquid | 2 ppm
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-07-27 | Liquid | 3 ppm
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-08-01 | Liquid | 1 ppm
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-08-10 | Liquid | 2 ppm | 75 mls (one run in service part of the week)
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-08-16 | Liquid | 3 ppm
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-08-24 | Liquid | 2 ppm | ~35 mls
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-08-30 | Liquid | 3 ppm | ~30 mls
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-09-07 | Liquid | 2 ppm | ~ 80 mls
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-09-14 | Liquid | 2 ppm | ~100 mls
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-09-20 | Liquid | 2 ppm | ~100 mls
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-09-28 | Liquid | 2 ppm | ~25 mls
300 A | 280.58 A | Kern River Tap Valve 2 | 2000-10-05 | Liquid | 2 ppm | ~20 mls
300 A | 284.69 A | Bakersfield Tap, L-142N |  | None |  | Tap not inspected or sampled
300 A | 285.36 A | Superior Road Tap | 2000-02-17 | Liquid | ND < 1 ppm
300 A | 285.36 A | Superior Road Tap | 2000-03-22 | Liquid | ND < 1 ppm
300 A | 288.98 A | M.L. Sheffield |  | None |  | Tap not inspected or sampled
300 A | 300.53 A | M. Riccomini |  | None |  | Tap not inspected or sampled
300 A | 308.26 A | Semitropic Water District |  | None |  | Tap not inspected or sampled
300 A | 323.36 A | Shell Midway Pump Station | 2000-02-17 | None |  | No liquid in filter
300 A | 344.52 A | Watson Realty Co. |  | None |  | Tap not inspected or sampled
300 A | 344.76 A | Watson Realty Co. |  | None |  | Tap not inspected or sampled
300 A | 345.71 A | Shell Kettleman Pump Station |  | None |  | Tap not inspected or sampled
300 A | 352.61 A | S.C. Gas |  | None |  | Tap not inspected or sampled
300 A | 364.11 A | Line 190 |  | None |  | Tap not inspected or sampled
300 A | 368.92 A | Harris Ranch Development |  | None |  | Tap not inspected or sampled
300 A | 371.81 A | Line 164 |  | None |  | Tap not inspected or sampled
300 A | 371.81 A | Line 164 | 2000-06-30 | None | 9 ppm
300 A | 371.85 A | Coalinga |  | None |  | Tap not inspected or sampled
300 A | 372.44 A | Harris Feed Lot |  | None |  | Tap not inspected or sampled
300 A | 373.68 A | Harris Farms |  | None |  | Tap not inspected or sampled
300 A | 378.65 A | Helm Tap Line 138 |  | None |  | Tap not inspected or sampled
300 A | 393.53 A | Panoche Junction |  | None |  | Tap not inspected or sampled
300 A | Comp Plt. | Plant Fuel |  | None |  | Tap not inspected or sampled
300 B | 231.27 B | Monolith Cement Plant, So. Cal Gas |  | None |  | Line not flowing gas. Tap not inspected or sampled.
300 B | 244.00 B | Bear Valley Springs |  | None |  | Tap not inspected or sampled
300 B | 245.69 B | Bear Valley Springs | 2000-03-02 | Liquid | 1 ppm | San Juan and Martindale
300 B | 245.69 B | Bear Valley Springs | 2000-04-20 | Liquid | 1 ppm | San Juan and Martindale
300 B | 245.69 B | Bear Valley Springs | 2000-06-02 | None |  | San Juan and Martindale
300 B | 245.69 B | Bear Valley Springs | 2000-06-15 | None |  | San Juan and Martindale
300 B | 245.69 B | Bear Valley Springs | 2000-06-29 | None |  | San Juan and Martindale
300 B | 245.69 B | Bear Valley Springs | 2000-07-23 | None |  | San Juan and Martindale
300 B | 245.69 B | Bear Valley Springs | 2000-08-10 | None |  | San Juan and Martindale
300 B | 245.69 B | Bear Valley Springs | 2000-09-08 | None |  | San Juan and Martindale
300 B | 245.69 B | Bear Valley Springs | 2000-10-05 | None |  | San Juan and Martindale
300 B | 245.91 B | Bear Valley Springs | 2000-06-30 | None
300 B | 247.18 B | Bear Valley Springs | 2000-09-08 | None |  | Tap not inspected or sampled
300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-02-17 | Liquid | ND < 25 | First sample filter was dry; second sample filter was dry. Watery sample was obtained from Camron Valve body. Sample reporting limit was raised to low surrogate spike QC recovery caused by low sample volume.
300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-03-22 | Liquid | ND < 1ppm
300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-02-17 | Wipe | ND < 1 ug | Drip located in sub-surface vault box. Small amount of liquid / sludge was obtained.
300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-06-21 | Liquid | 2 ppm
300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-07-23 | None |  | Dry
300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-08-10 | None |  | Dry
300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-10-05 | None |  | Dry
300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-06-29 | None |  | Dry
300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-07-23 | None |  | Dry
300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-08-10 | None |  | Dry
300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-09-08 | None |  | Dry
300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-10-05 | None |  | Dry
300 B | 257.52 B | Kenmore Road |  | None |  | Tap not inspected or sampled
300 B | 268.05 B | Costerian Farms |  | None |  | Tap not inspected or sampled
300 B | 269.45 B | Union Ave. Tap |  | None
300 B | 270.50 B | Beechor Cattle and Feed |  | None |  | Tap not inspected or sampled
300 B | 271.31 B | S.C. Gas |  | None |  | Tap not inspected or sampled
300 B | 273.06 B | Stine Rd. | 2000-02-17 | None |  | No liquid in filter
300 A | 273.06 B | Stine Rd. | 2000-06-30 | None
300 B | 273.06 B | Rudnick Cattle Co. |  | None |  | Tap not inspected or sampled
300 B | 273.06 B | Rudnick Cattle Co. | 2000-08-21 | None | 1 ppm
300 B | 273.50 B | Ridgeview High School Drip | 2000-02-17 | Liquid | < 1 ppm | Small amount of liquid and sludge obtained (~< 5 mls)
300 B | 273.50 B | Ridgeview High School Drip | 2000-03-08 | Liquid | 1 ppm
300 B | 273.50 B | Ridgeview High School Drip | 2000-04-06 | Liquid | 1 ppm
300 B | 273.50 B | Ridgeview High School Drip | 2000-04-19 | Liquid | 1 ppm
300 B | 273.50 B | Ridgeview High School Drip | 2000-05-10 | Liquid | 2 ppm
300 B | 273.50 B | Ridgeview High School Drip | 2000-05-26 | Liquid | 1 ppm
300 B | 273.50 B | Ridgeview High School Drip | 2000-06-07 | Liquid | <1 ppm
300 B | 273.50 B | Ridgeview High School Drip | 2000-07-20 | Liquid | 2 ppm
300 B | 273.50 B | Ridgeview High School Drip | 2000-07-27 | Liquid | 2 ppm
300 B | 273.50 B | Ridgeview High School Drip | 2000-08-01 | Liquid | 2 ppm
300 B | 273.50 B | Ridgeview High School Drip | 2000-08-10 | Liquid | 2 ppm | 50 mls.
300 B | 273.50 B | Ridgeview High School Drip | 2000-08-16 | Liquid | 2 ppm
300 B | 273.50 B | Ridgeview High School Drip | 2000-08-24 | Liquid | 2 ppm | ~ 30 mls
300 B | 273.50 B | Ridgeview High School Drip | 2000-08-30 | Liquid | 2 ppm | ~ 75 mls
300 B | 273.50 B | Ridgeview High School Drip | 2000-09-07 | Liquid | 2 ppm | ~10 mls
300 B | 273.50 B | Ridgeview High School Drip | 2000-09-14 | Liquid | 2 ppm | <10 mls
300 B | 273.50 B | Ridgeview High School Drip | 2000-09-20 | None |  | < 10 mls (Dry)
300 B | 273.50 B | Ridgeview High School Drip | 2000-09-28 | Liquid | 2 ppm | < 10 mls (Dry)
300 B | 273.50 B | Ridgeview High School Drip | 2000-10-05 | Liquid | 1 ppm | < 10 mls (Dry)
300 B | 274.00 B | Line 300 B Drip | 2000-03-22 | Liquid | 1 ppm
300 B | 274.00 B | Line 300 B Drip | 2000-05-31 | Liquid | 1 ppm
300 B | 274.00 B | Line 300 B Drip | 2000-06-30 | Liquid | 1 ppm
300 B | 275.86 B | Gosford Road, D/S reg. | 2000-02-16 | Liquid | ND < 12 | Reporting limit raised due to interfering matrix
300 B | 275.86 B | Gosford Road North Filter Outlet | 2000-02-16 | Liquid | ND < 2 ppm | Line 142 South, small amount of liquid taken downstream of regulator
300 B | 275.86 B | Gosford Road North Filter Outlet | 2000-07-23 | None |  | Dry
300 B | 275.86 B | Gosford Road North Filter Outlet | 2000-08-10 | None |  | Dry
300 B | 275.86 B | Gosford Road North Filter Outlet | 2000-08-21 | None |  | Dry
300 B | 275.86 B | Gosford Road North Filter Outlet | 2000-09-08 | None |  | Dry
300 B | 275.86 B | Gosford Road North Filter Outlet | 2000-09-21 | Liquid | 4 ppm | ~10 mls
300 B | 275.86 B | Gosford Road North Filter Outlet | 2000-10-05 | None |  | Dry
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-02-16 | Liquid | ND < 1 ppm | Liquid obtained from Outlet Valve V-1 drain, Run M-1
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-04-06 | Liquid | 6 ppm
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-04-20 | Liquid | 3 ppm
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-06-30 | Liquid | 3 ppm
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-05-04 | Liquid | 2 ppm
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-06-02 | Liquid | 3 ppm
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-06-15 | Liquid | 4 ppm
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-06-29 | None
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-07-23 | Liquid | 6 ppm
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-07-27 | Liquid | 7 ppm
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-08-10 | Liquid | 8 ppm | ~ 50 mls
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-08-24 | Liquid | 4 ppm | ~ 25 mls
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-04-06 | Liquid | 2 ppm
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-04-06 | Liquid | < 1 ppm
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-05-04 | Liquid | 2 ppm
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-05-18 | Liquid | 2 ppm
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-06-02 | Liquid | 3 ppm
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-06-15 | Liquid | 2 ppm
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-06-29 | None
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-07-13 | Liquid | 2 ppm
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-08-10 | Liquid | 3 ppm | < 10 mls (bottom of filter was wet)
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-08-24 | Liquid | 4 ppm | ~25 mls
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-09-08 | Liquid | 2 ppm | ~50 -75 mls
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-09-21 | Liquid | 4 ppm | ~25 mls
300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-10-05 | Liquid | 2 ppm | ~25 mls
300 B | 275.87 B | Gosford Reg Station | 2000-03-15 | Liquid | 2 ppm
300 B | 278.31 B | S.C. Gas |  | None |  | Tap not inspected or sampled
300 B | 278.31 B | S.C. Gas | 2000-06-30 | None |  | Tap not inspected or sampled
300 B | 280.69 B | Kern Bellview Well |  | None |  | Tap not inspected or sampled - tap is retired
300 B | 284.62 B | Bakersfield Tap, L-142N | 2000-02-17 | None |  | No suitable location to sample (Jr. fittings on orifice plates)
300 B | 288.42 B | Buttonwillow Intertie - SoCal Gas | 2000-02-17 | None |  | Reg. filter was dry
300 B | 295.02 B | Getty Oil | 2000-02-17 | None |  | Tap not inspected or sampled
300 B | 305.94 B | Mettler Semi-Tropic Farm |  | None |  | Tap not inspected or sampled (may be capped?)
300 B | 306.34 B | (Falcon Well #1) L-300B |  | None |  | Tap not inspected or sampled (may be capped)
300 B | 308.67 B | Semitropic school | 2000-02-17 | None |  | Reg. Filter was dry
300 B | 309.63 B | Hartley Natural Resources |  | None |  | Tap not inspected or sampled
300 B | 344.78 B | Westlake #1 |  | None |  | Tap not inspected or sampled
300 B | 345.02 B | Tulare Lake |  | None |  | Husky Oil - Tap not inspected or sampled
300 B | 345.95 B | Kettlemen City |  | None |  | Tap not inspected or sampled
300 B | 347.01 B | Couture Farms |  | None |  | Tap is capped
300 B | 353.0 B | Kettlemen Compressor Station Intake | 2000-04-04 | Liquid | < 1ppm
300 B | 353.0 B | Kettlemen Compressor Station Intake | 2000-06-01 | Liquid | < 1ppm
300 B | 353.0 B | Kettlemen Compressor Station C Bank Scrubber | 2000-04-20 | Liquid | < 1ppm
300 B | 353.0 B | Kettlemen Compressor Station C Bank Scrubber | 2000-06-27 | Liquid | < 1ppm
300 B | 353.80 B | Calorimeter & Domestic Cust. Kettlemen |  | None |  | Tap not inspected or sampled
300 B | 355.15 B | Kochergen Farms |  | None |  | Capped on an emergency basis
300 B | 358.90 B | Line 300 B Drip | 2000-05-10 | Liquid | 1 ppm
300 B | 362.73 B | City of Huron |  | None |  | Tap not inspected or sampled
300 B | 363.89 B | Line 190 |  | None |  | Tap not inspected or sampled
300 A | 367.62 B | Giffen Farms |  | None |  | Tap not inspected or sampled
300 A | 367.62 B | Giffen Farms | 2000-08-07 | None |  | Tap not inspected or sampled
300 A | 367.62 B | Giffen Farms | 2000-08-21 | None |  | Tap not inspected or sampled
300 B | 372.72 B | Harris Feeding Co. |  | None |  | Tap not inspected or sampled
300 B | 372.72 B | Harris Feeding Co. |  | None |  | Tap not inspected or sampled
300 B | 373.49 B | Harris Feeding Co. |  | None |  | Tap not inspected or sampled
300 B | 373.49 B | Harris Feeding Co. |  | None |  | Tap not inspected or sampled
300 B | 376.01 B | Harris Ranch |  | None |  | Tap not inspected or sampled
300 B | 378.78 B | Helm Tap Line 138 |  | None |  | Tap not inspected or sampled
300 B | 385.40 B | Getty Oil and Three Rocks |  | None |  | Tap not inspected or sampled
300 B | 393.76 B | Panoche Junction |  | None |  | Tap not inspected or sampled
300 B |  | Coalinga Line 164 |  | None |  | Tap not inspected or sampled
Sample tap available from bottom of filter - No liquids were found.(Resample)
300 B
|  |  | 2000-08-18 |  | 9 ppm
2000-03-23
2000-08-18
2000-04-04
|  |  | 2000-08-21 |  | 2 ppm
2000-06-30
|  |  | 2000-06-30 |  | 1 ppm
2000-08-21
Ridgecrest West End Primary
|  |  | 2000-04-06 |  | 9 ppm
2000-06-30
|  |  | 2000-08-07 |  | 4 ppm | 10 mls
|  |  | 2000-08-22 |  | 3 ppm
|  |  | 2000-04-05 |  | 3 ppm as Aroclor 1016, 3ppm as Aroclor 1254
38.57
|  |  | 2000-05-16 |  | 4 ppm as Aroclor 1016, 12 ppm as Aroclor 1254
| 54.88 |  |  |  | 0.2 ppm as Aroclor 1016, 0.8 ppm, as Aroclor 1254 | Sample from Filter
54.88
| 54.88 |  | 2000-04-05 | Wipe
54.88
54.88
54.88
| 54.88 |  | 2000-05-15 |  | 2 ppm as Aroclor 1016, 4 ppm as Aroclor 1254
54.88
54.88
54.88
54.88
54.88
54.88
54.88
54.88
54.88
54.88
54.88
| 54.88 |  | 08//08/00 |  | 29 ppm as Aroclor 1016, 27 ppm as Aroclor 1254 | <10 mls
|  |  | 2000-05-15 |  | 25 ppm, 4 ppm as Aroclor 1254
|  |  | 2000-05-15 |  | 5 ppm, 2 ppm as Aroclor 1254 | Bottom inside Meter
|  |  | 2000-08-08 |  | 8 ppm as Aroclor 1016, 19 ppm as Aroclor 1254
|  |  | 2000-08-21 |  | 8 ppm as Aroclor 1016, 27 ppm as Aroclor 1254
16 ppm as Aroclor 1016, 7 ppm as Aroclor 1260
8 ppm as Aroclor 1016, 7 ppm as Aroclor 1260
Feeds Oro Grande Township
9 ppm as Aroclor 1016, 2 ppm as Aroclor 1254
|  |  | 2000-05-15 | Solid | < 1 ppm | Dust from Filter
2000-06-13
|  |  | 2000-08-08 | None |  | Meter set dry
|  |  | 2000-08-21 | Liquid | ND < 1 ppm
|  |  | 2000-08-08 |  | 40 ppm, 12 ppm as Aroclor 1254
|  |  | 2000-08-21 |  | 25 ppm, 14 ppm as Aroclor 1254
Filter was dry
|  |  | 2000-08-21 |  | 16 ppm
|  |  | 2000-06-29 |  | 10 ppm
314 X
314 X |  |  | 2000-08-18 |  | 16 ppm as Aroclor 1016, 2 ppm as Aroclor 1260
314 X |  |  | 2000-06-29 |  | 16 ppm as Aroclor 1016, 3 ppm as Aroclor 1254
2000-08-21

## MOJAVE Filter Separator
LINE | Mile Point | Description | Sample Date | Sample Type | Result (All results as Aroclor 1016 unless otherwise noted) | Comments
300 A | 218.69 A | F/S C-1 A Inlet | 2000-07-26 | Liquid | 1.5 ppm as Aroclor 1016, 0.4 ppm as Aroclor 1260 | F/S sump1/2 full
300 A | 218.69 A | F/S C-1 A Inlet | 2000-08-16 | Liquid | 2 ppm
300 A | 218.69 A | F/S C-1 A Inlet | 2000-09-06 | Liquid | 2 ppm
300 A | 218.69 A | F/S C-1 A Inlet | 2000-10-02 | Liquid | 3 ppm
300 A | 218.69 A | F/S C-1 A Inlet | 2000-09-18 | Liquid | 2 ppm
300 A | 218.69 A | F/S C-1 B Outlet | 2000-07-26 | Liquid | 2 ppm | F/S sump1/2 full
300 A | 218.69 A | F/S C-1 B Outlet | 2000-08-16 | Liquid | 2 ppm
300 A | 218.69 A | F/S C-1 B Outlet | 2000-09-06 | Liquid | 2 ppm
300 A | 218.69 A | F/S C-1 B Outlet | 2000-09-18 | Liquid | 2 ppm
300 A | 218.69 A | F/S C-1 B Outlet | 2000-10-02 | Liquid | 3 ppm
300 A | 218.69 A | F/S C-2 A Inlet | 2000-07-26 | Liquid | 2 ppm | F/S sump full
300 A | 218.69 A | F/S C-2 A Inlet | 2000-08-16 | Liquid | 2 ppm
300 A | 218.69 A | F/S C-2 A Inlet | 2000-09-06 | Liquid | 3 ppm
300 A | 218.69 A | F/S C-2 A Inlet | 2000-09-18 | Liquid | 2 ppm
300 A | 218.69 A | F/S C-2 A Inlet | 2000-10-02 | Liquid | 2 ppm
300 A | 218.69 A | F/S C-2 B Outlet | 2000-07-26 | Liquid | 3 ppm | F/S sump 1/2 full
300 A | 218.69 A | F/S C-2 B Outlet | 2000-08-16 | Liquid | 2 ppm
300 A | 218.69 A | F/S C-2 B Outlet | 2000-09-06 | Liquid | 3 ppm
300 A | 218.69 A | F/S C-2 B Outlet | 2000-09-18 | Liquid | 3 ppm
300 A | 218.69 A | F/S C-2 B Outlet | 2000-10-02 | Liquid | 2 ppm
300 B | 219.49 B | F/S C-3 A Inlet | 2000-07-26 | Liquid | 2 ppm | F/S sump full
300 B | 219.49 B | F/S C-3 A Inlet | 2000-08-16 | Liquid | 2 ppm
300 B | 219.49 B | F/S C-3 A Inlet | 2000-09-06 | Liquid | 3 ppm
300 B | 219.49 B | F/S C-3 A Inlet | 2000-09-18 | Liquid | 2 ppm
300 B | 219.49 B | F/S C-3 A Inlet | 2000-10-03 | Liquid | 2 ppm
300 B | 219.49 B | F/S C-3 B Outlet | 2000-07-26 | Liquid | 1 ppm | F/S sump full
300 B | 219.49 B | F/S C-3 B Outlet | 2000-08-16 | Liquid | 1 ppm
300 B | 219.49 B | F/S C-3 B Outlet | 2000-09-06 | Liquid | 2 ppm
300 B | 219.49 B | F/S C-3 B Outlet | 2000-09-18 | Liquid | 2 ppm
300 B | 219.49 B | F/S C-3 B Outlet | 2000-10-02 | Liquid | 2 ppm
300 B | 219.49 B | F/S C-4 A Inlet | 2000-07-26 | Liquid | 1 ppm | F/S sump full
300 B | 219.49 B | F/S C-4 A Inlet | 2000-08-16 | Liquid | 1 ppm
300 B | 219.49 B | F/S C-4 A Inlet | 2000-09-06 | Liquid | 2 ppm
300 B | 219.49 B | F/S C-4 A Inlet | 2000-09-18 | Liquid | 1 ppm
300 B | 219.49 B | F/S C-4 A Inlet | 2000-10-02 | Liquid | 2 ppm
300 B | 219.49 B | F/S C-4 B Outlet | 2000-07-26 | Liquid | ND <1 ppm | F/S sump 1/2 full
300 B | 219.49 B | F/S C-4 B Outlet | 2000-08-16 | Liquid | 2 ppm
300 B | 219.49 B | F/S C-4 B Outlet | 2000-09-06 | Liquid | 2 ppm
300 B | 219.49 B | F/S C-4 B Outlet | 2000-09-18 | Liquid | 2 ppm
300 B | 219.49 B | F/S C-4 B Outlet | 2000-10-02 | Liquid | 1 ppm
300 A/B |  | F/S Waste Tank | 2000-07-26 | Liquid | 2 ppm | All liquids from F/S sumps transferred to waste tank after sampling Tank ~ 1/3 full
.
Filter was dry