## Hinkley District, 2000
Sample Point Code | LINE | Mile Point | Description | Sample Date | Sample Type | Result (All results as Aroclor 1016 unless otherwise noted) | Comments
| 300 A | 116.48 A | Pisgah |  | None |  | Tap not inspected or sampled
| 300 A | 130.37 A | PLS 2XA Insertion Meter | 2000-02-16 | Wipe | ND <0.7 ug/100cm2
| 300 A | 131.94 A | Newberry Springs Community Tap | 2000-02-09 | Wipe | ND <1ug/wipe | Removed primary regulator; opened it and obtained wipe sample - non quantitative
| 300 A | 134.00 A | Southwest Gas (Martino) |  | None |  | Tap not inspected or sampled
| 300 A | 135.98 A | Southwest Gas (Masimini) |  | None |  | Tap not inspected or sampled
| 300 A | 137.00 A | Southwest Gas |  | None |  | Tap not inspected or sampled
| 300 A | 137.50 A | Southwest Gas |  | None |  | Tap not inspected or sampled
| 300 A | 141.03 A | Lucerne Valley - Main #313 XA | 2000-02-11 | None |  | Sample taps located immediately upstream and downstream of orifice plate. Both taps were dry.
| 300 A | 141.03 A | Lucerne Valley - Main #313 XA | 2001-06-25 | Liquid | 24 ppm as Aroclor 1242 | 20 mls
H13 | 300 A | 147.91 A | Barstow B Meter | 2000-02-11 | Liquid | 11 ppm
H13 | 300 A | 147.91 A | Barstow B Meter | 2000-02-28 | Liquid |  | Insufficient Sample
H13 | 300 A | 147.91 A | Barstow B Meter | 2000-03-10 | Liquid | 16 ppm
H13 | 300 A | 147.91 A | Barstow B Meter | 2000-03-21 | Liquid | 13 ppm
H13 | 300 A | 147.91 A | Barstow B Meter | 2000-04-05 | Liquid | 18 ppm
H13 | 300 A | 147.91 A | Barstow B Meter | 2000-04-19 | Liquid | 10 ppm
H13 | 300 A | 147.91 A | Barstow B Meter | 2000-05-01 | Liquid | 11 ppm
H13 | 300 A | 147.91 A | Barstow B Meter | 2000-05-14 | Liquid | 18 ppm
H13 | 300 A | 147.91 A | Barstow B Meter | 2000-05-30 | Liquid | 11 ppm
H13 | 300 A | 147.91 A | Barstow B Meter | 2000-06-14 | Liquid | 24 ppm
H13 | 300 A | 147.91 A | Barstow B Meter | 2000-06-30 | Liquid | 25 ppm
H13 | 300 A | 147.91 A | Barstow B Meter | 2000-07-29 | Liquid | 8 ppm
H13 | 300 A | 147.91 A | Barstow B Meter | 2000-08-18 | Liquid | 10 ppm
H13 | 300 A | 147.91 A | Barstow B Meter | 2000-09-05 | Liquid | 14 ppm | <10 mls
H13 | 300 A | 147.91 A | Barstow B Meter | 2000-09-19 | Liquid | 15 ppm | <10 mls (trace)
H13 | 300 A | 147.91 A | Barstow B Meter | 2000-12-18 | Liquid | 18 ppm | ~10 mls (trace)
H13 | 300 A | 147.91 A | Barstow B Meter | 2001-02-22 | Liquid | 27 ppm | <10 mls
H13 | 300 A | 147.91 A | Barstow B Meter | 2001-03-14 | Liquid | 13 ppm | ~15 mls
H13 | 300 A | 147.91 A | Barstow B Meter | 2001-04-25 | Liquid | 20 ppm | ~20 mls
H13 | 300 A | 147.91 A | Barstow B Meter | 2001-05-25 | Liquid | 25 ppm | ~20 mls
H13 | 300 A | 147.91 A | Barstow B Meter | 2001-06-25 | Liquid | 8 ppm as Aroclor 1242 | ~20 mls
H13 | 300 A | 147.91 A | Barstow B Meter | 2001-07-09 | Liquid | 14ppm as Aroclor 1242 | ~10 mls
H13 | 300 A | 147.91 A | Barstow B Meter | 2001-08-27 | Liquid | 3 ppm as Aroclor 1242 | ~15 mls
H13 | 300 A | 147.91 A | Barstow B Meter | 2001-10-22 | Liquid |  | < 10 mls (insufficient sample)
H11 | 300 A | 151.05 A | Barstow "A" Filter | 2000-02-17 | Liquid | 6 ppm
H11 | 300 A | 151.05 A | Barstow "A" Filter | 2000-02-28 | Liquid | 13 ppm
H11 | 300 A | 151.06 A | Barstow "A" Filter | 2000-03-10 | Liquid | 15 ppm
H11 | 300 A | 151.06 A | Barstow "A" Filter | 2000-03-21 | Liquid | 15 ppm
H11 | 300 A | 151.06 A | Barstow "A" Filter | 2000-04-05 | Liquid | 22 ppm
H11 | 300 A | 151.06 A | Barstow "A" Filter | 2000-04-18 | Liquid | 11 ppm
H11 | 300 A | 151.06 A | Barstow "A" Filter | 2000-05-01 | Liquid | 7 ppm
H11 | 300 A | 151.06 A | Barstow "A" Filter | 2000-05-14 | Liquid | 26 ppm
H11 | 300 A | 151.06 A | Barstow "A" Filter | 2000-05-30 | Liquid | 10 ppm
H11 | 300 A | 151.06 A | Barstow "A" Filter | 2000-06-14 | Liquid | 18 ppm
H11 | 300 A | 151.06 A | Barstow "A" Filter | 2000-11-20 | Liquid | 23 ppm | ~ 45 mls
H11 | 300 A | 151.06 A | Barstow "A" Filter | 2000-12-18 | Liquid | 18 ppm | ~ 260 mls
H11 | 300 A | 151.06 A | Barstow "A" Filter | 2001-02-22 | Liquid | 28 ppm | ~ 40 mls
H11 | 300 A | 151.06 A | Barstow "A" Filter | 2001-03-14 | Liquid | 23 ppm | ~ 20 mls
H11 | 300 A | 151.06 A | Barstow "A" Filter | 2001-04-24 | Liquid | 18 ppm | ~ 30 mls
H11 | 300 A | 151.06 A | Barstow "A" Filter | 2001-05-25 | Liquid | 24 ppm | ~ 40 mls
H11 | 300 A | 151.06 A | Barstow "A" Filter | 2001-06-26 | Liquid | 26 ppm | ~ 70 mls
H11 | 300 A | 151.06 A | Barstow "A" Filter | 2001-07-09 | Liquid | 24 ppm | ~ 20 mls
H11 | 300 A | 151.06 A | Barstow "A" Filter | 2001-08-27 | Liquid | 18 ppm | ~ 75 mls
H11 | 300 A | 151.06 A | Barstow "A" Filter | 2001-09-25 | Liquid | 43 ppm | ~ 60 mls
H11 | 300 A | 151.06 A | Barstow "A" Filter | 2001-10-22 | Liquid | 36 ppm | ~ 20 mls
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-02-17 | Liquid | 9 ppm
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-02-28 | Liquid | 20 ppm
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-03-10 | Liquid | 16 ppm
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-03-21 | Liquid | 15 ppm
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-04-05 | Liquid | 18 ppm
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-04-18 | Liquid | 8 ppm
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-05-01 | Liquid | 17 ppm
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-05-14 | Liquid | 33 ppm
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-05-30 | Liquid | 5 ppm
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-06-14 | Liquid | 17 ppm
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-06-30 | Liquid | 15 ppm
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-07-29 | Liquid | 16 ppm
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-08-10 | Liquid | 1 ppm
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-08-16 | Liquid | 2 ppm
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-08-18 | Liquid | 9 ppm
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-08-24 | Liquid | 3 ppm
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-08-30 | Liquid | 4 ppm
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-09-05 | Liquid | 15 ppm | < 10 mls
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-09-19 | Liquid | 14 ppm | ~ 20 mls
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-10-02 | Liquid | 13 ppm | ~ 20 mls
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-10-16 | Liquid | 13 ppm | ~ 20 mls
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-10-26 | Liquid | 8 ppm | ~ 5 mls
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-11-20 | Liquid | 15 ppm | ~ 25 mls
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2000-12-18 | Liquid | 14 ppm | ~ 25 mls
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2001-01-23 | Liquid | 20 ppm as Aroclor 1242 | ~ 30 mls
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2001-02-22 | Liquid | 58 ppm as Aroclor 1242 | ~ 40 mls
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2001-03-14 | Liquid | 30 ppm as Aroclor 1242 | ~ 40 mls
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2001-04-24 | Liquid | 31 ppm as Aroclor 1242 | ~ 30 mls
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2001-05-25 | Liquid | 26 ppm as Aroclor 1242 | ~ 20 mls
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2001-06-25 | Liquid | 31 ppm as Aroclor 1242 | ~ 25 mls
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2001-07-09 | Liquid | 14 ppm as Aroclor 1242 | ~ 10 mls
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2001-08-27 | Liquid | 12 ppm as Aroclor 1242 | ~ 30 mls
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2001-10-22 | Liquid | 23 ppm as Aroclor 1242 | < 10 mls (trace)
H12 | 300 A | 151.06 A | Barstow "A" Meter | 2001-09-25 | Liquid | 12 ppm as Aroclor 1242 | ~ 15 mls
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2000-02-18 | Liquid | 38 ppm
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2000-02-28 | Liquid | 39 ppm
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2000-03-10 | Liquid | 34 ppm
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2000-03-21 | Liquid | 45 ppm
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2000-04-05 | Liquid | 29 ppm
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2000-04-18 | Liquid | 27 ppm
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2000-05-01 | Liquid | 28 ppm
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2000-05-14 | Liquid | 33 ppm
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2000-05-25 | Liquid | 19 ppm
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2000-06-14 | Liquid | 33 ppm
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2000-06-30 | Liquid | 22 ppm
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2000-07-29 | None
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2000-09-19 | Liquid | 30 ppm | 20 mls
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2000-10-02 | Liquid | 31 ppm | 20 mls
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2000-10-16 | Liquid | 34 ppm | 20 mls
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2000-10-26 | Liquid | 38 ppm | ~10 mls
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2000-11-20 | Liquid | 44 ppm | ~20 mls
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2000-12-18 | Liquid | 30 ppm as Aroclor 1242 | ~25 mls
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2001-01-23 | Liquid |  | Sample container received broken - no analysis
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2001-02-22 | Liquid | 44 ppm as Aroclor 1242 | ~ 20 mls
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2001-03-14 | Liquid | 40 ppm as Aroclor 1242 | ~ 20 mls
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2001-04-24 | Liquid | 36 ppm as Aroclor 1242 | ~ 20 mls
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2001-05-23 | Liquid | 42 ppm as Aroclor 1242 | ~ 15 mls
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2001-06-25 | Liquid | 47 ppm as Aroclor 1242 | ~ 10 mls
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2001-07-09 | Liquid | 53 ppm | <10 mls
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2001-08-27 | Liquid | 96 ppm | <10 mls
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2001-09-25 | Liquid | 30 | <10 mls (trace)
H14 | 300 A | 154.70 A | Barstow "D" Meter | 2001-10-22 | Liquid |  | <10 mls (insufficient sample)
H15 | 300 A | 154.70 A | Barstow "D" East Filter | 2000-02-11 | Liquid | ND < 1 ppm
H15 | 300 A | 154.70 A | Barstow "D" East Filter | 2000-02-28 | Liquid |  | Insufficient Sample
H15 | 300 A | 154.70 A | Barstow "D" East Filter | 2000-03-21 | Liquid | 0.45
H15 | 300 A | 154.70 A | Barstow "D" East Filter | 2000-04-05 | Liquid | < 1 ppm
H15 | 300 A | 154.70 A | Barstow "D" East Filter | 2000-07-29 | None
H15 | 300 A | 154.70 A | Barstow "D" East Filter | 2000-08-10 | Liquid | 3 ppm
H15 | 300 A | 154.70 A | Barstow "D" East Filter | 2000-08-16 | Liquid | 2 ppm
H15 | 300 A | 154.70 A | Barstow "D" East Filter | 2000-08-24 | Liquid | 3 ppm
H15 | 300 A | 154.70 A | Barstow "D" East Filter | 2000-08-30 | Liquid | 2 ppm
H15 | 300 A | 154.70 A | Barstow "D" East Filter | 2000-09-07 | Liquid | 2 ppm
| 300 A | 159.33 A | Emergency Fuel |  | None |  | Tap not inspected or sampled
| 300 A | 159.33 A | Hinkley, K-11 Crankcase | 2000-05-01 | Liquid | ND < 1 ppm
| 300 A | 159.33 A | Hinkley, K-11 Compressor | 2000-05-01 | Liquid | 6 ppm
|  | 159.33 A | Hinkley Station Fuel Gas Filter | 2001-03-01 | Liquid | 14 ppm | ~30 mls
|  | 159.33 A | Hinkley, K-4 Compressor, # 1 | 2001-03-01 | Liquid | 3 ppm | ~60 mls
H01 | 300 A | 159.33 A | Hinkley Compressor Station 300A Suction Drip, Inlet 211 | 2000-01-27 | Liquid | 4 ppm
H01 | 300 A | 159.33 A | Hinkley Compressor Station 300A Suction Drip, Inlet 211 | 2000-02-10 | Liquid | 3 ppm | Black; liquid obtained. Drip was emptied after sample was obtained Sample tap was plugged and was replaced with metric valve.
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-02-25 | Liquid | 7 ppm
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-03-09 | Liquid | 8 ppm
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-04-06 | Liquid | 7 ppm
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-05-01 | Liquid | 10 ppm
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-05-14 | Liquid | 15 ppm
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-05-14 | Liquid | 15 ppm
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-05-30 | Liquid | 6 ppm
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-06-30 | Liquid | 9 ppm
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-07-29 | Liquid | 9 ppm
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-09-18 | Liquid | 14 ppm | ~ 40 mls
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-10-02 | Liquid | 21 ppm | ~ 40 mls
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-10-27 | Liquid | 19 ppm | ~10 mls
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2000-12-19 | Liquid | 18 ppm as Aroclor 1242 | ~20 mls
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2001-01-23 | Liquid | 16 ppm as Aroclor 1242 | ~20 mls
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2001-02-22 | Liquid | 16 ppm as Aroclor 1242 | ~20 mls
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2001-04-24 | Liquid | 18 ppm as Aroclor 1242 | ~20 mls
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2001-05-25 | Liquid | 18 ppm as Aroclor 1242 | ~30 mls
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2001-06-26 | Liquid | 16 ppm as Aroclor 1242 | ~45 mls
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2001-07-09 | Liquid | 17 ppm as Aroclor 1242 | ~25 mls
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2001-08-27 | Liquid | 14 ppm as Aroclor 1242 | ~40 mls
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2001-09-25 | Liquid | 13 ppm as Aroclor 1242 | ~40 mls
H01 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-211 | 2001-10-18 | Liquid | 5 ppm as Aroclor 1242 | ~45 mls
H02 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2000-05-01 | Liquid | 7 ppm
H02 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2000-08-10 | Liquid | 2 ppm
H02 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2000-08-16 | Liquid | 3 ppm
H02 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2000-08-24 | Liquid | 2 ppm
H02 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2000-08-30 | Liquid | 3 ppm
H02 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2000-09-07 | Liquid | 2 ppm
H02 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2000-10-02 | Liquid | 13 ppm | ~30 mls
H02 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2000-10-16 | Liquid | 19 ppm | ~10 mls
H02 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2000-11-20 | Liquid | 12 ppm | ~20 mls
H02 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2000-12-19 | Liquid | 12 ppm as Aroclor 1242 | ~40 mls
H02 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2001-01-23 | Liquid | 13 ppm as Aroclor 1242 | ~40 mls
H02 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2001-02-22 | Liquid | 14 ppm as Aroclor 1242 | ~20 mls
H02 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2001-03-14 | Liquid | 19 ppm as Aroclor 1242 | ~20 mls
H02 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2001-05-25 | Liquid | 19 ppm as Aroclor 1242 | ~30 mls
H02 | 300 A | 159.33 A | Hinkley Compressor Station A Inlet Drip V-212 | 2001-07-09 | Liquid | 17 ppm as Aroclor 1242 | ~25 mls
| 300 A | 160.00 A | Southwest Gas 3 Customers (Neirmeirer - McCormack) |  | None |  | Tap not inspected or sampled
H05 | 300 A | 161.93 A | A Line Drip | 2000-02-10 | Liquid | <1 ppm
H05 | 300 A | 161.93 A | A Line Drip | 2000-02-24 | Liquid | 2 ppm
H05 | 300 A | 161.93 A | A Line Drip | 2000-03-09 | Liquid | ND < 1 ppm
H05 | 300 A | 161.93 A | A Line Drip | 2000-03-23 | Liquid | ND < 1 ppm
H05 | 300 A | 161.93 A | A Line Drip | 2000-04-06 | Liquid | <1 ppm
H05 | 300 A | 161.93 A | A Line Drip | 2000-04-19 | Liquid | <1 ppm
H05 | 300 A | 161.93 A | A Line Drip | 2000-05-01 | Liquid | <1 ppm
H05 | 300 A | 161.93 A | A Line Drip | 2000-05-14 | Liquid | <1 ppm
H05 | 300 A | 161.93 A | A Line Drip | 2000-06-01 | Liquid | <1 ppm
H05 | 300 A | 161.93 A | A Line Drip | 2000-06-14 | Liquid | 1 ppm
H05 | 300 A | 161.93 A | A Line Drip | 2000-06-30 | Liquid | <1 ppm
H05 | 300 A | 161.93 A | A Line Drip | 2000-07-23 | None
H05 | 300 A | 161.93 A | A Line Drip | 2000-07-29 | Liquid | 1.7 ppm as Aroclor 1016, 0.5 ppm as Aroclor 1260
H05 | 300 A | 161.93 A | A Line Drip | 2000-09-06 | Liquid | 1 ppm | ~40 mls
H05 | 300 A | 161.93 A | A Line Drip | 2000-09-18 | Liquid | 2 ppm | ~20 mls
H05 | 300 A | 161.93 A | A Line Drip | 2000-10-03 | Liquid | 2 ppm | ~10 mls
H05 | 300 A | 161.93 A | A Line Drip | 2000-10-16 | Liquid | 2 ppm | <10 mls
H05 | 300 A | 161.93 A | A Line Drip | 2000-10-27 | Liquid | 3 ppm | ~10 mls
H05 | 300 A | 161.93 A | A Line Drip | 2000-11-21 | Liquid | 3 ppm | <10 mls (sample contr. recv'd. broken)
H05 | 300 A | 161.93 A | A Line Drip | 2000-12-19 | Liquid | 3 ppm as Aroclor 1242 | ~20 mls
H05 | 300 A | 161.93 A | A Line Drip | 2001-01-23 | Liquid | 3 ppm as Aroclor 1242 | ~20 mls
H05 | 300 A | 161.93 A | A Line Drip | 2001-02-22 | Liquid | 3 ppm as Aroclor 1242 | ~20 mls
H05 | 300 A | 161.93 A | A Line Drip | 2001-03-14 | Liquid | 3 ppm as Aroclor 1242 | ~30 mls
H05 | 300 A | 161.93 A | A Line Drip | 2001-04-25 | Liquid | 2 ppm as Aroclor 1242 | ~20 mls
H05 | 300 A | 161.93 A | A Line Drip | 2001-05-25 | Liquid | 1 ppm as Aroclor 1242 | ~25 mls
H05 | 300 A | 161.93 A | A Line Drip | 2001-06-26 | Liquid | 2 ppm as Aroclor 1242 | ~25 mls
H05 | 300 A | 161.93 A | A Line Drip | 2001-07-09 | Liquid | 3 ppm as Aroclor 1242 | ~25 mls
H05 | 300 A | 161.93 A | A Line Drip | 2001-08-27 | Liquid | 2 ppm as Aroclor 1242 | ~25 mls
H05 | 300 A | 161.93 A | A Line Drip | 2001-09-24 | Liquid | 1 ppm as Aroclor 1242 | ~25 mls
H05 | 300 A | 161.93 A | A Line Drip | 2001-10-17 | Liquid | 2 ppm as Aroclor 1242 | ~40 mls
H06 | 300 A | 164.71 A | A Line Drip | 2000-02-10 | Liquid | <1
H06 | 300 A | 164.71 A | A Line Drip | 2000-02-24 | Liquid | 5 ppm
H06 | 300 A | 164.71 A | A Line Drip | 2000-03-09 | Liquid | <1 ppm
H06 | 300 A | 164.71 A | A Line Drip | 2000-03-28 | Liquid | <1 ppm
H06 | 300 A | 164.71 A | A Line Drip | 2000-04-06 | Liquid | <1 ppm
H06 | 300 A | 164.71 A | A Line Drip | 2000-04-19 | Liquid | < 1 ppm
H06 | 300 A | 164.71 A | A Line Drip | 2000-05-14 | Liquid | < 1 ppm
H06 | 300 A | 164.71 A | A Line Drip | 2000-06-01 | Liquid | < 1 ppm
H06 | 300 A | 164.71 A | A Line Drip | 2000-06-15 | Liquid | 1 ppm
H06 | 300 A | 164.71 A | A Line Drip | 2000-06-30 | Liquid | 1 ppm
H06 | 300 A | 164.71 A | A Line Drip | 2000-07-23 | None
H06 | 300 A | 164.71 A | A Line Drip | 2000-07-29 | Liquid | 1 ppm
H06 | 300 A | 164.71 A | A Line Drip | 2000-08-21 | Liquid | 1 ppm
H06 | 300 A | 164.71 A | A Line Drip | 2000-09-06 | Liquid | 1 ppm | ~ 20 mls
H06 | 300 A | 164.71 A | A Line Drip | 2000-09-18 | Liquid | 1 ppm | ~ 40 mls
H06 | 300 A | 164.71 A | A Line Drip | 2000-10-03 | Liquid | 1 ppm | ~ 50 mls
H06 | 300 A | 164.71 A | A Line Drip | 2000-10-16 | Liquid | 1 ppm | ~ 30 mls
H06 | 300 A | 164.71 A | A Line Drip | 2000-10-27 | Liquid | 1 ppm | ~ 20 mls
H06 | 300 A | 164.71 A | A Line Drip | 2000-11-21 | Liquid | 1 ppm | ~ 20 mls
H06 | 300 A | 164.71 A | A Line Drip | 2000-12-19 | Liquid | 2 ppm as Aroclor 1242 | ~ 30 mls
H06 | 300 A | 164.71 A | A Line Drip | 2001-02-22 | Liquid | 3 ppm as Aroclor 1242 | ~ 20 mls
H06 | 300 A | 164.71 A | A Line Drip | 2001-03-14 | Liquid | 3 ppm as Aroclor 1242 | ~ 20 mls
H06 | 300 A | 164.71 A | A Line Drip | 2001-04-26 | Liquid | 2 ppm as Aroclor 1242 | ~ 20 mls
H06 | 300 A | 164.71 A | A Line Drip | 2001-05-25 | Liquid | 1 ppm as Aroclor 1242 | ~ 30 mls
H06 | 300 A | 164.71 A | A Line Drip | 2001-06-26 | Liquid | 2 ppm as Aroclor 1242 | ~ 20 mls
H06 | 300 A | 164.71 A | A Line Drip | 2001-07-09 | Liquid | 4 ppm as Aroclor 1242 | ~ 20 mls
H06 | 300 A | 164.71 A | A Line Drip | 2001-08-27 | Liquid | 1 ppm as Aroclor 1242 | ~ 20 mls
H06 | 300 A | 164.71 A | A Line Drip | 2001-09-24 | Liquid | 1 ppm as Aroclor 1242 | ~ 15 mls
H06 | 300 A | 164.71 A | A Line Drip | 2001-10-17 | Liquid | 3 ppm as Aroclor 1242 | ~ 40 mls
H07 | 300 A | 167.37 A | A Line Drip | 2000-02-10 | Liquid | <1 ppm
H07 | 300 A | 167.37 A | A Line Drip | 2000-02-24 | Liquid | 6 ppm
H07 | 300 A | 167.37 A | A Line Drip | 2000-03-09 | Liquid | <1 ppm
H07 | 300 A | 167.37 A | A Line Drip | 2000-03-23 | Liquid | ND < 1 ppm
H07 | 300 A | 167.37 A | A Line Drip | 2000-04-06 | Liquid | < 1 ppm
H07 | 300 A | 167.37 A | A Line Drip | 2000-04-19 | Liquid | 1 ppm
H07 | 300 A | 167.37 A | A Line Drip | 2000-05-01 | Liquid | < 1 ppm
H07 | 300 A | 167.37 A | A Line Drip | 2000-05-14 | Liquid | < 1 ppm
H07 | 300 A | 167.37 A | A Line Drip | 2000-06-01 | Liquid | < 1 ppm
H07 | 300 A | 167.37 A | A Line Drip | 2000-06-16 | Liquid | < 1 ppm
H07 | 300 A | 167.37 A | A Line Drip | 2000-06-30 | Liquid | 1 ppm
H07 | 300 A | 167.37 A | A Line Drip | 2000-07-29 | Liquid | 1 ppm
H07 | 300 A | 167.37 A | A Line Drip | 2000-08-21 | Liquid | 1 ppm
H07 | 300 A | 167.37 A | A Line Drip | 2000-09-06 | Liquid | 1 ppm | ~20 mls
H07 | 300 A | 167.37 A | A Line Drip | 2000-09-18 | Liquid | 1 ppm | ~20 mls
H07 | 300 A | 167.37 A | A Line Drip | 2000-10-03 | Liquid | 3 ppm | ~50 mls
H07 | 300 A | 167.37 A | A Line Drip | 2000-10-27 | Liquid | 2 ppm | ~20 mls
H07 | 300 A | 167.37 A | A Line Drip | 2000-11-21 | Liquid | 3 ppm | ~20 mls
H07 | 300 A | 167.37 A | A Line Drip | 2001-01-22 | Liquid | 3 ppm as Aroclor 1242 | ~10 mls
H07 | 300 A | 167.37 A | A Line Drip | 2001-02-22 | Liquid | 3 ppm as Aroclor 1242 | ~20 mls
H07 | 300 A | 167.37 A | A Line Drip | 2001-03-14 | Liquid | 2 ppm as Aroclor 1242 | ~20 mls
H07 | 300 A | 167.37 A | A Line Drip | 2001-04-26 | Liquid | 1 ppm as Aroclor 1242 | ~25 mls
H07 | 300 A | 167.37 A | A Line Drip | 2001-05-25 | Liquid | 2 ppm as Aroclor 1242 | ~30 mls
H07 | 300 A | 167.37 A | A Line Drip | 2001-06-26 | Liquid | 3 ppm as Aroclor 1242 | ~25 mls
H07 | 300 A | 167.37 A | A Line Drip | 2001-07-09 | Liquid | 2 ppm as Aroclor 1242 | ~20 mls
H07 | 300 A | 167.37 A | A Line Drip | 2001-08-27 | Liquid | 2 ppm as Aroclor 1242 | ~30 mls
H07 | 300 A | 167.37 A | A Line Drip | 2001-09-24 | Liquid | 1 ppm as Aroclor 1242 | ~20 mls
H07 | 300 A | 167.37 A | A Line Drip | 2001-10-17 | Liquid | 2 ppm as Aroclor 1242 | ~25 mls
H09 | 300 A | 170.61 A | A Line Drip | 2000-04-06 | Liquid | ND < 1ppm
H09 | 300 A | 170.61 A | A Line Drip | 2000-04-19 | Liquid | ND < 1ppm
H09 | 300 A | 170.61 A | A Line Drip | 2000-05-14 | Liquid | ND < 1ppm
H09 | 300 A | 170.61 A | A Line Drip | 2000-06-01 | Liquid | ND < 1ppm
H09 | 300 A | 170.61 A | A Line Drip | 2000-06-15 | Liquid | ND < 1ppm
H09 | 300 A | 170.61 A | A Line Drip | 2000-06-30 | Liquid | ND < 1ppm
H09 | 300 A | 170.61 A | A Line Drip | 2000-07-23 | None
H09 | 300 A | 170.61 A | A Line Drip | 2000-08-21 | Liquid | 1 ppm
H09 | 300 A | 170.61 A | A Line Drip | 2000-09-06 | Liquid | <1 ppm | ~10 mls
H09 | 300 A | 170.61 A | A Line Drip | 2000-09-19 | Liquid | <1 ppm | <10 mls (trace)
H09 | 300 A | 170.61 A | A Line Drip | 2000-10-03 | Liquid | <1 ppm | <10 mls (trace)
H09 | 300 A | 170.61 A | A Line Drip | 2000-10-27 | Liquid | 18 ppm | ~20 mls (trace)
H09 | 300 A | 170.61 A | A Line Drip | 2000-12-19 | Liquid | < 1 ppm | ~20 mls (trace)
H09 | 300 A | 170.61 A | A Line Drip | 2001-01-23 | Liquid | 3 ppm as Aroclor 1242 | ~15 mls
H09 | 300 A | 170.61 A | A Line Drip | 2001-03-14 | Liquid | 1 ppm as Aroclor 1242 | ~15 mls
H09 | 300 A | 170.61 A | A Line Drip | 2001-04-26 | Liquid | < 1 ppm | ~15 mls
H09 | 300 A | 170.61 A | A Line Drip | 2001-05-25 | Liquid | < 1 ppm | < 10 mls
H09 | 300 A | 170.61 A | A Line Drip | 2001-06-21 | Liquid | < 1 ppm | < 10 mls
H09 | 300 A | 170.61 A | A Line Drip | 2001-09-24 | Liquid | ND < 1 ppm | < 10 mls (trace)
H09 | 300 A | 170.61 A | A Line Drip | 2001-10-17 | Liquid | 2 ppm | ~ 50 mls
| 300 A | 170.62 A | Line 300 A Drip at Victorville Tap | 2000-02-10 | None |  | <10 mls (trace)
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-02-10 | Liquid | ND < 1 ppm
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-02-24 | Liquid | 7 ppm
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-03-09 | Liquid | 1 ppm
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-04-06 | Liquid | < 1 ppm
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-04-19 | Liquid | 1 ppm
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-05-14 | Liquid | < 1 ppm
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-06-01 | Liquid | < 1 ppm
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-06-15 | Liquid | 1 ppm
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-06-29 | None | 1 ppm
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-06-30 | Liquid | 1 ppm
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-07-23 | Liquid | 1 ppm
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-07-29 | Liquid | 1 ppm
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-08-10 | Liquid | 2 ppm
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-08-16 | Liquid | 2 ppm
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-08-21 | Liquid | 1 ppm
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-08-24 | Liquid | 2 ppm
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-08-30 | Liquid | 2 ppm
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-09-06 | Liquid | 2 ppm | ~20 mls
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-09-07 | Liquid | 2 ppm
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-09-19 | Liquid | 3 ppm | ~20 mls
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-10-03 | Liquid | 3 ppm | ~50 mls
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-10-16 | Liquid | 2 ppm | ~20 mls
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-11-21 | Liquid | 2 ppm | ~20 mls
H10 | 300 A | 175.49 A | Line 300 A Drip | 2000-12-19 | Liquid | 2 ppm as Aroclor 1242 | ~10 mls
H10 | 300 A | 175.49 A | Line 300 A Drip | 2001-02-22 | Liquid | 2 ppm as Aroclor 1242 | ~20 mls
H10 | 300 A | 175.49 A | Line 300 A Drip | 2001-03-14 | Liquid | 2 ppm as Aroclor 1242 | ~20 mls
H10 | 300 A | 175.49 A | Line 300 A Drip | 2001-05-25 | Liquid |  | Insufficient sample, <10 mls
H10 | 300 A | 175.49 A | Line 300 A Drip | 2001-07-09 | Liquid | 2 ppm as Aroclor 1242 | ~5 mls
H10 | 300 A | 175.49 A | Line 300 A Drip | 2001-10-17 | Liquid | 2 ppm as Aroclor 1242 | ~20 mls
| 300 A | 180.64 A | Trona - Main # 311 X | 2000-02-10 | None |  | No liquids in filter (east filter tap)
R14 | 300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-02-10 | Liquid | 4 ppm | Second Stage sample point - good liquid sample obtained
R14 | 300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-02-24 | Liquid | 5 ppm | Second stage Regulator
R14 | 300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-03-08 | Liquid | 7 ppm
R14 | 300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-03-21 | Liquid | 26 ppm
R14 | 300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-04-05 | Liquid | 11 ppm | Regulator Pit
R14 | 300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-04-18 | Liquid | 6 ppm
R14 | 300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-05-03 | Liquid | 12 ppm
R14 | 300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-05-15 | Liquid | 14 ppm
R14 | 300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-05-30 | Liquid | 26 ppm
R14 | 300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-07-25 | None
R14 | 300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-08-10 | Liquid | 8 ppm
R14 | 300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-08-21 | None
R14 | 300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-08-24 | Liquid | 4 ppm
R14 | 300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-09-06 | Liquid | 9 ppm | <10 mls
R14 | 300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-09-19 | None |  | Dry
R14 | 300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-10-04 | None |  | Dry
R14 | 300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-11-03 | None |  | Dry
R14 | 300 A | 181.79 A | Kramer Junction (4 Corners) | 2000-12-05 | None |  | Dry
R14 | 300 A | 181.79 A | Kramer Junction (4 Corners) | 2001-01-03 | None |  | Dry
R14 | 300 A | 181.79 A | Kramer Junction (4 Corners) | 2001-02-02 | Liquid | 20 ppm as Aroclor 1242 | < 10 mls
| 301 A | 181.79 A | Kramer Junction (4 Corners) | 2001-03-05 | Liquid | 8 ppm as Aroclor 1242 | < 10 mls
| 301 A | 181.79 A | Kramer Junction (4 Corners) | 2001-10-02 | None
| 300 A | 188.06 A | Boron Town Site |  | None |  | Tap not inspected or sampled
| 300 A | 188.06 A | Boron Town Site | 2000-06-01 | Liquid | 1 ppm
| 300 A | 191.09 A | US Borax and Chem. Co., Hal B Hayes |  | None |  | Tap not inspected or sampled
| 300 A | 197.63 A | North Edwards - Red Barn | 2000-02-10 | None |  | Didn't sample
| 300 A | 200.97 A | Clay Mine Road (Muroc Motel) | 2000-02-10 | None |  | Didn't sample
| 300 A | 200.97 A | Clay Mine Road (Muroc Motel) | 2001-04-16 | Wipe | < 1ug/wipe | Sample taken downstream of regulator
| 300 A | 203.01 A | PLS 3A Insertion Meter | 2000-02-16 | Wipe | ND <0.7 ug/100cm2
| 300 A | 203.02 A | Edwards AFB, from PLS #3, elbow | 2000-02-10 | Wipe | 1.3 ug/wipe | East Run - Two Wipe samples taken (semi-quantitative)
| 300 A | 203.02 A | Edwards AFB, from PLS #3, elbow | 2000-08-10 | Wipe | 3 ppm
| 300 A | 203.02 A | Edwards AFB, from PLS #3, valve | 2000-02-10 | Wipe | < 1ug/wipe | East Run - Two Wipe samples taken (semi-quantitative)
R12 | 300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-03-22 | Wipe | 2 ug /wipe as Aroclor 1016, 1 ug/wipe as Aroclor 1254
R12 | 300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-04-04 | Wipe | 0.8 ug /wipe as Aroclor 1016, 0.8 ug/wipe as Aroclor 1254
R12 | 300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-05-15 | Liquid | 1 ppm
R12 | 300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-06-01 | Liquid | 8 ppm
R12 | 300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-06-13 | Liquid | 3 ppm
R12 | 300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-07-24 | Liquid | 2.6 ppm as Aroclor 1016, 0.6 ppm as Aroclor 1260 | < 10 mls
R12 | 300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-08-22 | Liquid | 2 ppm as Aroclor 1016, 1 ppm as Aroclor 1254 | < 10 mls liquid
R12 | 300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-09-06 | Liquid | 2 ppm as Aroclor 1016, 2 ppm as Aroclor 1254 | < 10 mls
R12 | 300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-09-19 | Liquid | 2 ppm | < 10 mls
R12 | 300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-10-03 | Liquid | 19 ppm | < 10 mls
R12 | 300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2000-11-03 | Liquid | <1 ppm | < 10 mls?
R12 | 300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2001-01-02 | Liquid | 1 ppm as Aroclor 1242, 0.7ppm as Aroclor 1254 | < 10 mls
R12 | 300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2001-02-02 | Liquid | 2 ppm as Aroclor 1242 | < 10 mls
R12 | 300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2001-04-02 | Liquid | 2 ppm as Aroclor 1242 | < 10 mls
R12 | 300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2001-05-01 | Liquid | 2 ppm as Aroclor 1242, 1 ppm as Aroclor 1254 | < 10 mls
R12 | 300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2001-07-03 | None
R12 | 300 A | 203.02 A | Edwards AFB, Industrial Meter Set | 2001-10-02 | None
R11 | 300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-03-22 | Liquid | < 1 ppm
R11 | 300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-04-04 | Liquid | < 1 ppm
R11 | 300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-04-19 | Liquid | ND < 1 ppm
R11 | 300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-05-04 | Liquid | ND < 1 ppm
R11 | 300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-05-15 | Liquid |  | Insufficient Sample
R11 | 300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-06-01 | Liquid |  | Insufficient Sample
R11 | 300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-06-13 | Liquid | ND < 1 ppm
R11 | 300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-06-27 | Liquid |  | Insufficient Sample
R11 | 300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-07-24 | None
R11 | 300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-08-21 | None
R11 | 300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-09-06 | Liquid |  | Insufficient sample, <10 mls
R11 | 300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-09-19 | None |  | no liquid
R11 | 300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-10-03 | None |  | no liquid
R11 | 300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-11-03 | Liquid | ND < 1ppm | <10 mls
R11 | 300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2000-12-01 | Liquid | 1 ppm as Aroclor 1016, < 1ppm, as Aroclor 1254 | <10 mls
R11 | 300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2001-01-02 | Liquid | ND < 1 ppm | <10 mls
R11 | 300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2001-02-02 | Liquid | ND < 5 ppm | <10 mls
R11 | 300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2001-04-02 | Liquid | ND < 10 ppm | <10 mls (detection limit raised due to insufficient sample volume)
R11 | 300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2001-05-01 | Liquid | ND < 1 ppm | <10 mls
R11 | 300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2001-07-03 | None |  | Sample received broken
R11 | 300 A | 203.02 A | Edwards AFB, Housing Meter Set | 2001-10-01 | None
| 300 A | 210.47 A | All American Pipeline Filter | 2000-02-29 | Liquid | < 1 ppm | Sample from filter (Site shut-in as of 4/00)
| 300 A | 210.47 A | All American Pipeline Filter | 2000-02-29 | Liquid | 1 ppm | Additional sample obtained from filter (Site shut-in as of 4/00)
| 300 A | 218.73 A | Mojave Meter and Reg Station, So. Cal Gas |  | None |  | Tap not inspected or sampled
R09 | 300 A | 225.57 A | California Portland Cement | 2000-02-24 | Liquid | ND < 1ppm | Sample from Old Orifice meter (Left)
R09 | 300 A | 225.57 A | California Portland Cement | 2000-05-15 | Liquid | 1 ppm | Tap meter
R09 | 300 A | 225.57 A | California Portland Cement | 2000-06-10 | Liquid | 1 ppm | Tap meter
R09 | 300 A | 225.57 A | California Portland Cement | 2000-06-26 | Liquid | 1 ppm | Tap meter
R09 | 300 A | 225.57 A | California Portland Cement | 2000-07-24 | Liquid | 2 ppm | Tap meter, < 10 mls
R09 | 300 A | 225.57 A | California Portland Cement | 2000-08-07 | Liquid | 2 ppm | Tap meter, < 10 mls
R09 | 300 A | 225.57 A | California Portland Cement | 2000-08-21 | Liquid | 8 ppm | Tap meter, < 10 mls
R09 | 300 A | 225.57 A | California Portland Cement | 2000-09-18 | Liquid | 2 ppm | Tap meter, < 10 mls
R09 | 300 A | 225.57 A | California Portland Cement | 2000-10-02 | Liquid | 2 ppm | Tap meter, < 10 mls
R09 | 300 A | 225.57 A | California Portland Cement | 2000-10-30 | Liquid | 1 ppm | Tap meter, < 10 mls
R09 | 300 A | 225.57 A | California Portland Cement | 2000-12-01 | Liquid | 2 ppm | Tap meter, < 10 mls
R09 | 300 A | 225.57 A | California Portland Cement | 2001-01-02 | Liquid | 2 ppm as Aroclor 1242 | Tap meter, < 10 mls
R09 | 300 A | 225.57 A | California Portland Cement | 2001-02-02 | Liquid | 2 ppm as Aroclor 1242 | Tap meter, < 10 mls
R09 | 301 A | 225.57 A | California Portland Cement | 2001-03-05 | Liquid | < 1 ppm | Tap meter, < 10 mls
R09 | 301 A | 225.57 A | California Portland Cement | 2001-04-02 | Liquid | < 1 ppm | Tap meter, < 10 mls
R09 | 301 A | 225.57 A | California Portland Cement | 2001-05-01 | Liquid | 1 ppm as Aroclor 1242 | Tap meter, < 10 mls ?
R09 | 300 A | 225.57 A | California Portland Cement | 2001-05-29 | Liquid | 6 ppm as Aroclor 1242 | Tap meter, < 10 mls
R09 | 300 A | 225.57 A | California Portland Cement | 2001-08-01 | Liquid | 1 ppm as Aroclor 1242 | Tap meter, < 10 mls
R09 | 300 A | 225.57 A | California Portland Cement | 2001-08-31 | Liquid | ND < 1 ppm | Tap meter, < 10 mls
R09 | 300 A | 225.57 A | California Portland Cement | 2001-10-02 | Liquid | ND < 2 ppm | Tap meter, < 10 mls (reporting limit raised due to insufficient sample)
R09 | 300 A | 225.57 A | California Portland Cement | 2001-11-02 | Liquid |  | Tap meter, < 10 mls (insufficient sample)
| 300 A | 225.91 A | California Portland Cement | 2000-04-05 | Liquid | ND < 1 ppm | Primary, downstream
| 300 A | 225.91 A | California Portland Cement | 2000-05-04 | Liquid | ND < 1 ppm | Primary, downstream
| 300 A | 225.91 A | California Portland Cement | 2000-10-02 | Liquid | 4 ppm as Aroclor 1260 | 12 GT Meter, sample taken downstream
R10 | 300 A | 225.91 A | California Portland Cement Meter | 2000-04-19 | Liquid | ND < 1ppm
R10 | 300 A | 225.91 A | California Portland Cement Meter | 2000-05-15 | Liquid |  | Insufficient Sample
R10 | 300 A | 225.91 A | California Portland Cement Meter | 2000-06-10 | Liquid | 1 ppm
R10 | 300 A | 225.91 A | California Portland Cement Meter | 2000-07-24 | None
R10 | 300 A | 225.91 A | California Portland Cement Meter | 2000-08-21 | None
R10 | 300 A | 225.91 A | California Portland Cement Meter | 2000-09-05 | Liquid | 1 ppm | <10 mls
R10 | 300 A | 225.91 A | California Portland Cement Meter | 2000-09-18 | None |  | no liquid
R10 | 300 A | 225.91 A | California Portland Cement Meter | 2000-10-02 | None |  | no liquid
R10 | 300 A | 225.91 A | California Portland Cement Meter | 2001-01-02 | None |  | no liquid
R10 | 300 A | 225.91 A | California Portland Cement Meter | 2001-04-02 | Liquid | ND < 1 ppm | < 10 mls,12 GT Meter, taken from large separator; no oil in small separator
R10 | 300 A | 225.91 A | California Portland Cement Meter | 2001-10-02 | None
| 300 A | 297.63 A | Red Barn Regulator | 2001-04-17 | Wipe | < 1 ug/wipe | Sample taken downstream of regulator
| 300 A | 116.28 B | P.L.G. X-tie (Pisgah) |  | None |  | Tap not inspected or sampled
| 300 B | 129.92 B | John R. Mason, Newberry (Customer meter) | 2000-02-09 | None |  | No liquid; no wipe
| 300 B | 129.92 B | John R. Mason, Newberry (Mason'sTAP) | 2000-02-09 | None |  | No readily acceptable sampling point
| 300 B | 129.92 B | John R. Mason, Newberry (Mason'sTAP) | 2000-02-09 | Wipe | < 1 ug/wipe | sample taken from downstream regulator
| 300 B | 130.38 B | Line 300 B insertion meter | 2000-02-11 | Wipe | ND < 0.7 ug/100cm2 | Pulled insertion meter; measured exterior surface area (not including turbine wheel); took wipe sample of measured area
| 300 B | 130.38 B | PLS 2XA Mist Extractor | 2000-04-12 | Liquid | ND <1ppm
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2000-02-08 | Liquid | 6 ppm | Sample obtained from filter, downstream of regulator. Black thick liquid obtained Good taps before and after meter available for sampling.
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2000-02-24 | Liquid | 14 ppm | Meter Set, Filter
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2000-03-09 | Liquid | 10 ppm | Meter Set, Filter
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2000-03-21 | Liquid | 17 ppm | Meter Set, Filter
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2000-04-05 | Liquid | 13 ppm | Meter Set, Filter
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2000-04-17 | Liquid | 13 ppm | Meter Set, Filter
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2000-04-17 | Liquid | ND < 1ppm | Meter Separator
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2000-05-03 | Liquid | 35 ppm | Meter Set, Filter
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2000-05-16 | Liquid | 12 ppm | Meter Set, Filter
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2000-05-30 | Liquid | 12 ppm | Meter Set, Filter
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2000-06-13 | Liquid | 12 ppm | Meter Set, Filter
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2000-06-27 | Liquid | 12 ppm | Meter Set, Filter
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2000-07-25 | Liquid | 10 ppm | Meter Set, Filter, < 10 mls
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2000-08-22 | None |  | no liquid - new filter separator installed
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2000-09-19 | None |  | no liquid - new filter separator installed
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2000-10-03 | None |  | no liquid - new filter separator installed
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2000-12-05 | None |  | no liquid - new filter separator installed
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2001-01-03 | None |  | no liquid - new filter separator installed
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2001-02-05 | Liquid | 22 ppm as Aroclor 1242 | < 10 mls from separator
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2001-03-02 | Liquid | 15 ppm as Aroclor 1242 | < 10 mls from separator
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2001-04-03 | Liquid | 16 ppm as Aroclor 1242 | < 10 mls from separator
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2001-05-02 | Liquid | 42 ppm as Aroclor 1242 | < 10 mls from separator ?
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2001-05-29 | Liquid | 46 ppm as Aroclor 1242 | < 10 mls from separator
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2001-06-25 | None |  | Insufficient Sample
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2001-07-09 | None |  | Sample received broken
R01 | 300 B | 131.37 B | RHEOX Chem. Co. | 2001-08-27 | None |  | < 10 mls from separator
| 300 B | 131.94 B | Newberry Springs | 2001-04-10 | Wipe | < 1 ug/wipe | sample taken from downstream regulator
| 300 B | 135.65 B | Southwest Gas Corp. (Cirano Farm) |  | None |  | Tap not inspected or sampled
| 300 B | 137.55 B | SWG, Daggett Airport Tap | 2000-02-11 | None |  | Sample tap available from bottom of filter - No liquids were found.
| 300 B | 138.67 B | Hell's Acre Ranch |  | None |  | Tap not inspected or sampled - Service Tee and Valve only. Southwest Gas to furnish meter, etc.
| 300 B | 140.00 B | Kern River Daggett Intertie | 2000-02-10 | None |  | No liquid from #7 Bypass valve next to filter separator. Separator is shut-in.
| 300 B | 140.65 B | SEGS 1 Meter Set | 2000-02-08 | Wipe | < 1ug/100cm2 | Wipe taken from 2 inches inside meter casing on inlet side
| 300 B | 140.65 B | SEGS 1 Meter Set | 2000-02-08 | Liquid | 6 ppm | Small amount of clear liquid present at bottom of meter.
| 300 B | 140.65 B | SEGS 1 Meter Set | 2000-02-23 | Liquid | 2 ppm
| 300 B | 140.65 B | SEGS 1 Meter Set | 2000-03-21 | Liquid | 4 ppm
| 300 B | 140.65 B | SEGS 1 Meter Set | 2000-04-05 | Liquid | 6 ppm
| 300 B | 140.65 B | SEGS 1 Meter Set | 2000-04-17 | Liquid | 4 ppm
| 300 B | 140.65 B | SEGS 1 Meter Set | 2000-05-03 | Liquid | 5 ppm
| 300 B | 140.65 B | SEGS 1 Meter Set | 2000-06-13 | Liquid | 6 ppm
R02 | 300 B | 140.65 B | SEGS 1 Primary drip Pot | 2000-02-08 | Wipe | < 1ug/100cm2 | Wipe sample taken from East filter only filter was degraded
R02 | 300 B | 140.65 B | SEGS 1 Primary drip Pot | 2000-03-09 | Liquid | 2 ppm
R02 | 300 B | 140.65 B | SEGS 1 Primary drip Pot | 2000-06-13 | Liquid | 6 ppm
R02 | 300 B | 140.65 B | SEGS 1 Primary drip Pot | 2000-06-27 | Liquid | 5 ppm
R02 | 300 B | 140.65 B | SEGS 1 Primary drip Pot | 2000-07-25 | None
R02 | 300 B | 140.65 B | SEGS 1 Primary drip Pot | 2000-08-21 | None
R02 | 300 B | 140.65 B | SEGS 1 Primary drip Pot | 2000-09-19 | None |  | Dry
R02 | 300 B | 140.65 B | SEGS 1 Primary drip Pot | 2000-10-03 | None |  | Dry
R02 | 300 B | 140.65 B | SEGS 1 Primary drip Pot | 2000-11-03 | None |  | Dry
R02 | 300 B | 140.65 B | SEGS 1 Primary drip Pot | 2000-12-05 | None |  | Dry
R02 | 300 B | 140.65 B | SEGS 1 Primary drip Pot | 2001-01-03 | Liquid | 5 ppm | < 10 mls
R02 | 300 B | 140.65 B | SEGS 1 Primary drip Pot | 2001-02-05 | Liquid | 9 ppm as Aroclor 1016 | < 10 mls
R02 | 300 B | 140.65 B | SEGS 1 Primary drip Pot | 2001-02-28 | Liquid | 6 ppm as Aroclor 1242 | < 10 mls (no oil in separator)
R02 | 300 B | 140.65 B | SEGS 1 Primary drip Pot | 2001-06-25 | None |  | Insufficient Sample
R02 | 300 B | 140.65 B | SEGS 1 Primary drip Pot | 2001-07-09 | None | 5 ppm as Aroclor 1242 | < 10 mls
R02 | 300 B | 140.65 B | SEGS 1 Primary drip Pot | 2001-08-27 | None | 6 ppm as Aroclor 1242 | < 10 mls (trace)
| 300 B | 140.91 B | SWG, Daggett | 2000-02-10 | None |  | Sample tap available from bottom of filter - No liquids were found.
| 300 B | 159.33 B | Hinkley Compressor Station K-7, B Outlet | 2000-02-15 | Liquid | ND < 1 ppm
| 300 B | 159.33 B | Hinkley Compressor Station K-7, B Outlet | 2000-02-15 | Wipe | < 1ug/wipe
| 300 B | 159.33 B | Hinkley Compressor Station K-7, B Inlet | 2000-02-15 | Liquid | 1 ppm
| 300 B | 159.33 B | Hinkley Compressor Station 300B Suction Drip | 2000-01-27 | Liquid | 4 ppm
| 300 B | 159.33 B | Hinkley Compressor Station 300B Suction Drip | 2000-02-10 | Liquid | 4 ppm | Black liquid obtained. Drip was emptied after sample was obtained
| 300 B | 159.33 B | Hinkley Compressor Station B V-211 Inlet Drip | 2000-04-20 | Liquid | 11 ppm
| 300 B | 159.33 B | Hinkley Compressor Station B V-211 Inlet Drip | 2000-05-02 | Liquid | 10 ppm
| 300 B | 159.33 B | Hinkley Compressor Station B V-211 Inlet Drip | 2000-06-15 | Liquid | 8 ppm
| 300 B | 159.33 B | Hinkley Compressor Station B V-211 Inlet Drip | 2000-08-18 | Liquid | 9 ppm
| 300 B | 159.33 B | Hinkley Compressor Station B V-211 Inlet Drip | 2000-09-05 | Liquid | 12 ppm | 50 mls
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-02-25 | Liquid | 7 ppm
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-03-09 | Liquid | 8 ppm
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-03-23 | Liquid | 12 ppm
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-04-06 | Liquid | 7 ppm
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-04-20 | Liquid | 7 ppm
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-05-01 | Liquid | 7 ppm
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-05-14 | Liquid | 11 ppm
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-05-30 | Liquid | 7 ppm
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-06-15 | Liquid | 8 ppm
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-06-30 | Liquid | 8 ppm
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-08-18 | Liquid | 9 ppm
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-08-18 | Liquid | 10 ppm | ~40 mls
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-09-18 | Liquid | 10 ppm | ~40 mls
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-10-16 | Liquid | 12 ppm | ~20 mls
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-10-26 | Liquid | 13 ppm | ~15 mls
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-11-20 | Liquid | 21 ppm | ~ 40 mls
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2000-12-19 | Liquid | 12 | ~ 30 mls
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2001-02-22 | Liquid | 14 | ~ 20 mls
H02 | 301 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2001-03-14 | Liquid | 16 ppm as Aroclor 1242 | ~ 20 mls
H02 | 301 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2001-04-24 | Liquid | 15 ppm as Aroclor 1242 | ~ 40 mls
H02 | 301 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2001-05-25 | Liquid | 14 ppm as Aroclor 1242 | ~ 30 mls
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2001-06-26 | Liquid | 19 ppm as Aroclor 1242 | ~ 30 mls
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2001-07-09 | Liquid | 16 ppm as Aroclor 1242 | ~ 30 mls
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2001-08-27 | Liquid | 14 ppm as Aroclor 1242 | ~ 45 mls
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2001-09-25 | Liquid | 13 ppm as Aroclor 1242 | ~ 40 mls
H02 | 300 B | 161.02 B | Hinkley Compressor Station B V-212 Inlet Drip | 2001-10-19 | Liquid | 5 ppm as Aroclor 1242 | ~ 30 mls
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-02-10 | Liquid | 1ppm | Sample obtained from bottom of inlet filter to 8" meter run.
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-02-25 | Liquid | 2 ppm | Sample obtained from 8" filter
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-03-09 | Liquid | 1 ppm | Sample obtained from 8" filter
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-03-23 | Liquid | 2 ppm | Sample obtained from 8" filter
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-04-18 | Liquid | 2 ppm | Sample taken from 8" filter
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-04-23 | Liquid | <1 ppm | Sample obtained from 8" filter
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-05-01 | Liquid | 1 ppm | Sample obtained from 8" filter
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-05-14 | Liquid | 1 ppm | Sample obtained from 8" filter
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-06-01 | Liquid | 1 ppm | Sample obtained from 8" filter
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-06-15 | Liquid | 2 ppm | Sample obtained from 8" filter
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-06-30 | Liquid | 1 ppm | Sample obtained from 8" filter
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-07-29 | Liquid | 1 ppm | Sample obtained from 8" filter
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-08-21 | Liquid | 2 ppm | Sample obtained from 8" filter
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-09-05 | Liquid | 2 ppm | Sample obtained from 8" filter, ~10 mls
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-09-19 | Liquid | 2 ppm | Sample obtained from 8" filter, ~10 mls
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-10-03 | Liquid | 2 ppm | Sample obtained from 8" filter, < 10 mls
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-10-17 | Liquid | 2 ppm | Sample obtained from 8" filter, < 10 mls
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-10-27 | Liquid | 3 ppm | Sample obtained from 8" filter, < 10 mls
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2000-12-19 | Liquid | 2 ppm as Aroclor 1242 | Sample obtained from 8" filter, ~10 mls (sample container received broken)
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2001-01-22 | Liquid | 2 ppm as Aroclor 1242 | Sample obtained from 8" filter, ~10 mls
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2001-02-22 | Liquid | 4 ppm as Aroclor 1242 | Sample obtained from 8" filter, <10 mls
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2001-03-14 | Liquid | 2 ppm as Aroclor 1242 | Sample obtained from 8" filter, <10 mls
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2001-04-26 | Liquid | 3 ppm as Aroclor 1242 | Sample obtained from 8" filter, <10 mls
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2001-05-25 | Liquid | 2 ppm as Aroclor 1242 | Sample obtained from 8" filter, <10 mls
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2001-07-09 | Liquid | 3 ppm as Aroclor 1242 | Sample obtained from 8" filter, <10 mls
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2001-08-27 | Liquid | 2 ppm as Aroclor 1242 | Sample obtained from 8" filter, <10 mls
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2001-09-24 | Liquid | 2 ppm as Aroclor 1242 | Sample obtained from 8" filter, ~10 mls
H03 | 300 B | 168.39 B | SWG, Harper lake Meter Station | 2001-10-22 | Liquid | 5 ppm as Aroclor 1242 | Sample obtained from 8" filter, ~10 mls
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-02-10 | Liquid | 1 ppm
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-02-10 | Liquid | 1 ppm | Liquids obtained from drip. Drip completely drained after sampling. Drip was also drained during first week of 2/2000.
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-03-09 | Liquid | 1 ppm
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-04-06 | Liquid | 1 ppm
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-04-19 | Liquid | < 1 ppm
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-05-01 | Liquid | ND < 1 ppm
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-05-14 | Liquid | ND < 1 ppm
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-06-01 | Liquid |  | Insufficient sample
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-06-15 | Liquid | 1 ppm
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-06-30 | Liquid | 1 ppm
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-07-29 | Liquid | 1 ppm
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-08-21 | Liquid | 1 ppm
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-09-06 | Liquid | 1 ppm | ~20 mls
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-09-19 | Liquid | 2 ppm | ~20 mls
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-10-03 | Liquid | 2 ppm | ~20 mls
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-10-17 | Liquid | 2 ppm | ~20 mls
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-10-27 | Liquid | 2 ppm | ~40 mls
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-11-21 | Liquid | 3 ppm | ~15 mls
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2000-12-19 | Liquid | 2 ppm | ~30 mls
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2001-01-23 | Liquid | < 1 ppm | ~25 mls
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2001-02-22 | Liquid | 3 ppm as Aroclor 1242 | ~10 mls
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2001-03-14 | Liquid | 2 ppm as Aroclor 1242 | ~20 mls
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2001-04-26 | Liquid | 1 ppm as Aroclor 1242 | ~20 mls
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2001-06-26 | Liquid | 2 ppm as Aroclor 1242 | ~25 mls
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2001-07-09 | Liquid | 2 ppm as Aroclor 1242 | ~15 mls
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2001-08-27 | Liquid | 2 ppm as Aroclor 1242 | ~20 mls
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2001-09-24 | Liquid | 2 ppm as Aroclor 1242 | ~15 mls
H08 | 300 B | 169.95 B | Line 300 B Drip at Victorville Tap | 2001-10-17 | Liquid | 2 ppm as Aroclor 1242 | <10 mls (trace)
| 300 B | 170.44 B | South West Gas - Harper Lake Meter Station |  | None |  | Tap not inspected or sampled
| 300 B | 180.11 B | Trona - Main # 311 X |  | None |  | Tap not inspected or sampled
| 300 B | 182.00 B | John Wiles Co. |  | None |  | Farm tap Reg. Set. Tap. Service tap not inspected or sampled and is abandoned
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-02-10 | Liquid | 2 ppm | Mist generated during sampling (light coating in bottle only)
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-02-24 | Liquid | 2 ppm
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-03-08 | Liquid | 3 ppm
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-03-22 | Liquid | 3 ppm
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-04-05 | Liquid | 2 ppm
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-04-17 | Liquid | 3 ppm
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-05-04 | Liquid | 2 ppm
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-05-16 | Liquid | 1 ppm
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-05-30 | Liquid | 2 ppm
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-06-13 | Liquid | 2 ppm
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-06-27 | Liquid | 3 ppm
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-07-25 | Liquid | 3 ppm | < 10 mls
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-08-07 | Liquid | 4 ppm | ~10 mls
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-08-22 | Liquid | 3 ppm | ~50 mls liquid
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-09-06 | Liquid | 6 ppm as Aroclor 1016, 2 ppm as Aroclor 1254 | ~10 mls
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-09-18 | Liquid | 6 ppm | ~10 mls
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-10-04 | Liquid | 4 ppm | ~20 mls
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-11-03 | Liquid | 3 ppm | ~20 mls
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2000-12-04 | Liquid | 4 ppm | ~10 mls
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2001-01-03 | Liquid | 13 ppm as Aroclor 1242 | ~10 mls
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2001-02-05 | Liquid | 6 ppm as Aroclor 1242 | ~25mls
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2001-03-05 | Liquid | 6 ppm as Aroclor 1242 | <10 mls
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2001-04-03 | Liquid | 4 ppm as Aroclor 1242 | <10 mls
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2001-05-01 | Liquid | 5 ppm as Aroclor 1242 | <10 mls?
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2001-05-31 | Liquid | 7 ppm as Aroclor 1242 | <10 mls
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2001-07-03 | None |  | <25 mls (taken from filter drain)
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2001-08-01 | Liquid | 3 ppm as Aroclor 1242 | <25 mls (taken from filter drain)
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2001-08-31 | Liquid | 2 ppm as Aroclor 1242 | <25 mls (taken from filter drain)
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2001-10-02 | Liquid | 2 ppm as Aroclor 1242 | <25 mls (taken from filter drain)
R15 | 300 B | 182.58 B | SEGS 3 & 4 Primary Filter | 2001-11-01 | Liquid | 2 ppm as Aroclor 1242 | <25 mls (taken from filter drain)
| 300 B | 182.58 B | SEGS 5,6 & 7 Primary | 2000-02-10 | None |  | Filter was dry
| 300 B | 182.58 B | SEGS 7 Meter Set | 2000-02-10 | None |  | Turbine mater sample - dry
R13 | 300 B | 187.78 B | Boron Tap | 2000-02-10 | Liquid | 1 ppm | Primary reg. filter, East run; good sample
R13 | 300 B | 187.78 B | Boron Tap | 2000-02-24 | Liquid | 2 ppm
R13 | 300 B | 187.78 B | Boron Tap | 2000-03-08 | Liquid | 1 ppm
R13 | 300 B | 187.78 B | Boron Tap | 2000-04-04 | Liquid | 1 ppm
R13 | 300 B | 187.78 B | Boron Tap | 2000-04-17 | Liquid | 1 ppm
R13 | 300 B | 187.78 B | Boron Tap | 2000-05-04 | Liquid | 1 ppm
R13 | 300 B | 187.78 B | Boron Tap | 2000-05-15 | Liquid | 1 ppm
R13 | 300 B | 187.78 B | Boron Tap | 2000-06-01 | Liquid | 1 ppm
R13 | 300 B | 187.78 B | Boron Tap | 2000-06-27 | None |  | Insufficient sample
R13 | 300 B | 187.78 B | Boron Tap | 2000-08-22 | None |  | no liquids
R13 | 300 B | 187.78 B | Boron Tap | 2000-09-06 | None |  | no liquids
R13 | 300 B | 187.78 B | Boron Tap | 2000-09-19 | None |  | no liquids
R13 | 300 B | 187.78 B | Boron Tap | 2000-10-03 | None |  | no liquids
R13 | 300 B | 187.78 B | Boron Tap | 2000-10-31 | None |  | no liquids
R13 | 300 B | 187.78 B | Boron Tap | 2000-12-05 | None |  | no liquids
R13 | 300 B | 187.78 B | Boron Tap | 2001-01-03 | None |  | no liquids
R13 | 300 B | 187.78 B | Boron Tap | 2001-07-03 | Liquid | 8 ppm as Aroclor 1242, 7 ppm as Aroclor 1254 | Sample taken from inlet filter
R13 | 300 B | 187.78 B | Boron Tap | 2001-10-02 | None
| 300 B | 187.78 B | Boron High School Dry Gas Meter No. 32707774 | 2000-03-15 | Wipe | ND < 1ug/wipe | Meter removed and replaced. Non-quantitative wipe taken on drain cover and inside of drain cover opening.
| 300 B | 187.78 B | Joshua Trailer Park, 26611 Nugent, Boron | 2000-03-13 | Wipe | ND < 1ug/wipe | Non-quantitative wipe inside filter
| 300 B | 191.14 B | US Borax (Bypass) |  | None |  | Tap not inspected or sampled
| 300 B | 191.18 B | Desert Lakes US Borax | 2000-02-10 | None |  | Primary reg. filter, North run; dry (Recheck filter)
| 300 B | 191.18 B | US Borax |  | None |  | Tap not inspected or sampled
| 300 B | 191.18 B | Desert Lakes US Borax | 2001-03-20 | Liquid | < 1 ppm | < 10 mls Inside reg pilot
| 300 B | 197.70 B | M. Penn Philips Tract, Gilbert St. |  | None |  | Tap not inspected or sampled; line abandoned
| 300 B | 198.86 B | Clay Mine Rd Reg. | 2001-04-17 | Wipe | < 1ug/wipe | Sample taken downstream from regulator
| 300 B | 198.88 B | Edgemont Road District (West Boron Area) Increase Capacity |  | None |  | San Joaquin Div., original farm tap and reg. Installed second farm tap and reg. in parallel with existing set. Taps not inspected or sampled.
| 300 B | 199.24 B | Fountain Trailer Court |  | None |  | Tap not inspected or sampled - line abandoned in 1987
| 300 B | 203.07 B | PLS 3B Insertion Meter | 2000-02-16 | Wipe | ND <0.7 ug/100cm2
| 300 B | 203.07 B | PLS 3B Mist Extractor | 2000-04-14 | Liquid | ND < 1ppm
| 300 B | 203.07 B | Emergency Tie-in to Main 300B |  | None |  | Tap not inspected or sampled
| 300 B | 239.04 B | Tehachapi |  | None |  | Tap not inspected or sampled - line abandoned
R07 | 311 X | 54.14 | Ridgecrest West End Primary | 2000-02-22 | Wipe | < 1ug/100cm2 | Right Filter
R07 | 311 X | 54.14 | Ridgecrest West End Primary | 2000-04-06 | Wipe | ND < 1ug/wipe | Right Filter (non-quantitative wipe)
R07 | 311 X | 54.14 | Ridgecrest West End Primary | 2000-04-19 | Wipe | ND < 1ug/wipe | Right Filter (non-quantitative wipe)
R07 | 311 X | 54.14 | Ridgecrest West End Primary | 2000-07-24 | None
R07 | 311 X | 54.14 | Ridgecrest West End Primary | 2000-09-18 | None
R07 | 311 X | 54.14 | Ridgecrest West End Primary | 2000-10-02 | None
R07 | 311 X | 54.14 | Ridgecrest West End Primary | 2001-01-02 | None
R07 | 311 X | 54.14 | Ridgecrest West End Primary | 2001-07-02 | Liquid | 10 ppm as Aroclor 1242 | No volume recorded
R07 | 311 X | 54.14 | Ridgecrest West End Primary | 2001-08-01 | Liquid | 11 ppm as Aroclor 1242 | > 50 mls from separator drain
R07 | 311 X | 54.14 | Ridgecrest West End Primary | 2001-09-04 | Liquid | 12 ppm as Aroclor 1242 | > 50 mls from separator drain
R07 | 311 X | 54.14 | Ridgecrest West End Primary | 2001-10-01 | Liquid | 22 ppm as Aroclor 1242, 4 ppm as Aroclor 1254 | < 50 mls from separator drain
R07 | 311 X | 54.14 | Ridgecrest West End Primary | 2001-11-01 | Liquid | 20 ppm as Aroclor 1242, 5 ppm as Aroclor 1254 | < 50 mls from separator drain
R08 | 311 X | 54.44 | West End Plant (old meter set) | 2000-06-12 | Wipe | ND < 1 ug/wipe | Semi-quantitative
R08 | 311 X | 54.44 | West End Plant (old meter set) | 2000-08-21 | None |  | no liquid found
R08 | 311 X | 54.44 | West End Plant (old meter set) | 2001-01-02 | None |  | no liquid found
R08 | 311 X | 54.44 | West End Plant (old meter set) | 2001-10-01 | None |  | no liquid found
| 311 X | 54.88 | IMC Chemical, Trona | 2000-04-03 | Wipe | 2.6 ug/wipe as Aroclor 1016, 1.2 ug/wipe as Aroclor 1254 | West End Turbine Meter
| 311 X | 54.88 | Ridgecrest West End Turbine Meter | 2000-04-19 | Liquid | 11 ppm as Aroclor 1016, 12 ppm as Aroclor 1260
| 311 X | 54.88 | Ridgecrest West End Turbine Meter | 2000-05-04 | Liquid | 11 ppm as Aroclor 1016, 8 ppm as Aroclor 1254
| 311 X | 54.88 | Ridgecrest West End Turbine Meter | 2000-05-31 | Liquid | 13 ppm as Aroclor 1016, 9 ppm as Aroclor 1254
| 311 X | 54.88 | Ridgecrest West End Turbine Meter | 2000-06-12 | Liquid | 16 ppm as Aroclor 1016, 7 ppm as Aroclor 1260
| 311 X | 54.88 | Ridgecrest West End Turbine Meter | 2000-06-26 | Liquid | 11 ppm as Aroclor 1016, 17 ppm as Aroclor 1260
| 311 X | 54.88 | Ridgecrest West End Turbine Meter | 2000-07-24 | Liquid | 8.4 ppm as Aroclor 1016, 7.9 ppm as Aroclor 1260
| 311 X | 54.88 | Ridgecrest West End Turbine Meter | 2000-08-08 | Liquid | 29 ppm as Aroclor 1016, 27 ppm as Aroclor 1254 | <10 mls
| 311 X | 54.88 | Ridgecrest West End Turbine Meter | 2000-09-05 | Liquid | 6 ppm as Aroclor 1016, 9 ppm as Aroclor 1254 | < 10 mls
| 311 X | 54.88 | Ridgecrest West End Turbine Meter | 2000-09-18 | Liquid | 7 ppm as Aroclor 1016, 9 ppm as Aroclor 1260 | < 10 mls
| 311 X | 54.88 | Ridgecrest West End Turbine Meter | 2000-10-02 | Liquid |  | < 10 mls (Insufficient sample)
R17 | 311 X | 54.88 | Ridgecrest West End Process | 2000-05-04 | Liquid | 4 ppm as Aroclor 1016, 4 ppm as Aroclor 1254 | Turbine mater
R17 | 311 X | 54.88 | Ridgecrest West End Process | 2000-05-16 | Liquid | 4 ppm as Aroclor 1016, 12 ppm as Aroclor 1254
R17 | 311 X | 54.88 | Ridgecrest West End Process | 2000-05-31 | Liquid | 5 ppm as Aroclor 1016, 8 ppm as Aroclor 1254
R17 | 311 X | 54.88 | Ridgecrest West End Process | 2000-08-21 | None |  | no liquids found
R17 | 311 X | 54.88 | Ridgecrest West End Process | 2000-10-02 | Liquid | 10 ppm as Aroclor 1016, 7 ppm as Aroclor 1260 | < 10 mls
R17 | 311 X | 54.88 | Ridgecrest West End Process | 2000-10-31 | Liquid | 6.7 ppm as Aroclor 1016, 5.8 ppm as Aroclor 1260 | < 10 mls
R17 | 311 X | 54.88 | Ridgecrest West End Process | 2001-01-02 | Liquid | 3 ppm as Aroclor 1242, 3 ppm as Aroclor 1254 | < 10 mls
R17 | 311 X | 54.88 | Ridgecrest West End Process | 2001-02-01 | Liquid | 12 ppm as Aroclor 1242, 12ppm as Aroclor 1254 | < 10 mls from filter
R17 | 311 X | 54.88 | Ridgecrest West End Process | 2001-04-02 | Liquid | 11 ppm as Aroclor 1242, 9 ppm as Aroclor 1254 | < 10 mls from filter
R17 | 311 X | 54.88 | Ridgecrest West End Process | 2001-04-30 | Liquid | 12 ppm as Aroclor 1242, 8 ppm as Aroclor 1254 | < 10 mls from filter ?
R17 | 311 X | 54.88 | Ridgecrest West End Process | 2001-06-01 | Liquid | 11 ppm as Aroclor 1242 | Trace
R17 | 311 X | 54.88 | Ridgecrest West End Process | 2001-08-01 | Liquid | 9 ppm as Aroclor 1242, 11 ppm as Aroclor 1254 | <10 mls
R17 | 311 X | 54.88 | Ridgecrest West End Process | 2001-09-04 | Liquid | 12 ppm as Aroclor 1242 | ~ 50 mls
R17 | 311 X | 54.88 | Ridgecrest West End Process | 2001-10-01 | None
R16 | 311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2000-05-31 | Liquid | 4 ppm as Aroclor 1016, 11 ppm as Aroclor 1254 | 12 GT Meter
R16 | 311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2000-06-12 | Liquid | 6 ppm as Aroclor 1016, 7 ppm as Aroclor 1260
R16 | 311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2000-06-26 | Liquid | 5 ppm as Aroclor 1016, 9 ppm as Aroclor 1260
R16 | 311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2000-08-08 | Liquid | 8 ppm as Aroclor 1016, 19 ppm as Aroclor 1254
R16 | 311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2000-08-21 | Liquid | 8 ppm as Aroclor 1016, 27 ppm as Aroclor 1254 | <10 mls taken from meter drip
R16 | 311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2000-09-05 | Liquid | 3 ppm as Aroclor 1016, 11 ppm as Aroclor 1254 | < 10 mls
R16 | 311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2000-09-18 | Liquid | 3 ppm as Aroclor 1016, 12 ppm as Aroclor 1260 | < 10 mls
R16 | 311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2000-10-02 | Liquid | 2 ppm as Aroclor 1016, 8 ppm as Aroclor 1260 | < 10 mls
R16 | 311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2000-10-31 | Liquid | 2.8 ppm as Aroclor 1016, 8.9 ppm as Aroclor 1260 | < 10 mls
R16 | 311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2000-12-01 | Liquid | 4 ppm as Aroclor 1016, 9 ppm as Aroclor 1254 | < 10 mls
R16 | 311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2001-01-02 | Liquid | 5 ppm as Aroclor 1016, 17 ppm as Aroclor 1254 | < 10 mls
R16 | 311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2001-02-01 | Liquid | 7 ppm as Aroclor 1242, 14 ppm as Aroclor 1254 | < 10 mls from filter
R16 | 311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2001-02-28 | Liquid | 4 ppm as Aroclor 1242, 15 ppm as Aroclor 1254 | < 10 mls from meter
R16 | 311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2001-04-02 | Liquid | 4 ppm as Aroclor 1242, 12 ppm as Aroclor 1254 | < 10 mls from meter
R16 | 311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2001-04-30 | Liquid | 3 ppm as Aroclor 1242, 11 ppm as Aroclor 1254 | < 10 mls from meter ?
R16 | 311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2001-06-01 | Liquid | 5 ppm as Aroclor 1242 | < 10 mls from meter
R16 | 311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2001-07-02 | Liquid | 5 ppm as Aroclor 1242, 35 ppm as Aroclor 1254 | < 10 mls from meter?
R16 | 311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2001-08-01 | Liquid | 3 ppm as Aroclor 1242, 15 ppm as Aroclor 1254 | < 10 mls
R16 | 311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2001-09-04 | Liquid | 2 ppm as Aroclor 1242, 11 ppm as Aroclor 1254 | < 10 mls
R16 | 311 X | 58.04 | IMC Chemical, Trona - Argus, Main Tap | 2001-10-01 | None
| 313 X | 27.26 | SWG Rabbit Springs Rd. | 2000-02-09 | Liquid | 2 ppm, < 1ppm as Aroclor 1260. Semi quantitative results due to small sample | Obtained small amount of liquid obtained from bottom tap of meter. No liquid from gooseneck pipe on north filter.
H17 | 313 X | 27.26 | SWG Rabbit Springs Rd. Meter | 2000-02-28 | Liquid | 4 ppm
H17 | 313 X | 27.26 | SWG Rabbit Springs Rd. Meter | 2000-03-10 | Liquid | 10 ppm
H17 | 313 X | 27.26 | SWG Rabbit Springs Rd. Meter | 2000-03-22 | Liquid | 5 ppm
H17 | 313 X | 27.26 | SWG Rabbit Springs Rd. Meter | 2000-04-06 | Liquid | 9 ppm
H17 | 313 X | 27.26 | SWG Rabbit Springs Rd. Meter | 2000-05-14 | Liquid | 4 ppm
H17 | 313 X | 27.26 | SWG Rabbit Springs Rd. Meter | 2000-06-14 | Liquid | 11 ppm
H17 | 313 X | 27.26 | SWG Rabbit Springs Rd. Meter | 2000-06-30 | Liquid | 9 ppm as Aroclor 1016, 2 ppm as Aroclor 1254
H17 | 313 X | 27.26 | SWG, Rabbit Springs Rd. Meter | 2000-02-09 | None |  | Filter downstream from MP27.26 not accessible
H17 | 313 X | 27.26 | SWG, Rabbit Springs Rd. Meter | 2000-07-29 | Liquid | 6.8 ppm, as Aroclor 1016, 1.1 ppm, as Aroclor 1260
H17 | 313 X | 27.26 | SWG, Rabbit Springs Rd. Meter | 2000-09-05 | Liquid |  | <10 mls (insufficient sample)
H17 | 313 X | 27.26 | SWG, Rabbit Springs Rd. Meter | 2001-03-14 | Liquid | 6 ppm, as Aroclor 1242 | <10 mls (insufficient sample)
H17 | 313 X | 27.26 | SWG, Rabbit Springs Rd. Meter | 2001-04-26 | Liquid |  | Insufficient sample
H17 | 313 X | 27.26 | SWG, Rabbit Springs Rd. Meter | 2001-05-25 | Liquid | 1 ppm, as Aroclor 1242 | ~10 mls
H17 | 313 X | 27.26 | SWG, Rabbit Springs Rd. Meter | 2001-06-25 | Liquid | 3 ppm, as Aroclor 1242 | ~10 mls
H17 | 313 X | 27.26 | SWG, Rabbit Springs Rd. Meter | 2001-07-09 | Liquid | 2 ppm, as Aroclor 1242 | ~20 mls
H17 | 313 X | 27.26 | SWG, Rabbit Springs Rd. Meter | 2001-08-27 | Liquid | < 1ppm | ~20 mls
H17 | 313 X | 27.26 | SWG, Rabbit Springs Rd. Meter | 2001-09-24 | Liquid | < 1ppm | ~10 mls
H17 | 313 X | 27.26 | SWG, Rabbit Springs Rd. Meter | 2001-09-24 | Liquid | < 1ppm | <10 mls (trace)
| 313 X | 29.08 | SWG Old Woman Springs | 2000-02-09 | None |  | North filter is dry (no way to sample bypass filter)
| 313 X | 29.08 | SWG Old Woman Springs | 2001-03-14 | Liquid | 2 ppm, as Aroclor 1242, 1 ppm as Aroclor 1254
| 313 X | 33.9 | El Vaquaro Tap | 2001-04-16 | Wipe | ND < 1ug/wipe | Sample taken downstream for regulator
R03 | 313 X | 34.34 | Mitsubishi Cement | 2000-02-09 | Liquid | 2 ppm, 3ppm as Aroclor 1260 | Sample taken from bottom of filter (gas flowing 6 mcf / hour)
R03 | 313 X | 34.34 | Mitsubishi Cement | 2000-02-23 | None |  | Filter Dry (check location)
R03 | 313 X | 34.34 | Mitsubishi Cement | 2000-02-24 | Liquid | 3 ppm, 3ppm as Aroclor 1254 | Sample from meter set
R03 | 313 X | 34.34 | Mitsubishi Cement | 2000-03-08 | Liquid | 4 ppm as Aroclor 1016, 3ppm as Aroclor 1260 | Sample from meter set
R03 | 313 X | 34.34 | Mitsubishi Cement | 2000-03-20 | Liquid | 2 ppm as Aroclor 1016, 3ppm as Aroclor 1260 | Sample from meter set
R03 | 313 X | 34.34 | Mitsubishi Cement | 2000-04-05 | Liquid | 3 ppm as Aroclor 1016, 3ppm as Aroclor 1254 | Sample from meter set
R03 | 313 X | 34.34 | Mitsubishi Cement | 2000-04-05 | Liquid | 1 ppm as Aroclor 1016, 3ppm as Aroclor 1254 | Sample from meter set
R03 | 313 X | 34.34 | Mitsubishi Cement | 2000-04-27 | Liquid | 7 ppm as Aroclor 1016, 2 ppm as Aroclor 1254 | Sampled Labeled as "Big Bear B" at MP 34.34
R03 | 313 X | 34.34 | Mitsubishi Cement | 2000-05-01 | Liquid | 1 ppm as Aroclor 1016, 3 ppm as Aroclor 1254
R03 | 313 X | 34.34 | Mitsubishi Cement | 2000-05-15 | Liquid | 2 ppm as Aroclor 1016, 4 ppm as Aroclor 1254
R03 | 313 X | 34.34 | Mitsubishi Cement | 2000-05-30 | Liquid | 3 ppm as Aroclor 1016, 3 ppm as Aroclor 1254
R03 | 313 X | 34.34 | Mitsubishi Cement | 2000-06-13 | Liquid | 4 ppm as Aroclor 1016, 3 ppm as Aroclor 1260
R03 | 313 X | 34.34 | Mitsubishi Cement | 2000-07-24 | Liquid | 1 ppm as Aroclor 1016, 0.6 ppm as Aroclor 1260 | < 10 mls
R03 | 313 X | 34.34 | Mitsubishi Cement | 2000-08-08 | None |  | Meter set dry
R03 | 313 X | 34.34 | Mitsubishi Cement | 2000-08-21 | Liquid | ND < 1 ppm | < 10 mls
R03 | 313 X | 34.34 | Mitsubishi Cement | 2000-09-05 | Liquid | ND < 1 ppm | < 10 mls
R03 | 313 X | 34.34 | Mitsubishi Cement | 2000-09-18 | Liquid | ND < 3 ppm | < 10 mls (reporting limit raised because of small sample size)
R03 | 313 X | 34.34 | Mitsubishi Cement | 2000-10-04 | Liquid | 42 ppm | < 10 mls
R03 | 313 X | 34.34 | Mitsubishi Cement | 2000-12-04 | Liquid | 6 ppm as Aroclor 1016, 3 ppm as Aroclor 1260 | < 10 mls
R03 | 313 X | 34.34 | Mitsubishi Cement | 2001-01-03 | Liquid | 2 ppm as Aroclor 1242, 2 ppm as Aroclor 1254 | < 10 mls
R03 | 313 X | 34.34 | Mitsubishi Cement | 2001-02-02 | Liquid | 2 ppm as Aroclor 1016 | < 10 mls
R03 | 313 X | 34.34 | Mitsubishi Cement | 2001-03-02 | Liquid | <5 ppm | < 10 mls (no oil in separator)
R03 | 313 X | 34.34 | Mitsubishi Cement | 2001-06-25 | Liquid | 4 ppm as Aroclor 1242, 3 ppm as Aroclor 1254 | ~ 10 mls (no oil in separator)
R03 | 313 X | 34.34 | Mitsubishi Cement | 2001-07-09 | None |  | sample received broken
R03 | 313 X | 34.34 | Mitsubishi Cement | 2001-08-27 | None | ND < 1 ppm | < 10 mls (trace)
R03 | 313 X | 34.34 | Mitsubishi Cement | 2001-09-24 | None | < 10 ppm | (trace) Reporting Limit Raised - insufficient sample
| 314 X | 0.02 | Company Use |  |  |  | Tap not Inspected or sampled (Hinkley Tap)
| 314 X | 0.06 | SW Gas (Hinkley Tap) |  |  |  | Tap not Inspected or sampled
| 314 X | 8.76 | SW Gas (Zackey Farms) |  |  |  | Tap not inspected or sampled
| 314 X | 21.76 | SW Gas (La Delta, Helendale) |  |  |  | Tap not Inspected or sampled (San Joaquin Div. job)
R05 | 314 X | 24.31 | TXI Riverside Cement PLS | 2000-02-09 | None |  | Active filter next to Valve 4. Bottom tap of filter is dry. Note: Clearance reqrd. for filter removal and wipe sampling
R05 | 314 X | 24.31 | TXI Riverside Cement PLS | 2000-08-21 | None |  | no liquids
R05 | 314 X | 24.31 | TXI Riverside Cement PLS | 2000-09-06 | None |  | no liquids
R05 | 314 X | 24.31 | TXI Riverside Cement PLS | 2000-09-18 | None |  | no liquids
R05 | 314 X | 24.31 | TXI Riverside Cement PLS | 2000-10-04 | None |  | no liquids
R05 | 314 X | 24.31 | TXI Riverside Cement PLS | 2001-01-03 | None |  | no liquids
R05 | 314 X | 24.31 | TXI Riverside Cement PLS | 2001-02-02 | None |  | no liquids
R05 | 314 X | 24.31 | TXI Riverside Cement PLS | 2001-03-02 | None |  | no liquids
R05 | 314 X | 24.31 | TXI Riverside Cement PLS | 2001-07-09 | Liquid |  | Insufficient sample
H16 | 314 X | 24.72 | Oro Grande - Victorville F | 2000-05-14 | Liquid | 35 ppm | Feeds Oro Grande Township
H16 | 314 X | 24.72 | Oro Grande - Victorville F | 2000-05-30 | Liquid | 6 ppm
H16 | 314 X | 24.72 | Oro Grande - Victorville F | 2000-06-14 | Liquid | 11 ppm
H16 | 314 X | 24.72 | Oro Grande - Victorville F | 2000-06-29 | Liquid | 10 ppm
H16 | 314 X | 24.72 | Oro Grande - Victorville F | 2000-07-29 | None |  | Filter was dry
H16 | 314 X | 24.72 | Oro Grande - Victorville F | 2000-08-21 | Liquid | 16 ppm
H16 | 314 X | 24.72 | Oro Grande - Victorville F | 2000-10-02 | Liquid | 21 ppm | < 10 mls
H16 | 314 X | 24.72 | Oro Grande - Victorville F | 2000-10-26 | Liquid | 46 ppm | < 10 mls
H16 | 314 X | 24.72 | Oro Grande - Victorville F | 2000-11-20 | Liquid | 16 ppm | < 10 mls
H16 | 314 X | 24.72 | Oro Grande - Victorville F | 2000-12-18 | Liquid | 15 ppm | < 10 mls
H16 | 314 X | 24.72 | Oro Grande - Victorville F | 2001-01-23 | Liquid | 16 ppm | < 10 mls
H16 | 314 X | 24.72 | Oro Grande - Victorville F | 2001-02-22 | Liquid | 20 ppm as Aroclor 1242 | < 10 mls
H16 | 314 X | 24.72 | Oro Grande - Victorville F | 2001-04-25 | Liquid | 4 ppm as Aroclor 1242 | ~ 10 mls
H16 | 314 X | 24.72 | Oro Grande - Victorville F | 2001-05-25 | Liquid | 13 ppm as Aroclor 1242 | ~ 10 mls
H16 | 314 X | 24.72 | Oro Grande - Victorville F | 2001-06-25 | Liquid | 6 ppm as Aroclor 1242 | ~ 10 mls
H16 | 314 X | 24.72 | Oro Grande - Victorville F | 2001-07-09 | Liquid | 8 ppm as Aroclor 1242 | ~ 10 mls
H16 | 314 X | 24.72 | Oro Grande - Victorville F | 2001-08-27 | Liquid | 6 ppm as Aroclor 1242 | ~ 10 mls
H16 | 314 X | 24.72 | Oro Grande - Victorville F | 2001-09-24 | Liquid | 5 ppm as Aroclor 1242 | ~ 10 mls
H16 | 314 X | 24.72 | Oro Grande - Victorville F | 2001-10-22 | Liquid | 6 ppm as Aroclor 1242 | < 10 mls (trace)
| 314 X | 24.75 | TXI Riverside Tap Meter | 2000-02-09 | Liquid | 16 ppm, 4ppm as Aroclor 1260 | Sample taken from bottom of turbine meter - small amount of liquid
| 314 X | 24.75 | TXI Riverside Tap Meter | 2000-02-15 | Liquid | 9 ppm
| 314 X | 24.75 | TXI Riverside Tap Meter | 2000-02-23 | Liquid | 19 ppm as Aroclor 1016, 5 ppm as Aroclor 1254
| 314 X | 24.75 | TXI Riverside Tap Meter | 2000-03-08 | Liquid | 45 ppm
| 314 X | 24.75 | TXI Riverside Tap Meter | 2000-03-22 | Liquid | 11 ppm
| 314 X | 24.75 | TXI Riverside Tap Meter | 2000-04-05 | Liquid | 24 ppm as Aroclor 1016, 7 ppm as Aroclor 1254
| 314 X | 24.75 | TXI Riverside Tap Meter | 2000-04-18 | Liquid | 22 ppm, 5 ppm as Aroclor 1260
| 314 X | 24.75 | TXI Riverside Tap Meter | 2000-05-01 | Liquid | 6 ppm
| 314 X | 24.75 | TXI Riverside Tap Meter | 2000-05-15 | Liquid | 5 ppm, 2 ppm as Aroclor 1254 | Bottom inside Meter
| 314 X | 24.75 | TXI Riverside Tap Meter | 2000-05-15 | Liquid | < 1 ppm | Top of inside meter
| 314 X | 24.75 | TXI Riverside Tap Meter | 2000-05-30 | Liquid | 31 ppm, 3 ppm as Aroclor 1254 | Bottom inside Meter
| 314 X | 24.75 | TXI Riverside Tap Meter | 2000-06-12 | Liquid | 34 ppm, 3 ppm as Aroclor 1254
| 314 X | 24.75 | TXI Riverside Tap Meter | 2000-06-26 | Liquid | 30 ppm, 3 ppm as Aroclor 1254
| 314 X | 24.75 | TXI Riverside Tap Meter | 2000-07-24 | Liquid | 26 ppm, 2.5 ppm as Aroclor 1254 | < 10 mls
| 314 X | 24.75 | TXI Riverside Tap Meter | 2000-08-08 | Liquid | 40 ppm, 12 ppm as Aroclor 1254 | < 10 mls
| 314 X | 24.75 | TXI Riverside Tap Meter | 2000-08-21 | Liquid | 25 ppm, 14 ppm as Aroclor 1254 | < 10 mls
| 314 X | 24.75 | TXI Riverside Tap Meter | 2000-09-05 | Liquid | 16 ppm, 6 ppm as Aroclor 1254 | < 10 mls
| 314 X | 24.75 | TXI Riverside Tap Meter | 2000-09-18 | Liquid | 20 ppm, 3 ppm as Aroclor 1260 | < 10 mls
| 314 X | 24.75 | TXI Riverside Tap Meter | 2000-10-04 | Liquid | 22 ppm, 4 ppm as Aroclor 1254 | < 10 mls
| 314 X | 24.75 | TXI Riverside Tap Meter | 2000-11-03 | Liquid | 19 ppm, 3.5 ppm as Aroclor 1254 | < 10 mls
| 314 X | 24.75 | TXI Riverside Tap Meter | 2000-12-04 | Liquid | 22 ppm, 6 ppm as Aroclor 1254 | < 10 mls
| 314 X | 24.75 | TXI Riverside Tap Meter | 2001-01-03 | Liquid | 19 ppm as Aroclor 1242, 7 ppm as Aroclor 1254 | < 10 mls
| 314 X | 24.75 | TXI Riverside Tap Meter | 2001-02-01 | Liquid | 29 ppm as Aroclor 1016, 24 ppm as Aroclor 1254 | < 10 mls
| 314 X | 24.75 | TXI Riverside Tap Meter | 2001-03-02 | Liquid | 16 ppm as Aroclor 1242, 3 ppm as Aroclor 1254 | < 10 mls (no oil in separator)
| 314 X | 24.75 | TXI Riverside Tap Meter (Separator) | 2001-03-02 | Liquid | ND<5 ppm | < 10 mls (oil in separator - detection limit raised due to insufficient sample)
| 314 X | 25.2 | SW Gas (Academy Road) |  |  |  | Tap not Inspected or sampled (San Joaquin Div. job)
| 314 X | 26 | SW Gas (Clanton) |  |  |  | Tap not Inspected or sampled (San Joaquin Div. job)
| 314 X | 26.8 | None |  |  |  | Tap not inspected or sampled (4" valve installed on original const. for SWG - capped)
| 314 X | 27.46 | Victorville "B" Meter (Airbase Road) | 2000-02-15 | Liquid | 5 ppm
| 314 X | 27.46 | Victorville "B" Meter | 2000-07-15 | Liquid | 3.5 ppm as Aroclor 1016, 0.6 ppm as Aroclor 1260
| 314 X | 27.46 | Victorville "B" Meter | 2001-03-14 | Liquid | 4 ppm, as Aroclor 1242 | ~10 mls
| 314 X | 28.76 | Southwest Portland Cement |  |  |  | Tap not inspected or sampled - Original Construction
| 314 X | 30.5 | Stoddard Wells Tap |  |  |  | Tap not inspected or sampled
H18 | 314 X | 34.34 | Big Bear "B" | 2000-02-09 | None |  | Two filters; both are dry
H18 | 314 X | 34.34 | Big Bear "B" | 2000-04-27 | Liquid | 7 ppm as Aroclor 1016, 2 ppm as Aroclor 1254
H18 | 314 X | 34.34 | Big Bear "B" | 05/14/00. | Liquid | 38 ppm as Aroclor 1016, 3 ppm as Aroclor 1254 | Sample from meter set
H18 | 314 X | 34.34 | Big Bear "B" | 2000-05-30 | Liquid | 6 ppm as Aroclor 1016, 2 ppm as Aroclor 1254
H18 | 314 X | 34.34 | Big Bear "B" | 2000-06-14 | Liquid | 16 ppm as Aroclor 1016, 2 ppm as Aroclor 1260
H18 | 314 X | 34.34 | Big Bear "B" | 2000-06-29 | Liquid | 16 ppm as Aroclor 1016, 3 ppm as Aroclor 1254
H18 | 314 X | 34.34 | Big Bear "B" | 2000-07-29 | Liquid | 15 ppm as Aroclor 1016, 2 ppm as Aroclor 1254
H18 | 314 X | 34.34 | Big Bear "B" | 2000-08-18 | Liquid | 16 ppm as Aroclor 1016, 2 ppm as Aroclor 1260
H18 | 314 X | 34.34 | Big Bear "B" | 2000-09-05 | Liquid | 16 ppm as Aroclor 1016, 3 ppm as Aroclor 1254 | ~20 mls
H18 | 314 X | 34.34 | Big Bear "B" | 2000-09-18 | Liquid | 17 ppm as Aroclor 1016, 3 ppm as Aroclor 1254 | ~20 mls
H18 | 314 X | 34.34 | Big Bear "B" | 2000-10-02 | Liquid | 15 ppm as Aroclor 1016, 2.4 ppm as Aroclor 1254 | ~10 mls
H18 | 314 X | 34.34 | Big Bear "B" | 2000-10-26 | Liquid | 13.2 ppm as Aroclor 1016, 2.4 ppm as Aroclor 1254 | ~10 mls
H18 | 314 X | 34.34 | Big Bear "B" | 2000-11-20 | Liquid | 7.2 ppm as Aroclor 1016, 2.6 ppm as Aroclor 1254 | ~10 mls
H18 | 314 X | 34.34 | Big Bear "B" | 2000-12-18 | Liquid | 5 ppm as Aroclor 1016, 2 ppm as Aroclor 1254 | ~10 mls
H18 | 314 X | 34.34 | Big Bear "B" | 2001-01-23 | Liquid | 7 ppm as Aroclor 1242 | <10 mls
H18 | 314 X | 34.34 | Big Bear "B" | 2001-02-22 | Liquid | 16 ppm as Aroclor 1242, 7 ppm as Aroclor 1260 | <10 mls
H18 | 314 X | 34.34 | Big Bear "B" | 2001-03-14 | Liquid | 5 ppm as Aroclor 1242 | <10 mls
H18 | 314 X | 34.34 | Big Bear "B" | 2001-04-25 | Liquid | 6 ppm as Aroclor 1242, 1 ppm as Aroclor 1254 | ~15 mls
H18 | 314 X | 34.34 | Big Bear "B" | 2001-05-24 | Liquid | 31 ppm as Aroclor 1242 | ~20 mls
H18 | 314 X | 34.34 | Big Bear "B" | 2001-06-25 | Liquid | 16 ppm as Aroclor 1242, 2 ppm, as Aroclor 1254 | ~20 mls
H18 | 314 X | 34.34 | Big Bear "B" | 2001-07-09 | Liquid | 19 ppm as Aroclor 1242, 4 ppm, as Aroclor 1254 | <10 mls
H18 | 314 X | 34.34 | Big Bear "B" | 2001-08-27 | Liquid | 23 ppm as Aroclor 1242, 14 ppm, as Aroclor 1254 | ~10 mls
H18 | 314 X | 34.34 | Big Bear "B" | 2001-09-29 | Liquid | 25 ppm as Aroclor 1242, 17 ppm, as Aroclor 1254 | <10 mls
H18 | 314 X | 34.34 | Big Bear "B" | 2001-10-22 | Liquid | No result | <10 mls (insufficient sample)
| 314 X | 38.57 | Victorville "C" SWG | 2000-02-09 | None |  | Two filters; both are dry
| 314 X | 38.57 | Victorville "C" Meter | 2000-02-17 | Liquid | 5 ppm as Aroclor 1016, 4 ppm, as Aroclor 1254
| 314 X | 38.57 | Victorville "C" Meter | 2000-03-22 | Liquid | 3 ppm, as Aroclor 1254
R04 | 314 X | 43.18 | Black Mountain Cement | 2000-02-09 | None |  | Meter tap is dry. Filter on low flow run is dry
R04 | 314 X | 43.18 | Black Mountain Cement | 2000-03-23 | Liquid | 0.2 ppm as Aroclor 1016, 0.8 ppm, as Aroclor 1254 | Sample from Filter
R04 | 314 X | 43.18 | Black Mountain Cement | 2000-03-23 | Wipe | 2 ug /wipe as Aroclor 1254 | semi-quantitative wipe inside filter canister
R04 | 314 X | 43.18 | Black Mountain Cement | 2000-04-05 | Wipe | 2 ug /wipe as Aroclor 1254 | semi-quantitative wipe inside filter canister
R04 | 314 X | 43.18 | Black Mountain Cement | 2000-03-23 | Liquid | 3 ppm as Aroclor 1254 | Sample from Filter
R04 | 314 X | 43.18 | Black Mountain Cement | 2000-05-01 | Liquid |  | Insufficient Sample
R04 | 314 X | 43.18 | Black Mountain Cement | 2000-05-15 | Solid | < 1 ppm | Dust from Filter
R04 | 314 X | 43.18 | Black Mountain Cement | 2000-07-24 | None |  | Filter
R04 | 314 X | 43.18 | Black Mountain Cement | 2000-08-21 | Wipe | ND < 1ug/100cm2
R04 | 314 X | 43.18 | Black Mountain Cement | 2000-09-06 | None |  | No liquids
R04 | 314 X | 43.18 | Black Mountain Cement | 2000-09-18 | None |  | No liquids
R04 | 314 X | 43.18 | Black Mountain Cement | 2000-10-04 | None |  | No liquids
R04 | 314 X | 43.18 | Black Mountain Cement | 2000-11-03 | None |  | No liquids
R04 | 314 X | 43.18 | Black Mountain Cement | 2001-01-03 | None |  | No liquids
R04 | 314 X | 43.18 | Black Mountain Cement | 2001-05-01 | Liquid | ND <1 ppm | Liquid from separator
R04 | 314 X | 43.18 | Black Mountain Cement | 2001-07-09 | None |  | sample received broken
R06 | 372 X (Line 311 branch) | 3.7 | R.C. Primary Reg. Station | 2000-05-04 | Wipe | ND < 1ug/100cm2 | Ridgecrest primary filter
R06 | 372 X (Line 311 branch) | 3.7 | R.C. Primary Reg. Station | 2000-05-16 | Wipe | ND < 1ug/100cm2 | Ridgecrest primary filter
R06 | 372 X (Line 311 branch) | 3.7 | R.C. Primary Reg. Station | 2000-05-16 | Liquid | < 1 ppm | Ridgecrest primary, liquid taken from orifice meter
R06 | 372 X (Line 311 branch) | 3.7 | R.C. Primary Reg. Station | 2000-08-21 | None |  | Filter Dry
R06 | 372 X (Line 311 branch) | 3.7 | R.C. Primary Reg. Station | 2000-10-02 | None |  | Filter Dry
R06 | 372 X (Line 311 branch) | 3.7 | R.C. Primary Reg. Station | 2001-01-02 | None |  | Filter Dry
R06 | 372 X (Line 311 branch) | 3.7 | R.C. Primary Reg. Station | 2001-04-27 | Wipe | < 1 ug/100 cm2 | Filter Dry
R06 | 372 X (Line 311 branch) | 3.7 | R.C. Primary Reg. Station | 2001-07-09 | None |  | Filter Dry
R06 | 372 X (Line 311 branch) | 3.7 | R.C. Primary Reg. Station | 2001-10-01 | None |  | Filter Dry

## Kettleman District 2000
Sample Point Code | LINE | Mile Point | Description | Sample Date | Sample Type | Result (All results as Aroclor 1016 unless otherwise noted) | Comments
| 111 | N/A | Helm Junction Tap | 2001-03-07 | Liquid | ND < 1 ppm | < 10 mls from filter tap
| 138 | 14.71 | Fed to Selma, Fowler, Fresno | 2001-03-07 | Liquid | ND < 1 ppm | < 10 mls from bottom tap inlet to orifice meter
K13 | 142 | 1.28 | Gosford and White Road tap | 2000-05-27 | Liquid | 1 ppm
K13 | 142 | 1.28 | Gosford and White Road tap | 2000-06-02 | Liquid | 2 ppm
K13 | 142 | 1.28 | Gosford and White Road tap | 2000-07-13 | Liquid | 2 ppm
K13 | 142 | 1.28 | Gosford and White Road tap | 2000-07-23 | None |  | Dry
K13 | 142 | 1.28 | Gosford and White Road tap | 2000-08-10 | None |  | insufficient sample
K13 | 142 | 1.28 | Gosford and White Road tap | 2000-09-08 | None |  | insufficient sample
K13 | 142 | 1.28 | Gosford and White Road tap | 2000-09-21 | Liquid | 2 ppm | < 10 ml
K13 | 142 | 1.28 | Gosford and White Road tap | 2000-10-05 | Liquid | 2 ppm | < 10 ml
K13 | 142 | 1.28 | Gosford and White Road tap | 2000-10-20 | Liquid | 2 ppm | < 10 ml
K13 | 142 | 1.28 | Gosford and White Road tap | 2000-11-09 | Liquid | 3 ppm | < 10 ml?
K13 | 142 | 1.28 | Gosford and White Road tap | 2000-12-08 | Liquid | 2 ppm | < 10 ml
K13 | 142 | 1.28 | Gosford and White Road tap | 2001-01-09 | Liquid | 2 ppm | < 10 ml
K13 | 142 | 1.28 | Gosford and White Road tap | 2001-03-06 | Liquid | 4 ppm as Aroclor 1242 | < 10 ml
K13 | 142 | 1.28 | Gosford and White Road tap | 2001-04-10 | Liquid | 3 ppm as Aroclor 1242 | < 10 ml
K13 | 142 | 1.28 | Gosford and White Road tap | 2001-05-15 | Liquid | 3 ppm as Aroclor 1242 | < 10 ml
K13 | 142 | 1.28 | Gosford and White Road tap | 2001-06-06 | Liquid | 3 ppm as Aroclor 1242 | < 10 ml
K13 | 142 | 1.28 | Gosford and White Road tap | 2001-07-11 | Trace | 4 ppm as Aroclor 1242 | < 10 mls (trace)
K13 | 142 | 1.28 | Gosford and White Road tap | 2001-08-08 | Trace | 4 ppm as Aroclor 1242 | < 10 mls (trace)
K13 | 142 | 1.28 | Gosford and White Road tap | 2001-09-06 | Trace | 3 ppm as Aroclor 1242 | < 10 mls (trace)
K13 | 142 | 1.28 | Gosford and White Road tap | 2001-10-09 | Trace | 3 ppm as Aroclor 1242 | < 10 mls (trace)
K13 | 142 | 1.28 | Gosford and White Road tap | 2001-11-08 | Trace | 2 ppm as Aroclor 1242 | < 10 mls (trace)
K14 | 142 | 4.3 | White Lane and Wible | 2000-07-23 | None |  | Dry
K14 | 142 | 4.3 | White Lane and Wible | 2000-08-10 | None |  | Dry
K14 | 142 | 4.3 | White Lane and Wible | 2000-09-08 | None |  | Dry
K14 | 142 | 4.3 | White Lane and Wible | 2000-10-05 | None |  | Dry
K16 | 142 | 11.47 | Bakersfield Tap off Line 300 A | 2000-07-13 | None
K16 | 142 | 11.47 | Bakersfield Tap | 2000-07-23 | Trace |  | Insufficient sample
K15 | 142 | 14.05 | Bakersfield Reg. Station | 2000-07-27 | Liquid | 3 ppm
K15 | 142 | 14.05 | Bakersfield Reg. Station | 2000-08-10 | Trace |  | Insufficient sample
K15 | 142 | 14.05 | Bakersfield Reg. Station | 2000-09-08 | Liquid | 4 ppm | <10 mls
K15 | 142 | 14.05 | Bakersfield Reg. Station | 2000-10-05 | None |  | Dry
| 300 A | 256.21 A | PLS4A Insertion Meter | 2000-02-17 | Wipe | ND < 0.7 ug/100cm2 | Took wipe samples on same surfaces as was done on Line 300 B PLS 2X Insertion Meter (MP 130.39 B)
| 300 A | 256.21 A | PLS4A tap | 2001-03-07 | Liquid | ND < 1 ppm | ~ 30 mls
| 300 A | 260.50 A | Arvin Cotton Gin |  | None |  | Tap not inspected or sampled
| 300 A | 267.26 A | Costerisan Farms |  | None |  | Tap not inspected or sampled
| 300 A | 269.05 A | Shafter School and Others |  | None |  | Tap not inspected or sampled
| 300 A | 270.74 A | Kern Delta Gin (new) | 2000-02-17 | None |  | Took wipe samples on same surfaces as was done on Line 300 B PLS 2x Insertion Meter (MP 130.39 B). Note: wipe sample accidentally dropped in meter pit.
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-03-22 | Liquid | 2 ppm
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-04-06 | Liquid | 3 ppm
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-04-12 | Liquid | 3 ppm
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-04-26 | Liquid | 1 ppm
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-05-04 | Liquid | 2 ppm
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-05-10 | Liquid | 2 ppm
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-05-26 | Liquid | 1 ppm
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-05-31 | Liquid | 2 ppm
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-06-07 | Liquid | 2 ppm
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-06-14 | Liquid | 2 ppm
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-06-21 | Liquid | 2 ppm
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-06-29 | Liquid | 3 ppm
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-07-07 | Liquid | 2 ppm
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-07-19 | Liquid | 2 ppm
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-07-27 | Liquid | 3 ppm
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-08-01 | Liquid | 2 ppm
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-08-10 | Liquid | 1 ppm | ~100 mls.
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-08-16 | Liquid | 2 ppm
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-08-24 | Liquid | 3 ppm | ~75 mls
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-08-30 | Liquid | 4 ppm | ~100 mls.
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-09-07 | Liquid | 2 ppm | ~125 mls
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-09-14 | Liquid | 3 ppm | ~125 mls
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-09-20 | Liquid | 2 ppm | ~100 mls.
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-09-28 | Liquid | 2 ppm | ~80 mls.
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-10-05 | Liquid | 2 ppm | ~125 mls
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-10-20 | Liquid | 2 ppm | ~100 mls
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-11-06 | Liquid | 3 ppm | ~95 mls
K05 | 300 A | 280.58 A | Kern River Intake Header | 2000-12-09 | Liquid | 3 ppm | ~80 mls
K05 | 300 A | 280.58 A | Kern River Intake Header | 2001-01-10 | Liquid | 2 ppm | < 10 mls
K05 | 300 A | 280.58 A | Kern River Intake Header | 2001-02-07 | Liquid | ND<1 ppm | < 25 mls
K05 | 301 A | 280.58 A | Kern River Intake Header | 2001-03-07 | Liquid | <2 ppm | < 25 mls
K05 | 301 A | 280.58 A | Kern River Intake Header | 2001-05-16 | Liquid | 2 ppm | < 10 mls
K05 | 301 A | 280.58 A | Kern River Intake Header | 2001-06-07 | Liquid | 3 ppm | ~ 25 mls
K05 | 301 A | 280.58 A | Kern River Intake Header | 2001-07-12 | Trace | 3 ppm as Aroclor 1242 | < 10 mls (trace)
K05 | 301 A | 280.58 A | Kern River Intake Header | 2001-08-08 | Liquid | 7 ppm as Aroclor 1242 | ~ 75 mls
K05 | 301 A | 280.58 A | Kern River Intake Header | 2001-09-07 | Liquid | 5 ppm as Aroclor 1242 | ~ 10 mls
K05 | 301 A | 280.58 A | Kern River Intake Header | 2001-10-15 | Liquid | 4 ppm as Aroclor 1242 | ~ 30 mls
K05 | 301 A | 280.58 A | Kern River Intake Header | 2001-11-08 | Liquid | 4 ppm as Aroclor 1242 | ~ 80 mls
K06 | 300 A | 280.58 A | Kern River Discharge Header | 2000-04-06 | Liquid | 2 ppm
K06 | 300 A | 280.58 A | Kern River Discharge Header | 2000-05-04 | Liquid | 2 ppm
K06 | 300 A | 280.58 A | Kern River Discharge Header | 2000-05-17 | Liquid | 2 ppm
K06 | 300 A | 280.58 A | Kern River Discharge Header | 2000-08-10 | None |  | Dry
K06 | 300 A | 280.58 A | Kern River Discharge Header | 2000-08-24 | None |  | Dry
K06 | 300 A | 280.58 A | Kern River Discharge Header | 2000-09-20 | None |  | Dry
K06 | 300 A | 280.58 A | Kern River Discharge Header | 2000-09-28 | None |  | Dry
K06 | 300 A | 280.58 A | Kern River Discharge Header | 2001-05-16 | None |  | Dry
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-02-16 | Liquid | < 1 ppm
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-03-22 | Liquid | < 1 ppm
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-04-06 | Liquid | 3 ppm
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-04-12 | Liquid | 4 ppm
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-04-19 | Liquid | 2 ppm
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-04-26 | Liquid | 1 ppm
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-05-04 | Liquid | 2 ppm
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-05-10 | Liquid | 2 ppm
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-05-17 | Liquid | 2 ppm
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-05-26 | Liquid | 1 ppm
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-05-31 | Liquid | 1 ppm
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-06-07 | Liquid | 2 ppm
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-06-14 | Liquid | 2 ppm
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-06-21 | Liquid | 2 ppm
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-06-29 | Liquid | 2 ppm
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-07-07 | Liquid | 2 ppm
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-07-19 | Liquid | 2 ppm
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-07-27 | Liquid | 3 ppm
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-08-01 | Liquid | 2 ppm
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-08-10 | Liquid | 3 ppm | 90 mls (one run in service part of the week)
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-08-16 | Liquid | 2 ppm
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-08-24 | Liquid | 3 ppm | ~75 mls
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-08-30 | Liquid | 2 ppm | ~75 mls
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-09-07 | Liquid | 2 ppm | ~ 80 mls
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-09-14 | Liquid | 3 ppm | ~125 mls
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-09-20 | Liquid | 2 ppm | ~100 mls.
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-09-28 | Liquid | 2 ppm | ~70 mls.
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-10-05 | Liquid | 2 ppm | ~60 mls.
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-10-20 | Liquid | 2 ppm | ~25 mls.
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2000-11-06 | Liquid | 3 ppm | ~25 mls.
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2001-02-07 | Liquid | 2 ppm | ~30 mls.
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2001-03-07 | Liquid | 2 ppm as Aroclor 1242 | < 10 mls
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2001-05-16 | Liquid | 3 ppm as Aroclor 1242 | ~ 10 mls
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2001-06-07 | Liquid | 4 ppm as Aroclor 1242 | ~ 15 mls (station shut-in)
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2001-07-12 | Liquid | 6 ppm as Aroclor 1242 | ~ 25 mls
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2001-08-08 | Trace | 5 ppm as Aroclor 1242 | < 10 mls (trace)
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2001-09-07 | Trace | 4 ppm as Aroclor 1242 | < 10 mls (trace)
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2001-10-15 | Trace | 5 ppm as Aroclor 1242 | ~15 mls
K07 | 300 A | 280.58 A | Kern River Tap Valve 1 | 2001-11-08 | Trace | 4 ppm as Aroclor 1242 | ~10 mls
K08 | 301 A | 280.58 A | Kern River Tap Valve 2 | 2001-02-08 | Liquid | 3 ppm | ~30 mls.
K08 | 301 A | 280.58 A | Kern River Tap Valve 2 | 2001-03-07 | Liquid | 2 ppm as Aroclor 1242 | < 10 mls
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-02-16 | Liquid | ND <1 ppm
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-03-22 | Liquid | <1 ppm
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-04-06 | Liquid | 1 ppm
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-04-12 | Liquid | 4 ppm
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-04-26 | Liquid | 1 ppm
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-05-04 | Liquid | 2 ppm
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-05-10 | Liquid | 2 ppm
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-05-17 | Liquid | 2 ppm
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-05-31 | Liquid | 1 ppm
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-06-07 | Liquid | 2 ppm
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-06-14 | Liquid | 2 ppm
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-06-29 | Liquid | 2 ppm
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-07-07 | Liquid | 2 ppm
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-07-19 | Liquid | 2 ppm
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-07-27 | Liquid | 3 ppm
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-08-01 | Liquid | 1 ppm
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-08-10 | Liquid | 2 ppm | 75 mls (one run in service part of the week)
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-08-16 | Liquid | 3 ppm
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-08-24 | Liquid | 2 ppm | ~35 mls
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-08-30 | Liquid | 3 ppm | ~30 mls
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-09-07 | Liquid | 2 ppm | ~ 80 mls
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-09-14 | Liquid | 2 ppm | ~100 mls
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-09-20 | Liquid | 2 ppm | ~100 mls
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-09-28 | Liquid | 2 ppm | ~25 mls
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-10-05 | Liquid | 2 ppm | ~20 mls
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-10-20 | Liquid | 2 ppm | ~10 mls
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-11-06 | Liquid | 3 ppm | ~15 mls
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2000-12-09 | Liquid | 3 ppm | ~75 mls
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2001-01-10 | Liquid | 2 ppm | ~75 mls
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2001-02-07 | Liquid | 3 ppm | ~25 mls
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2001-05-16 | Liquid | 2 ppm | ~10 mls
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2001-06-07 | Liquid | 3 ppm | ~10 mls (station shut-in)
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2001-07-12 | Liquid | 5 ppm as Aroclor 1242 | < 10 mls (trace)
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2001-08-08 | Liquid | 3 ppm as Aroclor 1242 | < 10 mls (trace)
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2001-09-07 | Liquid | 2 ppm as Aroclor 1242 | < 10 mls (trace)
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2001-10-15 | Liquid | 3 ppm as Aroclor 1242 | < 10 mls (trace)
K08 | 300 A | 280.58 A | Kern River Tap Valve 2 | 2001-11-08 | Liquid | 4 ppm as Aroclor 1242 | < 10 mls (trace)
| 300 A | 284.69 A | Bakersfield Tap, L-142N |  | None |  | Tap not inspected or sampled
| 300 A | 285.36 A | Superior Road Tap | 2000-02-17 | Liquid | ND < 1 ppm
| 300 A | 285.36 A | Superior Road Tap | 2000-03-22 | Liquid | ND < 1 ppm
| 300 A | 288.98 A | M.L. Sheffield |  | None |  | Tap not inspected or sampled
| 300 A | 299.0 A | PLS-5 A | 2001-03-07 | Liquid | ND < 1 ppm | ~125 mls
| 300 A | 300.53 A | M. Riccomini |  | None |  | Tap not inspected or sampled
| 300 A | 308.26 A | Semitropic Water District |  | None |  | Tap not inspected or sampled
| 300 A | 323.36 A | Shell Midway Pump Station | 2000-02-17 | None |  | No liquid in filter
| 300 A | 344.52 A | Watson Realty Co. |  | None |  | Tap not inspected or sampled
| 300 A | 344.76 A | Watson Realty Co. |  | None |  | Tap not inspected or sampled
| 300 A | 345.71 A | Shell Kettleman Pump Station |  | None |  | Tap not inspected or sampled
| 300 A | 352.61 A | S.C. Gas |  | None |  | Tap not inspected or sampled
| 300 A | 364.11 A | Line 190 |  | None |  | Tap not inspected or sampled
| 300 A | 368.92 A | Harris Ranch Development |  | None |  | Tap not inspected or sampled
| 300 A | 371.81 A | Line 164 |  | None |  | Tap not inspected or sampled
| 300 A | 371.81 A | Line 164 |  | None |  | Tap not inspected or sampled
| 300 A | 371.85 A | Coalinga |  | None |  | Tap not inspected or sampled
| 300 A | 372.44 A | Harris Feed Lot |  | None |  | Tap not inspected or sampled
| 300 A | 373.68 A | Harris Farms |  | None |  | Tap not inspected or sampled
| 300 A | 378.65 A | Helm Tap Line 138 |  | None |  | Tap not inspected or sampled
| 300 A | 393.53 A | Panoche Junction |  | None |  | Tap not inspected or sampled
| 300 A | Comp Plt. | Plant Fuel |  | None |  | Tap not inspected or sampled
| 300 B | 231.27 B | Monolith Cement Plant, So. Cal Gas |  | None |  | Line not flowing gas. Tap not inspected or sampled.
| 300 B | 244.00 B | Bear Valley Springs |  | None |  | Tap not inspected or sampled
K11 | 300 B | 245.69 B | Bear Valley Springs | 2000-03-02 | Liquid | 1 ppm | San Juan and Martindale
K11 | 300 B | 245.69 B | Bear Valley Springs | 2000-04-20 | Liquid | 1 ppm | San Juan and Martindale
K11 | 300 B | 245.69 B | Bear Valley Springs | 2000-06-02 | None |  | San Juan and Martindale
K11 | 300 B | 245.69 B | Bear Valley Springs | 2000-06-15 | None |  | San Juan and Martindale
K11 | 300 B | 245.69 B | Bear Valley Springs | 2000-06-29 | None |  | San Juan and Martindale
K11 | 300 B | 245.69 B | Bear Valley Springs | 2000-07-23 | None |  | San Juan and Martindale
K11 | 300 B | 245.69 B | Bear Valley Springs | 2000-08-10 | None |  | San Juan and Martindale
K11 | 300 B | 245.69 B | Bear Valley Springs | 2000-09-08 | None |  | San Juan and Martindale
K11 | 300 B | 245.69 B | Bear Valley Springs | 2000-10-05 | None |  | San Juan and Martindale
K11 | 300 B | 245.69 B | Bear Valley Springs | 2000-12-08 | Liquid | 2 ppm | < 10 mls, San Juan and Martindale
K11 | 300 B | 245.69 B | Bear Valley Springs | 2001-01-09 | Liquid | 3 ppm | < 10 mls, San Juan and Martindale
K11 | 300 B | 245.69 B | Bear Valley Springs | 2001-02-08 | Liquid | 4 ppm as Aroclor 1242 | < 10 mls, San Juan and Martindale
K11 | 301 B | 245.69 B | Bear Valley Springs | 2001-03-06 | Liquid | 3 ppm as Aroclor 1242 | < 10 mls, San Juan and Martindale
K11 | 301 B | 245.69 B | Bear Valley Springs | 2001-04-10 | Liquid | 3 ppm as Aroclor 1242 | < 10 mls, San Juan and Martindale
K11 | 301 B | 245.69 B | Bear Valley Springs | 2001-05-15 | Liquid | 5 ppm as Aroclor 1242 | < 10 mls, San Juan and Martindale
K11 | 301 B | 245.69 B | Bear Valley Springs | 2001-06-05 | Liquid | 5 ppm as Aroclor 1242 | < 10 mls, San Juan and Martindale
K11 | 301 B | 245.69 B | Bear Valley Springs | 2001-07-11 | Trace | 5 ppm as Aroclor 1242 | < 10 mls (trace)
K11 | 301 B | 245.69 B | Bear Valley Springs | 2001-08-08 | Trace | 5 ppm as Aroclor 1242 | < 10 mls (trace)
| 300 B | 245.91 B | Bear Valley Springs | 2000-06-30 | None
| 300 B | 247.18 B | Bear Valley Springs | 2000-09-08 | None |  | Tap not inspected or sampled
| 300 B | 256.64 B | PLS-4 B | 2001-03-07 | Liquid | ND < 1 ppm | ~ 50 mls
K09 | 300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-02-17 | Liquid | ND < 25 | First sample filter was dry; second sample filter was dry. Watery sample was obtained from Camron Valve body. Sample reporting limit was raised to low surrogate spike QC recovery caused by low sample volume.
K09 | 300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-03-22 | Liquid | ND < 1ppm
K09 | 300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-02-17 | Wipe | ND < 1 ug | Drip located in sub-surface vault box. Small amount of liquid / sludge was obtained.
K09 | 300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-06-21 | Liquid | 2 ppm
K09 | 300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-07-23 | None |  | Dry
K09 | 300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-08-10 | None |  | Dry
K09 | 300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-10-05 | None |  | Dry
| 300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-06-29 | None |  | Dry
| 300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-07-23 | None |  | Dry
| 300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-08-10 | None |  | Dry
| 300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-09-08 | None |  | Dry
| 300 B | 257.26 B | Sycamore Canyon Golf Course Meter Set - Kenneth Frick Ranch Tap | 2000-10-05 | None |  | Dry
| 300 B | 257.52 B | Kenmore Road |  | None |  | Tap not inspected or sampled
| 300 B | 268.05 B | Costerian Farms |  | None |  | Tap not inspected or sampled
| 300 B | 269.45 B | Union Ave. Tap |  | None
| 300 B | 269.45 B | Union Ave. Tap | 2001-03-06 | Liquid | 6 ppm as Aroclor 1242 | < 10 mls
| 300 B | 270.50 B | Beechor Cattle and Feed |  | None |  | Tap not inspected or sampled
| 300 B | 271.31 B | S.C. Gas |  | None |  | Tap not inspected or sampled
| 300 B | 273.06 B | Stine Rd. | 2000-02-17 | None |  | No liquid in filter
| 300 B | 273.06 B | Stine Rd. | 2000-06-30 | None
| 300 B | 273.06 B | Stine Rd. | 2001-03-06 | Liquid | 3 ppm | ~ 30 mls
| 300 B | 273.06 B | Rudnick Cattle Co. |  | None |  | Tap not inspected or sampled
| 300 B | 273.06 B | Rudnick Cattle Co. | 2000-08-21 | None | 1 ppm
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-02-17 | Liquid | < 1 ppm | Small amount of liquid and sludge obtained (~< 5 mls)
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-03-08 | Liquid | 1 ppm
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-04-06 | Liquid | 1 ppm
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-04-19 | Liquid | 1 ppm
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-05-10 | Liquid | 2 ppm
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-05-26 | Liquid | 1 ppm
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-06-07 | Liquid | <1 ppm
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-07-20 | Liquid | 2 ppm
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-07-27 | Liquid | 2 ppm
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-08-01 | Liquid | 2 ppm
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-08-10 | Liquid | 2 ppm | 50 mls.
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-08-16 | Liquid | 2 ppm
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-08-24 | Liquid | 2 ppm | ~ 30 mls
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-08-30 | Liquid | 2 ppm | ~ 75 mls
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-09-07 | Liquid | 2 ppm | ~10 mls
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-09-14 | Liquid | 2 ppm | <10 mls
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-09-20 | None |  | < 10 mls (Dry)
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-09-28 | Liquid | 2 ppm | < 10 mls (Dry)
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-10-05 | Liquid | 1 ppm | < 10 mls (trace)
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-10-20 | Liquid | 1 ppm | < 10 mls (trace)
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-11-06 | Liquid | 2 ppm | ~ 110 mls
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2000-12-09 | Liquid | 2 ppm | ~ 100 mls
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2001-01-10 | Liquid | 2 ppm | ~ 30 mls
K04 | 300 B | 273.50 B | Ridgeview High School Drip | 2001-02-07 | Liquid | 2 ppm | ~ 75 mls
K04 | 301 B | 273.50 B | Ridgeview High School Drip | 2001-03-07 | Liquid | 2 ppm as Aroclor 1242 | < 10 mls
K04 | 301 B | 273.50 B | Ridgeview High School Drip | 2001-05-16 | Liquid | 1 ppm as Aroclor 1242 | < 10 mls (mist)
K04 | 301 B | 273.50 B | Ridgeview High School Drip | 2001-06-07 | Liquid | 3 ppm as Aroclor 1242 | ~ 10 mls
K04 | 301 B | 273.50 B | Ridgeview High School Drip | 2001-07-12 | Liquid | 6 ppm as Aroclor 1242 | < 10 mls (trace)
K04 | 301 B | 273.50 B | Ridgeview High School Drip | 2001-08-08 | Liquid | 5 ppm as Aroclor 1242 | < 10 mls (mist)
K04 | 301 B | 273.50 B | Ridgeview High School Drip | 2001-09-07 | Liquid | 4 ppm as Aroclor 1242 | < 10 mls (mist)
K04 | 301 B | 273.50 B | Ridgeview High School Drip | 2001-10-15 | Liquid | 4 ppm as Aroclor 1242 | < 10 mls (mist)
K04 | 301 B | 273.50 B | Ridgeview High School Drip | 2001-11-08 | Liquid | 3 ppm as Aroclor 1242 | ~ 10 mls
| 300 B | 274.00 B | Line 300 B Drip | 2000-03-22 | Liquid | 1 ppm
| 300 B | 274.00 B | Line 300 B Drip | 2000-05-31 | Liquid | 1 ppm
| 300 B | 274.00 B | Line 300 B Drip | 2000-06-30 | Liquid | 1 ppm
| 300 B | 275.86 B | Gosford Road, D/S reg. | 2000-02-16 | Liquid | ND < 12 | Reporting limit raised due to interfering matrix
K03 | 300 B | 275.86 B | Gosford Road North Filter Outlet | 2000-02-16 | Liquid | ND < 2 ppm | Line 142 South, small amount of liquid taken downstream of regulator
K03 | 300 B | 275.86 B | Gosford Road North Filter Outlet | 2000-07-23 | None |  | Dry
K03 | 300 B | 275.86 B | Gosford Road North Filter Outlet | 2000-08-10 | None |  | Dry
K03 | 300 B | 275.86 B | Gosford Road North Filter Outlet | 2000-08-21 | None |  | Dry
K03 | 300 B | 275.86 B | Gosford Road North Filter Outlet | 2000-09-08 | None |  | Dry
K03 | 300 B | 275.86 B | Gosford Road North Filter Outlet | 2000-09-21 | Liquid | 4 ppm | ~10 mls
K03 | 300 B | 275.86 B | Gosford Road North Filter Outlet | 2000-10-05 | None |  | Dry
K03 | 300 B | 275.86 B | Gosford Road North Filter Outlet | 2000-10-20 | Liquid | 4 ppm | <10 mls
K03 | 300 B | 275.86 B | Gosford Road North Filter Outlet | 2000-11-09 | Liquid | 4 ppm | <10 mls?
K03 | 300 B | 275.86 B | Gosford Road North Filter Outlet | 2000-12-08 | Liquid | 3 ppm | ~ 70 mls
K03 | 300 B | 275.86 B | Gosford Road North Filter Outlet | 2001-01-09 | Liquid | 3 ppm | ~ 15mls
K03 | 300 B | 275.86 B | Gosford Road North Filter Outlet | 2001-02-08 | Liquid | 5 ppm as Aroclor 1242 | ~ 10 mls
K03 | 301 B | 275.86 B | Gosford Road North Filter Outlet | 2001-03-06 | Liquid | 6 ppm as Aroclor 1242 | ~ 10 mls
K03 | 301 B | 275.86 B | Gosford Road North Filter Outlet | 2001-04-10 | Liquid | 5 ppm as Aroclor 1242 | ~ 50 mls
K03 | 301 B | 275.86 B | Gosford Road North Filter Outlet | 2001-05-15 | Liquid | 5 ppm as Aroclor 1242 | < 10 mls
K03 | 301 B | 275.86 B | Gosford Road North Filter Outlet | 2001-06-05 | Liquid | 8 ppm as Aroclor 1242 | < 10 mls
K03 | 301 B | 275.86 B | Gosford Road North Filter Outlet | 2001-07-11 | Trace | 12 ppm as Aroclor 1242 | < 10 mls (trace)
K03 | 301 B | 275.86 B | Gosford Road North Filter Outlet | 2001-08-08 | Trace | 9 ppm as Aroclor 1242 | < 10 mls (trace)
K03 | 301 B | 275.86 B | Gosford Road North Filter Outlet | 2001-09-06 | Trace | 5 ppm as Aroclor 1242 | < 10 mls (trace)
K03 | 301 B | 275.86 B | Gosford Road North Filter Outlet | 2001-10-09 | Trace | 4 ppm as Aroclor 1242 | < 10 mls (trace)
K03 | 301 B | 275.86 B | Gosford Road North Filter Outlet | 2001-11-08 | Trace | 6 ppm as Aroclor 1242 | < 10 mls (trace)
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-02-16 | Liquid | ND < 1 ppm | Liquid obtained from Outlet Valve V-1 drain, Run M-1
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-04-06 | Liquid | 6 ppm
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-04-20 | Liquid | 3 ppm
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-06-30 | Liquid | 3 ppm
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-05-04 | Liquid | 2 ppm
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-06-02 | Liquid | 3 ppm
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-06-15 | Liquid | 4 ppm
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-06-29 | None
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-07-23 | Liquid | 6 ppm
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-07-27 | Liquid | 7 ppm
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-08-10 | Liquid | 8 ppm | ~ 50 mls
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-08-24 | Liquid | 4 ppm | ~ 25 mls
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-04-06 | Liquid | 2 ppm
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-04-06 | Liquid | < 1 ppm
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-05-04 | Liquid | 2 ppm
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-05-18 | Liquid | 2 ppm
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-06-02 | Liquid | 3 ppm
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-06-15 | Liquid | 2 ppm
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-06-29 | None
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-07-13 | Liquid | 2 ppm
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-08-10 | Liquid | 3 ppm | < 10 mls (bottom of filter was wet)
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-08-24 | Liquid | 4 ppm | ~25 mls
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-09-08 | Liquid | 2 ppm | ~50 -75 mls
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-09-21 | Liquid | 4 ppm | ~25 mls
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-10-05 | Liquid | 2 ppm | ~25 mls
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-10-20 | Liquid | 4 ppm | ~25 mls
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-11-09 | Liquid | 4 ppm | ~25 mls?
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2000-12-08 | Liquid | 3 ppm | ~25 mls?
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2001-01-09 | Liquid | 4 ppm | ~50 mls
K02 | 300 B | 275.86 B | Gosford Road South Filter Outlet | 2001-02-08 | Liquid | 4 ppm | ~40 mls
K02 | 301 B | 275.86 B | Gosford Road South Filter Outlet | 2001-03-06 | Liquid | 6 ppm as Aroclor 1242 | ~25 mls
K02 | 301 B | 275.86 B | Gosford Road South Filter Outlet | 2001-04-10 | Liquid | 4 ppm as Aroclor 1242 | ~50 mls
K02 | 301 B | 275.86 B | Gosford Road South Filter Outlet | 2001-05-15 | Liquid | 6 ppm as Aroclor 1242 | ~25 mls
K02 | 301 B | 275.86 B | Gosford Road South Filter Outlet | 2001-06-06 | Liquid | 11 ppm as Aroclor 1242 | < 10 mls
K02 | 301 B | 275.86 B | Gosford Road South Filter Outlet | 2001-07-11 | Trace | 9 ppm as Aroclor 1242 | < 10 mls (trace)
K02 | 301 B | 275.86 B | Gosford Road South Filter Outlet | 2001-08-08 | Trace | 11 ppm as Aroclor 1242 | <10 mls (trace)
K02 | 301 B | 275.86 B | Gosford Road South Filter Outlet | 2001-10-09 | Trace | 5 ppm as Aroclor 1242 | <10 mls (trace)
K02 | 301 B | 275.86 B | Gosford Road South Filter Outlet | 2001-11-08 | Trace | 6 ppm as Aroclor 1242 | ~10 mls (trace)
| 300 B | 275.87 B | Gosford Reg Station | 2000-03-15 | Liquid | 2 ppm | ~50 mls
| 300 B | 278.31 B | S.C. Gas |  | None |  | Tap not inspected or sampled
| 300 B | 278.31 B | S.C. Gas | 2000-06-30 | None |  | Tap not inspected or sampled
| 300 B | 280.69 B | Kern Bellview Well |  | None |  | Tap not inspected or sampled - tap is retired
| 300 B | 284.62 B | Bakersfield Tap, L-142N | 2000-02-17 | None |  | No suitable location to sample (Jr. fittings on orifice plates)
| 300 B | 288.42 B | Buttonwillow Intertie - SoCal Gas | 2000-02-17 | None |  | Reg. filter was dry
| 300 B | 295.02 B | Getty Oil | 2000-02-17 | None |  | Tap not inspected or sampled
| 300 B | 299.00 B | PLS-5 B | 2001-03-07 | Liquid | ND < 1 ppm | ~125 mls
| 300 B | 305.94 B | Mettler Semi-Tropic Farm |  | None |  | Tap not inspected or sampled (may be capped?)
| 300 B | 306.34 B | (Falcon Well #1) L-300B |  | None |  | Tap not inspected or sampled (may be capped)
| 300 B | 308.67 B | Semitropic school | 2000-02-17 | None |  | Reg. Filter was dry
| 300 B | 309.63 B | Hartley Natural Resources |  | None |  | Tap not inspected or sampled
| 300 B | 344.78 B | Westlake #1 |  | None |  | Tap not inspected or sampled
| 300 B | 345.02 B | Tulare Lake |  | None |  | Husky Oil - Tap not inspected or sampled
| 300 B | 345.95 B | Kettlemen City |  | None |  | Tap not inspected or sampled
| 300 B | 347.01 B | Couture Farms |  | None |  | Tap is capped
| 300 B | 353.0 B | Kettlemen Compressor Station Intake | 2000-04-04 | Liquid | < 1ppm
| 300 B | 353.0 B | Kettlemen Compressor Station Intake | 2000-06-01 | Liquid | < 1ppm
| 300 B | 353.0 B | Kettlemen Compressor Station C Bank Scrubber | 2000-04-20 | Liquid | < 1ppm
| 300 B | 353.0 B | Kettlemen Compressor Station C Bank Scrubber | 2000-06-27 | Liquid | < 1ppm
| 300 B | 353.0 B | Kettlemen Compressor Station C Bank Scrubber | 2000-12-18 | Liquid | 2 ppm
| 300 B | 353.0 B | Kettlemen Compressor Station C Bank Scrubber | 2001-01-11 | Liquid | 1 ppm
| 300 B | 353.0 B | Kettlemen Compressor Station C Bank Scrubber | 2001-02-01 | Liquid | 3 ppm as Aroclor 1242
| 301 B | 353.0 B | Kettlemen Compressor Station C Bank Scrubber | 2001-03-12 | Liquid | 1 ppm as Aroclor 1242
| 301 B | 353.0 B | Kettlemen Compressor Station Intake | 2001-09-10 | Liquid | ND < 1 ppm
| 300 B | 353.80 B | Calorimeter & Domestic Cust. Kettlemen |  | None |  | Tap not inspected or sampled
| 300 B | 355.15 B | Kochergen Farms |  | None |  | Capped on an emergency basis
| 300 B | 358.90 B | Line 300 B Drip | 2000-05-10 | Liquid | 1 ppm
| 300 B | 362.73 B | City of Huron |  | None |  | Tap not inspected or sampled
| 300 B | 363.89 B | Line 190 |  | None |  | Tap not inspected or sampled
| 300 A | 367.62 B | Giffen Farms |  | None |  | Tap not inspected or sampled
| 300 A | 367.62 B | Giffen Farms |  | None |  | Tap not inspected or sampled
| 300 A | 367.62 B | Giffen Farms |  | None |  | Tap not inspected or sampled
| 300 B | 372.72 B | Harris Feeding Co. |  | None |  | Tap not inspected or sampled
| 300 B | 372.72 B | Harris Feeding Co. |  | None |  | Tap not inspected or sampled
| 300 B | 373.49 B | Harris Feeding Co. |  | None |  | Tap not inspected or sampled
| 300 B | 373.49 B | Harris Feeding Co. |  | None |  | Tap not inspected or sampled
| 300 B | 376.01 B | Harris Ranch |  | None |  | Tap not inspected or sampled
| 300 B | 378.78 B | Helm Tap Line 138 |  | None |  | Tap not inspected or sampled
| 300 B | 385.40 B | Getty Oil and Three Rocks |  | None |  | Tap not inspected or sampled
| 300 B | 393.76 B | Panoche Junction |  | None |  | Tap not inspected or sampled
| 300 B |  | Coalinga Line 164 |  | None |  | Tap not inspected or sampled
| 306 X | 70.02 | Morro Bay Primary | 2001-03-21 | Liquid | < 1 ppm | Drip Tank
| 307 X | N/A | Spreckels Sugar Plant (Line 307 begins at Panoche Tap | 2001-03-07 | Liquid | < 1 ppm | ~ 20 mls from bottom of filter - Liquid clear in color
38.57
54.88
54.88
54.88
54.88
54.88
54.88
54.88
54.88
54.88
54.88
54.88
54.88
54.88
54.88
54.88
54.88
54.88
54.88
54.88
Meter set dry
Filter was dry
2000-08-21
Clay Mine Rd Reg.
No volume recorded
Tap not inspected or sampled - Original Construction

## MOJAVE Filter Separator
Sample Point Code | LINE | Mile Point | Description | Sample Date | Sample Type | Result (All results as Aroclor 1016 unless otherwise noted) | Comments
H19 | 300 A | 218.69 A | F/S C-1 A Inlet | 2000-07-26 | Liquid | 1.5 ppm as Aroclor 1016, 0.4 ppm as Aroclor 1260 | F/S sump1/2 full
H19 | 300 A | 218.69 A | F/S C-1 A Inlet | 2000-08-16 | Liquid | 2 ppm
H19 | 300 A | 218.69 A | F/S C-1 A Inlet | 2000-09-06 | Liquid | 2 ppm
H19 | 300 A | 218.69 A | F/S C-1 A Inlet | 2000-09-18 | Liquid | 2 ppm
H19 | 300 A | 218.69 A | F/S C-1 A Inlet | 2000-10-02 | Liquid | 3 ppm
H19 | 300 A | 218.69 A | F/S C-1 A Inlet | 2000-10-16 | Liquid | 3 ppm
H19 | 300 A | 218.69 A | F/S C-1 A Inlet | 2000-10-26 | Liquid | 2 ppm
H19 | 300 A | 218.69 A | F/S C-1 A Inlet | 2000-11-20 | Liquid | 3 ppm
H19 | 300 A | 218.69 A | F/S C-1 A Inlet | 2000-12-18 | Liquid | 2 ppm as Aroclor 1242
H19 | 300 A | 218.69 A | F/S C-1 A Inlet | 2001-01-22 | Liquid | 4 ppm as Aroclor 1242
H19 | 300 A | 218.69 A | F/S C-1 A Inlet | 2001-02-22 |  |  | Sample bottle received broken
H19 | 301 A | 218.69 A | F/S C-1 A Inlet | 2001-03-14 | Liquid | 6 ppm as Aroclor 1242
H19 | 301 A | 218.69 A | F/S C-1 A Inlet | 2001-04-25 | Liquid | 4 ppm as Aroclor 1242
H19 | 301 A | 218.69 A | F/S C-1 A Inlet | 2001-05-23 | Liquid | 4 ppm as Aroclor 1242
H19 | 301 A | 218.69 A | F/S C-1 A Inlet | 2001-06-26 | Liquid | 3 ppm as Aroclor 1242
H19 | 301 A | 218.69 A | F/S C-1 A Inlet | 2001-07-09 | Liquid | 5 ppm as Aroclor 1242
H19 | 301 A | 218.69 A | F/S C-1 A Inlet | 2001-08-27 | Liquid | 3 ppm as Aroclor 1242
H19 | 301 A | 218.69 A | F/S C-1 A Inlet | 2001-09-24 | Liquid | 3 ppm as Aroclor 1242
H19 | 301 A | 218.69 A | F/S C-1 A Inlet | 2001-10-22 | Liquid | 2 ppm as Aroclor 1242
H20 | 300 A | 218.69 A | F/S C-1 B Outlet | 2000-07-26 | Liquid | 2 ppm | F/S sump1/2 full
H20 | 300 A | 218.69 A | F/S C-1 B Outlet | 2000-08-16 | Liquid | 2 ppm
H20 | 300 A | 218.69 A | F/S C-1 B Outlet | 2000-09-06 | Liquid | 2 ppm
H20 | 300 A | 218.69 A | F/S C-1 B Outlet | 2000-09-18 | Liquid | 2 ppm
H20 | 300 A | 218.69 A | F/S C-1 B Outlet | 2000-10-02 | Liquid | 3 ppm
H20 | 300 A | 218.69 A | F/S C-1 B Outlet | 2000-10-16 | Liquid | 3 ppm
H20 | 300 A | 218.69 A | F/S C-1 B Outlet | 2000-10-26 | Liquid | 2 ppm
H20 | 300 A | 218.69 A | F/S C-1 B Outlet | 2000-11-20 | Liquid | 4 ppm
H20 | 300 A | 218.69 A | F/S C-1 B Outlet | 2000-12-18 | Liquid | 3 ppm as Aroclor 1242
H20 | 300 A | 218.69 A | F/S C-1 B Outlet | 2001-01-22 | Liquid | 4 ppm as Aroclor 1242
H20 | 300 A | 218.69 A | F/S C-1 B Outlet | 2001-02-21 | Liquid | 5 ppm as Aroclor 1242
H20 | 301 A | 218.69 A | F/S C-1 B Outlet | 2001-03-01 | Liquid | 5 ppm as Aroclor 1242
H20 | 301 A | 218.69 A | F/S C-1 B Outlet | 2001-04-25 | Liquid | 3 ppm as Aroclor 1242
H20 | 301 A | 218.69 A | F/S C-1 B Outlet | 2001-05-23 | Liquid | 4 ppm as Aroclor 1242
H20 | 301 A | 218.69 A | F/S C-1 B Outlet | 2001-06-26 | Liquid | 14ppm as Aroclor 1242
H20 | 301 A | 218.69 A | F/S C-1 B Outlet | 2001-07-09 | Liquid | 5 ppm as Aroclor 1242
H20 | 301 A | 218.69 A | F/S C-1 B Outlet | 2001-08-27 | Liquid | 3 ppm as Aroclor 1242
H20 | 301 A | 218.69 A | F/S C-1 B Outlet | 2001-09-24 | Liquid | 3 ppm as Aroclor 1242
H20 | 301 A | 218.69 A | F/S C-1 B Outlet | 2001-10-22 | Liquid | 3 ppm as Aroclor 1242
H21 | 300 A | 218.69 A | F/S C-2 A Inlet | 2000-07-26 | Liquid | 2 ppm | F/S sump full
H21 | 300 A | 218.69 A | F/S C-2 A Inlet | 2000-08-16 | Liquid | 2 ppm
H21 | 300 A | 218.69 A | F/S C-2 A Inlet | 2000-09-06 | Liquid | 3 ppm
H21 | 300 A | 218.69 A | F/S C-2 A Inlet | 2000-09-18 | Liquid | 2 ppm
H21 | 300 A | 218.69 A | F/S C-2 A Inlet | 2000-10-02 | Liquid | 2 ppm
H21 | 300 A | 218.69 A | F/S C-2 A Inlet | 2000-10-16 | Liquid | 2 ppm
H21 | 300 A | 218.69 A | F/S C-2 A Inlet | 2000-11-20 | Liquid | 3 ppm
H21 | 300 A | 218.69 A | F/S C-2 A Inlet | 2000-12-18 | Liquid | 2 ppm
H21 | 300 A | 218.69 A | F/S C-2 A Inlet | 2001-01-22 | Liquid | 2 ppm
H21 | 300 A | 218.69 A | F/S C-2 A Inlet | 2001-02-21 | Liquid | 6 ppm
H21 | 300 A | 218.69 A | F/S C-2 A Inlet | 2001-02-28 | Liquid | 7 ppm
H21 | 301 A | 218.69 A | F/S C-2 A Inlet | 2001-03-14 | Liquid | 8 ppm as Aroclor 1242
H21 | 301 A | 218.69 A | F/S C-2 A Inlet | 2001-04-25 | Liquid | 2 ppm as Aroclor 1242
H21 | 301 A | 218.69 A | F/S C-2 A Inlet | 2001-05-23 | Liquid | 4 ppm as Aroclor 1242
H21 | 301 A | 218.69 A | F/S C-2 A Inlet | 2001-07-09 | Liquid | 7 ppm as Aroclor 1242
H21 | 301 A | 218.69 A | F/S C-2 A Inlet | 2001-08-27 | Liquid | 3 ppm as Aroclor 1242
H21 | 301 A | 218.69 A | F/S C-2 A Inlet | 2001-09-24 | Liquid | 4 ppm as Aroclor 1242
H21 | 301 A | 218.69 A | F/S C-2 A Inlet | 2001-10-22 | Liquid | 4 ppm as Aroclor 1242
H22 | 300 A | 218.69 A | F/S C-2 B Outlet | 2000-07-26 | Liquid | 3 ppm | F/S sump 1/2 full
H22 | 300 A | 218.69 A | F/S C-2 B Outlet | 2000-08-16 | Liquid | 2 ppm
H22 | 300 A | 218.69 A | F/S C-2 B Outlet | 2000-09-06 | Liquid | 3 ppm
H22 | 300 A | 218.69 A | F/S C-2 B Outlet | 2000-09-18 | Liquid | 3 ppm
H22 | 300 A | 218.69 A | F/S C-2 B Outlet | 2000-10-02 | Liquid | 2 ppm
H22 | 300 A | 218.69 A | F/S C-2 B Outlet | 2000-10-16 | Liquid | 4 ppm
H22 | 300 A | 218.69 A | F/S C-2 B Outlet | 2000-10-26 | Liquid | 3 ppm
H22 | 300 A | 218.69 A | F/S C-2 B Outlet | 2000-11-20 | Liquid | 4 ppm
H22 | 300 A | 218.69 A | F/S C-2 B Outlet | 2000-12-18 | Liquid | 3 ppm
H22 | 300 A | 218.69 A | F/S C-2 B Outlet | 2001-01-22 | Liquid | 5 ppm
H22 | 300 A | 218.69 A | F/S C-2 B Outlet | 2001-02-21 | Liquid | 4 ppm
H22 | 300 A | 218.69 A | F/S C-2 B Outlet | 2001-02-28 | Liquid | 7 ppm
H22 | 301 A | 218.69 A | F/S C-2 B Outlet | 2001-03-14 | Liquid | 6 ppm as Aroclor 1242
H22 | 301 A | 218.69 A | F/S C-2 B Outlet | 2001-04-25 | Liquid | 4 ppm as Aroclor 1242
H22 | 301 A | 218.69 A | F/S C-2 B Outlet | 2001-05-23 | Liquid | 5 ppm as Aroclor 1242
H22 | 301 A | 218.69 A | F/S C-2 B Outlet | 2001-06-26 | Liquid | 5 ppm as Aroclor 1242
H22 | 301 A | 218.69 A | F/S C-2 B Outlet | 2001-07-09 | Liquid | 7 ppm as Aroclor 1242
H22 | 301 A | 218.69 A | F/S C-2 B Outlet | 2001-08-27 | Liquid | 4 ppm as Aroclor 1242
H22 | 301 A | 218.69 A | F/S C-2 B Outlet | 2001-10-22 | Liquid | 3 ppm
H22 | 301 A | 218.69 A | F/S C-2 B Outlet | 2001-09-24 | Liquid | 3 ppm as Aroclor 1242
H23 | 300 B | 219.49 B | F/S C-3 A Inlet | 2000-07-26 | Liquid | 2 ppm | F/S sump full
H23 | 300 B | 219.49 B | F/S C-3 A Inlet | 2000-08-16 | Liquid | 2 ppm
H23 | 300 B | 219.49 B | F/S C-3 A Inlet | 2000-09-06 | Liquid | 3 ppm
H23 | 300 B | 219.49 B | F/S C-3 A Inlet | 2000-09-18 | Liquid | 2 ppm
H23 | 300 B | 219.49 B | F/S C-3 A Inlet | 2000-10-02 | Liquid | 2 ppm
H23 | 300 B | 219.49 B | F/S C-3 A Inlet | 2000-10-16 | Liquid | 3 ppm
H23 | 300 B | 219.49 B | F/S C-3 A Inlet | 2000-10-26 | Liquid | 2 ppm
H23 | 300 B | 219.49 B | F/S C-3 A Inlet | 2000-11-20 | Liquid | 3 ppm
H23 | 300 B | 219.49 B | F/S C-3 A Inlet | 2000-12-18 | Liquid | 2 ppm
H23 | 300 B | 219.49 B | F/S C-3 A Inlet | 2001-01-22 | Liquid | 4 ppm
H23 | 300 B | 219.49 B | F/S C-3 A Inlet | 2001-02-21 | Liquid | 5 ppm
H23 | 300 B | 219.49 B | F/S C-3 A Inlet | 2001-02-22 | Liquid | 6 ppm
H23 | 300 B | 219.49 B | F/S C-3 A Inlet | 2001-03-14 | Liquid | 4 ppm as Aroclor 1242
H23 | 300 B | 219.49 B | F/S C-3 A Inlet | 2001-04-25 | Liquid | 2 ppm as Aroclor 1242
H23 | 300 B | 219.49 B | F/S C-3 A Inlet | 2001-05-23 | Liquid | 2 ppm as Aroclor 1242
H23 | 300 B | 219.49 B | F/S C-3 A Inlet | 2001-06-26 | Liquid | 2 ppm as Aroclor 1242
H23 | 300 B | 219.49 B | F/S C-3 A Inlet | 2001-07-09 | Liquid | 8 ppm as Aroclor 1242
H23 | 300 B | 219.49 B | F/S C-3 A Inlet | 2001-08-27 | Liquid | 2 ppm as Aroclor 1242
H23 | 300 B | 219.49 B | F/S C-3 A Inlet | 2001-09-24 | Liquid | 2 ppm as Aroclor 1242
H23 | 300 B | 219.49 B | F/S C-3 A Inlet | 2001-09-24 | Liquid | 2 ppm as Aroclor 1242
H24 | 300 B | 219.49 B | F/S C-3 B Outlet | 2000-07-26 | Liquid | 1 ppm | F/S sump full
H24 | 300 B | 219.49 B | F/S C-3 B Outlet | 2000-08-16 | Liquid | 1 ppm
H24 | 300 B | 219.49 B | F/S C-3 B Outlet | 2000-09-06 | Liquid | 2 ppm
H24 | 300 B | 219.49 B | F/S C-3 B Outlet | 2000-09-18 | Liquid | 2 ppm
H24 | 300 B | 219.49 B | F/S C-3 B Outlet | 2000-10-03 | Liquid | 2 ppm
H24 | 300 B | 219.49 B | F/S C-3 B Outlet | 2000-10-16 | Liquid | 2 ppm
H24 | 300 B | 219.49 B | F/S C-3 B Outlet | 2000-10-26 | Liquid | 3 ppm
H24 | 300 B | 219.49 B | F/S C-3 B Outlet | 2000-11-20 | Liquid | 4 ppm
H24 | 300 B | 219.49 B | F/S C-3 B Outlet | 2000-12-18 | Liquid | 3 ppm
H24 | 300 B | 219.49 B | F/S C-3 B Outlet | 2000-01-22 | Liquid | 5 ppm
H24 | 300 A | 218.69 A | F/S C-3 B Outlet | 2001-02-22 |  |  | Sample bottle received broken
H24 | 301 A | 218.69 A | F/S C-3 B Outlet | 2001-03-14 | Liquid | 5 ppm as Aroclor 1242
H24 | 301 A | 218.69 A | F/S C-3 B Outlet | 2001-04-25 | Liquid | 2 ppm as Aroclor 1242
H24 | 301 A | 218.69 A | F/S C-3 B Outlet | 2001-05-23 | Liquid | 2 ppm as Aroclor 1242
H24 | 301 A | 218.69 A | F/S C-3 B Outlet | 2001-06-24 | Liquid | 2 ppm as Aroclor 1242
H24 | 301 A | 218.69 A | F/S C-3 B Outlet | 2001-07-09 | Liquid | 8 ppm as Aroclor 1242
H24 | 301 A | 218.69 A | F/S C-3 B Outlet | 2001-08-27 | Liquid | 2 ppm as Aroclor 1242
H24 | 301 A | 218.69 A | F/S C-3 B Outlet | 2001-09-24 | Liquid | 2 ppm as Aroclor 1242
H24 | 301 A | 218.69 A | F/S C-3 B Outlet | 2001-10-22 | Liquid | 2 ppm as Aroclor 1242
H25 | 300 B | 219.49 B | F/S C-4 A Inlet | 2000-07-26 | Liquid | 1 ppm | F/S sump full
H25 | 300 B | 219.49 B | F/S C-4 A Inlet | 2000-08-16 | Liquid | 1 ppm
H25 | 300 B | 219.49 B | F/S C-4 A Inlet | 2000-09-06 | Liquid | 2 ppm
H25 | 300 B | 219.49 B | F/S C-4 A Inlet | 2000-09-18 | Liquid | 1 ppm
H25 | 300 B | 219.49 B | F/S C-4 A Inlet | 2000-10-02 | Liquid | 2 ppm
H25 | 300 B | 219.49 B | F/S C-4 A Inlet | 2000-10-16 | Liquid | 2 ppm
H25 | 300 B | 219.49 B | F/S C-4 A Inlet | 2000-10-26 | Liquid | 2 ppm
H25 | 300 B | 219.49 B | F/S C-4 A Inlet | 2000-11-20 | Liquid | 2 ppm
H25 | 300 B | 219.49 B | F/S C-4 A Inlet | 2000-12-18 | Liquid | 2 ppm
H25 | 300 B | 219.49 B | F/S C-4 A Inlet | 2001-01-22 | Liquid | 3 ppm
H25 | 300 B | 219.49 B | F/S C-4 A Inlet | 2001-02-21 | Liquid | 4 ppm
H25 | 301 B | 219.49 B | F/S C-4 A Inlet | 2001-03-14 | Liquid | 4 ppm as Aroclor 1242
H25 | 301 B | 219.49 B | F/S C-4 A Inlet | 2001-04-25 | Liquid | 3 ppm as Aroclor 1242
H25 | 301 B | 219.49 B | F/S C-4 A Inlet | 2001-05-23 | Liquid | 3 ppm as Aroclor 1242
H25 | 301 B | 219.49 B | F/S C-4 A Inlet | 2001-06-26 | Liquid | 3 ppm as Aroclor 1242
H25 | 301 B | 219.49 B | F/S C-4 A Inlet | 2001-07-09 | Liquid | 6 ppm as Aroclor 1242
H25 | 301 B | 219.49 B | F/S C-4 A Inlet | 2001-08-27 | Liquid | 2 ppm as Aroclor 1242
H25 | 301 B | 219.49 B | F/S C-4 A Inlet | 2001-10-22 | Liquid | 2 ppm as Aroclor 1242
H25 | 301 B | 219.49 B | F/S C-4 A Inlet | 2001-09-24 | Liquid | 2 ppm as Aroclor 1242
H26 | 300 B | 219.49 B | F/S C-4 B Outlet | 2000-07-26 | Liquid | ND <1 ppm | F/S sump 1/2 full
H26 | 300 B | 219.49 B | F/S C-4 B Outlet | 2000-08-16 | Liquid | 2 ppm
H26 | 300 B | 219.49 B | F/S C-4 B Outlet | 2000-09-06 | Liquid | 2 ppm
H26 | 300 B | 219.49 B | F/S C-4 B Outlet | 2000-09-18 | Liquid | 2 ppm
H26 | 300 B | 219.49 B | F/S C-4 B Outlet | 2000-10-02 | Liquid | 1 ppm
H26 | 300 B | 219.49 B | F/S C-4 B Outlet | 2000-10-16 | Liquid | 2 ppm
H26 | 300 B | 219.49 B | F/S C-4 B Outlet | 2000-11-20 | Liquid | 2 ppm
H26 | 300 B | 219.49 B | F/S C-4 B Outlet | 2000-12-18 | Liquid | 2 ppm
H26 | 300 B | 219.49 B | F/S C-4 B Outlet | 2001-01-22 | Liquid | 3 ppm
H26 | 300 B | 219.49 B | F/S C-4 B Outlet | 2001-02-21 | Liquid | 4 ppm
H26 | 301 B | 219.49 B | F/S C-4 B Outlet | 2001-03-14 | Liquid | 4 ppm as Aroclor 1242
H26 | 301 B | 219.49 B | F/S C-4 B Outlet | 2001-04-25 | Liquid | 2 ppm as Aroclor 1242
H26 | 301 B | 219.49 B | F/S C-4 B Outlet | 2001-05-23 | Liquid | 3 ppm as Aroclor 1242
H26 | 301 B | 219.49 B | F/S C-4 B Outlet | 2001-06-26 | Liquid | 3 ppm as Aroclor 1242
H26 | 301 B | 219.49 B | F/S C-4 B Outlet | 2001-07-09 | Liquid | 5 ppm as Aroclor 1242
H26 | 301 B | 219.49 B | F/S C-4 B Outlet | 2001-08-27 | Liquid | 2 ppm as Aroclor 1242
H26 | 301 B | 219.49 B | F/S C-4 B Outlet | 2001-09-24 | Liquid | 2 ppm as Aroclor 1242
H26 | 301 B | 219.49 B | F/S C-4 B Outlet | 2001-10-22 | Liquid | 2 ppm as Aroclor 1242
| 300 A/B | 219.49 B | F/S Waste Tank | 2000-07-26 | Liquid | 2 ppm | All liquids from F/S sumps transferred to waste tank after sampling Tank ~ 1/3 full
| 300 A/B | 219.49 B | F/S Waste Tank | 2000-10-16 | Liquid | 2 ppm
| 300 A/B | 219.49 B | F/S Waste Tank | 2000-10-26 | Liquid | 3 ppm
| 300 A/B | 219.49 B | F/S Waste Tank | 2000-11-20 | Liquid | 3 ppm
| 300 A/B | 219.49 B | F/S Waste Tank | 2000-12-18 | Liquid | 3 ppm
| 300 A/B | 219.49 B | F/S Waste Tank | 2001-01-22 | Liquid | 5 ppm
| 300 A/B | 219.49 B | F/S Waste Tank | 2001-02-28 | Liquid | 7 ppm
| 300 A/B | 219.49 B | F/S Waste Tank | 2001-03-14 | Liquid | 4 ppm as Aroclor 1242
| 300 A/B | 219.49 B | F/S Waste Tank | 2001-03-23 | Liquid | 2 ppm as Aroclor 1242
| 300 A/B | 219.49 B | F/S Waste Tank | 2001-04-25 | Liquid | 2 ppm as Aroclor 1242
| 301 A/B | 219.49 B | F/S Waste Tank | 2001-05-17 | Liquid | 1 ppm as Aroclor 1242
| 301 A/B | 219.49 B | F/S Waste Tank | 2001-07-09 | Liquid | 5 ppm as Aroclor 1242
| 301 A/B | 219.49 B | F/S Waste Tank | 2001-08-27 | Liquid | 2 ppm as Aroclor 1242
| 301 A/B | 219.49 B | F/S Waste Tank | 2001-09-24 | Liquid | 2 ppm as Aroclor 1242
| 301 A/B | 219.49 B | F/S Waste Tank | 2001-10-22 | Liquid | 3 ppm as Aroclor 1242
.
Filter was dry
Clay Mine Rd Reg.
No volume recorded
Tap not inspected or sampled - Original Construction