## UAE
Homestead SC
|  |  |  | Lowell, Mass |  | Plano |  | 6
| units |  |  | 5 |  | 6 |  | 270
|  |  |  | NEPCO |  | Rose-Golden adjusted |  | Golden's Guess
|  |  |  | 2000-04-26 |  | 2000-05-03 |  | 2000-04-17
Project Management
| Home office |  |  | 600670 | 110% | 660737 |  | 720804
| salaried staff |  |  | 778156 | 110% | 855971.6 |  | 947891
| hourly staff |  |  | 161200 | 110% | 177320 |  | 218756
|  |  |  | 1540026 |  | 1694028.6 |  | 1887451
Indirect Costs
Nepco Indirects
| equipment rental |  |  | 50000 | 110% | 55000 |  | 635659
| small tools |  |  | 30000 | 110% | 33000 |  | 254504
| GC other |  |  | 638676 | 110% | 702543.6 |  | 262371
|  |  |  | 718676 |  | 790543.6 |  | 893720
562500
| S/C indirects | [6 empty] | 6750
| salaried staff |  |  | 900610 | 110% | 990671 |  | 0
| hourly staff |  |  | 342633 | 110% | 376896.3 |  | 0
| equipment rental |  |  | 666369 | 110% | 733005.9 |  | 0
| small tools |  |  | 280580 | 110% | 308638 |  | 0
| temp facilities |  |  | 514566 | 110% | 566022.6 |  | 0
| GC other |  |  | 722844 | 110% | 795128.4 |  | 0
| prod loss |  |  | 1068864 | 110% | 1175750.4 |  | 0
| S/C margin |  |  | 1815000 | 110% | 1996500 |  | 0
| tax/bond |  |  | 6750 | 110% | 7425 |  | 0
|  |  |  | 6318216 |  | 6950037.6 |  | 2615504
| Indirect Subtotal |  |  | 7036892 |  | 7740581.2 |  | 2615504
Engineering
| Engr labor |  |  | 697640 | 110% | 767404 |  | 713243
|  |  |  | 697640 |  | 767404 |  | 713243
Procurement
Major Equipment
| CTG's |  |  | 71700000 | 120% | 86040000 |  | 86040000
| Inlet Air Anti-icing |  |  | 1134420 | 120% | 1361304 |  | 0
| Inlet air freight |  |  | 34050 | 120% | 40860 |  | 0
| dual fuel |  |  | 0 |  | 0 |  | 1680000
| CTG freight |  |  | 300000 | 120% | 360000 |  | 600000
|  |  |  | 73168470 |  | 87802164 |  | 88320000
Engineered Equipment
| buildings |  |  | 337500 | 150% | 506250 |  | 393750
| valves and specials |  |  | 329419 | 115% | 378831.85 |  | 384429
| cable |  |  | 187500 | 115% | 215625 |  | 225000
| dry xfmrs |  |  | 12440 | 115% | 14306 |  | 16794
| step-up transformers |  |  | 1953000 | 0% | 3000000 | 345 kV | 2154000
| pwr dist xfrms |  |  | 722528 | 110% | 794780.8 |  | 841032
| 600V MCC |  |  | 104630 | 120% | 125556 |  | 94842
| 600V swgr |  |  | 111005 | 120% | 133206 |  | 94167
| 5kV MCC |  |  | 163135 | 120% | 195762 |  | 185634
| 15kV swgr |  |  | 1043790 | 120% | 1252548 |  | 1260048
| control panel |  |  | 343950 | 115% | 395542.5 |  | 326620
| Hi voltage device |  |  | 49549 | 110% | 54503.9 |  | 46245
| DCS |  |  | 252450 | 110% | 277695 |  | 305550
| UPS |  |  | 20779 | 110% | 22856.9 |  | 25974
| fld mntd instr |  |  | 183812 | 110% | 202193.2 |  | 109940
| CEMS |  |  | 642400 | 120% | 770880 |  | 0
| control valves |  |  | 50625 | 110% | 55687.5 |  | 68875
| pumps |  |  | 216233 | 110% | 237856.3 |  | 271665
| cooling towers |  |  | 792500 | 0% | 0 | cooling towers in chiller | 0
| fin fan coolers |  |  | 325500 | 120% | 390600 |  | 0
| APC equipment |  |  | 6305000 | 0% | 0 |  | 0
| Gas Compression |  |  | 975000 | 0% | 0 |  | 2120000
| fuel gas filter |  |  | 104000 | 120% | 124800 |  | 168000
| chiller |  |  | 4642500 | 0% | 4000000 | based on 6 CTG's at 1700@ | 4600000
| pretreatment |  |  | 0 |  | 0 |  | 620000 | these are recent adds
| first stage RO |  |  | 0 |  | 0 |  | 1260000 | these are recent adds
| water treatment |  |  | 413200 | 170% | 702440 |  | 548100
| FLD/shop vessels |  |  | 387000 | 110% | 425700 |  | 82350
| vendor reps |  |  | 182375 | 110% | 200612.5 |  | 364750
| tank farm |  |  | 0 |  | 0 |  | 2250000
| Oil/water separator |  |  | 36600 | 110% | 40260 |  | 532500
| other |  |  | 182375 | 110% | 200612.5 |  | 566544
|  |  |  | 21070795 |  | 14719105.95 |  | 19916806
Bulk Material
| Bulk Material |  |  | 3563752 | 115% | 4098314.8 |  | 5044243
|  |  |  | 3563752 |  | 4098314.8 |  | 5044243
| Procurement Subtotal |  |  | 97803017 |  | 106619584.75 |  | 113281049
Construction
| site |  |  | 505265 | 115% | 581054.75 |  | 910904
| u/g electrical |  |  | 1281105 | 115% | 1473270.75 |  | 657630
| u/g piping |  |  | 838121 | 115% | 963839.15 |  | 445017
| concrete |  |  | 2406030 | 115% | 2766934.5 |  | 1129472
| grout |  |  | 134599 | 115% | 154788.85 |  | 58075
| steel |  |  | 154773 | 115% | 177988.95 |  | 62727
| architectural |  |  | 2724 | 115% | 3132.6 |  | 3814
| buildings |  |  | 280613 | 115% | 322704.95 |  | 157550
| a/g piping |  |  | 2304369 | 115% | 2650024.35 |  | 1074572
| a/g electrical |  |  | 1979274 | 115% | 2276165.1 |  | 1086685
| instrumentatiion |  |  | 309040 | 115% | 355396 |  | 201616
| insulation |  |  | 202466 | 115% | 232835.9 |  | 205509
| painting |  |  | 25586 | 115% | 29423.9 |  | 26272
| mech equipment |  |  | 1711599 | 115% | 1968338.85 |  | 907944
|  |  |  | 12135564 |  | 13955898.6 |  | 6927784
Startup
| startup |  |  | 632940 | 115% | 727881 |  | 759528
| oper training |  |  | 10000 | 100% | 10000 |  | 12500
| initial fill/spares |  |  | 106250 | 120% | 127500 |  | 123250
| manuals |  |  | 28000 | 100% | 28000 |  | 40600
| startup support |  |  | 194990 | 110% | 214489 |  | 112018
|  |  |  | 972180 |  | 1107870 |  | 1047896
Warranty
| warranty |  |  | 25000 | 110% | 27500 |  | 43750
|  |  |  | 25000 |  | 27500 |  | 43750
Owner Adds
| Substation |  |  | 0 |  | 2250000 | 3 345kV bays plus tube bus | 4675000 | 11 230 kV bays
| gas pipeline |  |  | 0 |  | 2700000 | 4.5 miles of 12" @$50,000/inch-mile | 1400000
| transmission line |  |  | 0 |  | 0 | in substation | 1500000
| ENA remote monitoring |  |  | 0 |  | 173000 |  | 173000
| admin buildings |  |  | 0 |  | 0 |  | 600000
|  |  |  | 0 |  | 5123000 |  | 8348000
Subtotal Cost |  |  |  | 125333319 |  | 137035867.15 |  | 134864677
| fixed G&A | 2% |  | 2506666.38 |  | 2740717.343 |  | 2697293.54
Total Cost |  |  |  | 127839985.38 |  | 139776584.493 |  | 137561970.54
| contingency |  | 2% | 2556799.7076 | 1.5% | 2096648.7674 |  | 2063429.5581
| margin |  | 6% | 7670399.1228 | 6% | 8386595.0696 |  | 8253718.2324
TOTAL PROJECT EPC |  |  |  | 138067184.2104 |  | 150259828.33 |  | 147879118.3305
capacity |  |  |  | 225 |  | 277 |  | 273
|  |  |  | 613.6319 |  | 542.4543 |  | 541.6818

## CTGprice
yes
Lowell deal
[5 empty] | units | 5
included
LM6000 |  |  | 13500000 |  | yes | 67500000
WestLB |  |  | 310000 |  | yes | 1550000
Sprint |  |  | 450000 |  | yes | 2250000
fin fan |  |  | 0 | included in base deal | yes | 0
chiller |  |  | 950000 |  | no | 0
cooling tower |  |  | 150000 |  | no | 0
water injection metering |  |  | 57000 |  | yes | 285000
additional CT's |  |  | 23000 |  | yes | 115000
60ft stack |  |  | 236000 |  | no | 0 | included in SCR
dual fuel |  |  | 280000 |  | no | 0 | gas fuel only
gas heater |  |  | 247000 |  | no | 0 | gas compression so no heating required
vendor TDI |  |  | 48000 |  | no | 0 | 240 mnhrs/unit included in base price
freight for stack |  |  | 18500 |  | no | 0
freight for CTG |  |  | 150000 |  | no | 0
|  |  | 16419500 |  |  | 71700000
14340000
OPTIONS
dual fuel |  |  | 280000
stack 45 ft standard |  |  | 198000
stack 45 ft heavy |  |  | 233000
chiller |  |  | 950000
LM6000 |  |  | 13500000
WestLB |  |  | 310000
Sprint |  |  | 450000
fin fan |  |  | 62000
chiller |  |  | 950000
cooling tower |  |  | 150000
15 kV swutchgear |  |  | 206258
15 kV to 4160 V transformer |  |  | 68753
4160 switchgear |  |  | 34376
4160 V to 480 V transformer |  |  | 34376
480 V distribution/switchpanel |  |  | 41252
BOP distribution panel/MCC |  |  | 34376
air compressor |  |  | 56377
liquid fuel tank heater | 2 | 50% | 154006
liquid fuel unloading station |  |  | 137506
liquid fuel treatment |  |  | 495020
liquid fuel forwarding skid |  |  | 61878
liquid fuel duplex filter |  |  | 36164
gas fuel filter skid |  |  | 99334
gas fuel scubber/heater |  |  | 199383
raw water forwarding skid |  |  | 44002
demin forwarding |  |  | 90794
oily water separator |  |  | 165007
anti-ice air to air |  |  | 226884

## calcs
unit capacity | kW | 47500
power factor |  | 0.9
unit output | kVA | 52777.7778
voltage | V | 13800
| A | 2208.0626