## M Data
Units
EMISSIONS CASE |  | 4 | 16
Mode | - | CC | CC
Fuel | - | NG | Distillate
Load Level | % | 100 | 100
Duct Fire | - | none | none
Ambient Temperature | deg F | 59,74,95 | 59,74,95
Ambient Relative Humidity | % | 65 | 65
CTG DATA
Load Condition
Exhaust Pressure Loss | inches Water | 14.8 | 14.1
Ambient Temp. | Deg F. | 80 | 80
Ambient Relative Humid. | % | 100 | 100
CTG conditioned inlet air temp | Deg F. | 45 | 45
CTG conditioned inlet air RH | % | 100 | 100
Fuel Type |  | Brooker Gas | Dist.
Fuel LHV | Btu/lb | 20884.8 | 18180
Fuel Temperature (site boundary) | Deg F | 77 | 77
Liquid Fuel H/C Ratio | - | - | 6.6
Net Output | kW | 184000 | 163320
Net Heat Rate (LHV) | Btu/kWh | 9344 | 9990
Heat Cons. (LHV) X 106 | Btu/h | 1719.296 | 1632.0568
Exhaust Flow X 103 | lb/h | 3733 | 3792
Exhaust Temp. | Deg F. | 1128 | 1019
Exhaust Heat (LHV) X 106 | Btu/h
Water Flow | lb/h | 0 | 53500
EMISSIONS
NOx | ppmvd@15%O2 | 25 | 42
NOx AS NO2 | lb / hr | 173 | 282
CO | ppmvd@15%O2 | 10 | 50
CO | lb / hr | 42 | 204
UHC | ppmvd@15%O2 | 5 | 75
UHC (as CH4) | lb / hr | 12 | 175
VOC (as 20% of UHC) | ppmvd@15%O2 | 1 | 15
VOC (as CH4) | lb / hr | 3 | 35
PM10 | mg / Nm3 | 5 | 10
PM10 | lb / hr | 14 | 28
(PM10 Front-half Filterable Only)
EXHAUST ANALYSIS % WT.
Argon | % | 1.31 | 1.29
Nitrogen | % | 73.36 | 72.17
Oxygen | % | 13.97 | 14.32
Carbon Dioxide | % | 6 | 7.46
Water | % | 5.36 | 4.76
MW | lb / lb - mol
NOTE |  | 1. Output is not limited by generator.
2. Duct firing is not our scope of supply, then all data when duct firing is blank.
3. Power output and heat rate are NET values.
4. NOx and PM10 @100% load are guarantee values. The others are expected only.
5. Fuel Bound Nitrogen (FBN) is none.
6. Sulfur in fuel gas is 3.536 ppmv. (Brooker gas) Sulfur in fuel oil is 0.05 wt.%.
7. Fuel conditions will be satisfied with MHI's requirements.