## Cover Page
ENRON TRANSPORTATION AND SERVICES
PROJECT COST ESTIMATE - 3/28/01
| Customer Company Name | FGT FACILITY PLANNING
| Project Name: | MANCINI
| Project Engineer: | GREG BIERMAN
| Revision: | 0
Project Summary
Project consists of installing .3 miles of 16" pipe and a 10" ultrasonic meter station in the
Pompano, Florida area. Estimated cost of entire project is $1,948,000. Please refer to
"PROJECT ESTIMATE" tab for cost breakdown. FGT 18" and 24" mainlines will be
hot tapped with 8" and 12" taps respectively.
Meter station includes 10" ultrasonic meter, with a 1" rotary meter in parallel for measuring
very small volume. Dry filter separator included in estimate. No pressure or flow control
valves included. Estimate does include gas chromatograph.
Design Specific Locations
FGT Mainline MAOP: 975 psig
New Pipeline & Meter Station Design Pressure: 975 psig
Design flow rate: 125 MMcf/d
Delivery pressure to customer: FGT line pressure
Class Location: 1
Design Factor - Meter Station: .5
Design Factor - Pipeline: .5
Location - | Tap location FGT mainline milepost 866.5 approx.
Special Notes
Note: ROW costs are very expensive ($217,800 per acre) at this location. See "PROJECT
ESTIMATE" tab for further details. Costs are based on actual tax appraised valves.
Confirmation of land value costs will require an actual appraisal of the property. - requiring
more time and money.

## RISKS
ENRON TRANSPORTATION AND SERVICES
PROJECT COST ESTIMATE - 3/28/01
| Customer Company Name | FGT FACILITY PLANNING
| Project Name: | MANCINI
| Project Engineer: | GREG BIERMAN
| Revision: | 0
Unexpected Additional Costs
Construction
Projected ROW costs are expected to be exorbitant. Seventy-five feet working width was
used in the estimate however the actual width (in an effort to reduce the total cost)
may be less than 75 feet thus resulting in a higher lay cost.
Wet weather will require additional construction time which will increase lay cost.
If higher than normal water table encountered, lay costs will increase.
Right of Way
Land prices are very expensive in the immediate area - possibly leading to increased
agent time, legal fees, etc.
Environmental
Construction in designated wetlands is not anticipated however nearby lake may be cause for
additional hay bales, silt fencing etc.
Although none is anticipated, state could require an archaeological dig along route.
Materials
Straight approach from FGT's mainline to meter station was assumed in estimate. Pipe footage
could increase due to ROW deviations, or unexpected ENVR concerns, etc.

## Misc Notes
ENRON TRANSPORTATION AND SERVICES
PROJECT COST ESTIMATE - 3/28/01
| Customer Company Name | FGT FACILITY PLANNING
| Project Name: | MANCINI
| Project Engineer: | GREG BIERMAN
| Revision: | 0
Misc Estimate Notes and Assumptions
Pipeline Lateral
Designed in accordance with ENRON Engineering Standards and 49 CFR Part 192.
Costs are based on 2001 construction.
Terrain is flat with no wetlands, stream crossings or foreign pipeline crossings.
Pipeline installed with conventional lay methods.
No directional drills were included in estimate (none expected).
Contractor expected to be on site for 13 workings days - barring any rain delays, etc.
Estimate does not include delays caused by the U.S. Fish & Wildlife endangered
species habitat conflicts.
Estimate include cost of Archaeology survey and not Archaeology dig if so required by SHPO.
Expediting materials is not included (either during mfg'ing or shipment).
Wetlands mitigation is not expected nor included.
Construction install cost was not completed or reviewed by a contractor.
Estimate accuracy is estimated to be +/-10%.
Hot tap includes TDW split tee and hot tap valve - all below grade. Valve extensions include.
No abovegrade valve at hot tap location included.
Check valve (wafer type) included on 8"/18" tie-over line.
No condemnations are included in estimate.
Pig launcher/receivers not included.
Meter Station
Designed in accordance with ENRON Engineering Standards and 49 CFR Part 192.
Costs are based on 2001 construction.
Meter station to be located inside of Customer's property - only minor ROW costs
included in estimate.
115 volt power will be made available by Customer at meter station.
Small building included with gas chromatograph.
Estimate accuracy is +/-10%.
Run switching included with meter runs.
Gas chromatograph costs included in meter station estimate.
No station ESD included with meter station estimate.
No pressure or control valves included.
No gas detection included in building
Expediting materials is not included (either during mfg'ing or shipment).

## PROJECT ESTIMATE
ENRON TRANSPORTATION AND SERVICES
PROJECT COST ESTIMATE - 3/28/01
| Customer Company Name | FGT FACILITY PLANNING
| Project Name: | MANCINI
| Project Engineer: | GREG BIERMAN
| Revision: | 0
PIPELINE (LATERAL) |  |  | Est. Qty | Unit | Unit Cost | Total
Contractor Installation Direct
| Upland Installation |  | 1584 | ft | 80.1768 | 127000
| Hot Tap 18" & 24" |  | 2 | ea. | 7250 | 14500
| Contractor Mob/Demob |  | 1 | ea. | 31368 | 31368
| Total Contractor Installation Direct |  |  |  |  | 172868
Contractor Adder Lay Cost
| Re-seeding |  | 1584 | ft | 2 | 3168
| Hay Bales |  | 500 | ft | 1 | 500
| Well Points |  | 1 | ea. | 8000 | 8000
| Concrete Set-on Weights |  | 66 | ea. | 200 | 13200
| Silt Fencing |  | 600 | ft | 10 | 6000
| Road Bores |  | 0 | ea. |  | 0
| Directional Drill |  | 0 | ea. |  | 0
| Contractor Supplied Material |  |  |  |  | 0
| Total Contractor Adder Lay Cost |  |  |  |  | 30868
Material (incl. Freight & taxes)
| See "MATL-Lateral" Tab |  |  |  |  | 72009.2961
| Freight |  | 8% |  |  | 5760.7437
| Taxes |  | 8% |  |  | 5760.7437
| Material (incl. Freight & taxes) |  |  |  |  | 83530.7834
Environmental Costs
| Hydrostatic Test Water Inspection |  | 1 | ea. | 4000 | 4000
| Archeological Survey |  | 1 | ea. | 8800 | 8800
| Site visit ENRON rep |  | 6 | days | 500 | 3000
| Total Environmental Costs |  |  |  |  | 15800
Construction Support
| Chief Inspector |  | 19 | days | 400 | 7600
| Construction Coordinator |  | 10 | days | 500 | 5000
| Clerk |  | 20 | days | 200 | 4000
| Welding Inspector |  | 19 | days | 300 | 5700
| Environmental Inspector |  | 19 | days | 300 | 5700
| Electrical Inspector |  | 0 | days |  | 0
| Construction Trailer |  | 0 | days |  | 0
| Mail/phone/Util/Misc. |  | 22 | days | 40 | 880
| Surveyors |  | 22 | M-days | 420 | 9240
| Hot Tap Crew |  | 7 | days | 400 | 2800
| X-Rays |  | 1 | ea | 15560 | 15560
| Total Construction Support |  |  |  |  | 56480
Company Labor
| Company Employees |  | 8 | days | 418.5 | 3348
| Total Construction Support |  |  |  |  | 3348
Engineering / Design
| Project Manager |  | 7 | days | 504 | 3528
| Project Engineer |  | 14 | days | 448 | 6272
| Travel / Misc |  | 1 | ea | 3480 | 3480
| In House Designers |  | 25 | days | 380 | 9500
| Total Engineering / Design |  |  |  |  | 22780
ROW
| New ROW 1,760' x 40' |  | 1.6162 | acres | 217800 | 352000
| Temp Work Space, 1760' x 35' |  | 1.4141 | acres | 54450 | 77000
| ROW Mgr |  | 5 | days | 400 | 2000
| Agents |  | 10 | days | 400 | 4000
| Temp Work Space, 100' x 100' (Hot tap) |  | 0.22957 | acres | 54450 | 12500
| ROW Damages |  | 1 | ea. | 500 | 500
| Permits, misc. |  | 1 | ea. | 1200 | 1200
| Total ROW |  |  |  |  | 449200
| Other (Blowdown & Purge) |  | 350 | Mcf | 5.2 | 1820
| As-built Package |  | 0.9747% |  |  | 8137.1332
| Overhead (FGT) |  | 20% |  |  | 168966.3833
| AFUDC |  | 3% |  |  | 30413.949
| Contingency |  | 14.73% |  |  | 153787.751
| TOTAL ESTIMATED COST |  |  |  |  | 1198000
METER STATION
Contractor Install Direct Cost
| Mech/Civil Direct |  | 1 | ea. | 125815 | 125815
| Electrical Direct |  | 1 | ea. | 30500 | 30500
| Contractor Mob/Demob |  | 1 | ea. | 12000 | 12000
| Total Contractor Install Direct Cost |  |  |  |  | 168315
Contractor Adder Install Cost
| Contractor Supplied Material |  | 1 | lot | 3485.3391 | 3485.3391
| Total Contractor Adder Install Cost |  |  |  |  | 3485.3391
Material
| See "MATL-Lateral" Tab |  |  |  |  | 254775.5414
| Freight |  | 8% |  |  | 20382.0433
| Taxes |  | 8% |  |  | 20382.0433
| Total Material Cost |  |  |  |  | 295539.628
Environmental Costs
| Hydrostatic Test Water Inspection |  | 1 | ea. | 3000 | 3000
| Site visit ENRON rep |  | 2 | days | 500 | 1000
| Total Environmental Costs |  |  |  |  | 4000
Construction Support
| Chief Inspector |  | 18 | days | 400 | 7200
| Construction Coordinator |  | 7 | days | 500 | 3500
| Clerk |  | 13 | days | 200 | 2600
| Welding Inspector |  | 14 | days | 300 | 4200
| Environmental Inspector |  | 0 | days | 300 | 0
| Electrical Inspector |  | 13 | days | 350 | 4550
| Construction Trailer |  | 0 | days |  | 0
| Mail/phone/Util/Misc. |  | 16 | days | 40 | 640
| Surveyors |  | 11 | M-days | 420 | 4620
| Hot Tap Crew |  | 0 | days | 400 | 0
| X-Rays |  | 1 | ea | 8300 | 8300
| Total Construction Support |  |  |  |  | 35610
Company Labor
| Company Employees |  | 5 | days | 380 | 1900
| Total Company Labor |  |  |  |  | 1900
Engineering / Design
| Project Manager |  | 6 | days | 504 | 3024
| Project Engineer |  | 24 | days | 448 | 10752
| Travel / Misc |  | 1 | ea | 3480 | 3480
| In House Designers |  | 45 | days | 380 | 17100
| Total Engineering / Design |  |  |  |  | 34356
ROW
| Agent |  | 5 | days | 400 | 2000
| Permits |  | 1 | ea. | 1200 | 1200
| Total ROW |  |  |  |  | 3200
| Gas Loss (Blowdown & Purge) |  | 20 | Mcf | 5.2 | 104
| As-built Package |  | 2% |  |  | 10930.1993
| Overhead (FGT) |  | 20% |  |  | 111488.0333
| AFUDC |  | 2% |  |  | 13378.564
| Contingency |  | 9.921% |  |  | 67693.2363
| TOTAL ESTIMATED COST |  |  |  |  | 750000
| TOTAL METER STATION ESTIMATED COST |  |  |  |  | 750000
| TOTAL PIPELINE LATERAL ESTIMATED COST |  |  |  |  | 1198000
| PROJECT ESTIMATED COST |  |  |  |  | 1948000

## MATL - Lateral
MANCINI Take-off and Pipeline
Bill of Materials
[12 empty] | Project Total: |  | 72009.2961
[11 empty] | *Contractor Supplied |  |  | 0
Elbow |  | Size (O.D.) | qty | unit | Deg |  |  | Gr |  | Amount | Unit |  | Total | 717.5833
| Elbow | 12 | 1 | ea. | 23 |  |  | B |  | 245.0833 | ea. |  | 245.0833
| Elbow | 8 | 2 | ea. | 45 |  |  | B |  | 146.25 | ea. |  | 292.5
| Elbow | 8 | 1 | ea. | 90 |  |  | B |  | 180 | ea. |  | 180
Pipe |  | Size (O.D.) | qty | unit |  | wall |  | f p b | Gr | Amount | Unit |  | Total | 43726.9905
| FBE 0.375 wall, X 42 | 16 | 1760 | ft |  | std |  | f | 42 | 24.2929 | ft |  | 42755.4267
| FBE 0.375 wall | 12 | 20 | ft |  | 0.375 |  | f | b | 30.1566 | ft |  | 603.1328
| FBE 0.322 wall | 8 | 20 | ft |  | 0.322 |  | f | 60 | 18.4216 | ft |  | 368.431
Tees (Reducing) |  | Run x | qty | unit | Branch |  |  | Gr |  | Amount | Unit |  | Total | 259.7222
| tee reducing | 12 | 1 | ea. | 8 |  |  | 42 |  | 259.7222 | ea. |  | 259.7222
Valves - Ball |  | Size (O.D.) | qty | unit | ANSI |  | W/F |  |  | Amount | Unit |  | Total | 17130
| Valves - Ball | 12 | 1 | ea. | 600 |  | F |  |  | 10230 | ea. |  | 10230
| Valves - Ball | 8 | 1 | ea. | 600 |  | F |  |  | 6900 | ea. |  | 6900
Flanges |  | Size (O.D.) | qty | unit | ANSI | wall | W/F |  |  | Amount | Unit |  | Total | 500
| Flange | 12 | 1 | ea. | 600 | std | W |  |  | 350 | ea. |  | 350
| Flange | 8 | 1 | ea. | 600 | std | W |  |  | 150 | ea. |  | 150
Bolt-up & Gaskets |  | Size (O.D.) | qty | unit | ANSI |  |  |  |  | Amount | Unit |  | Total | 330
| Bolt-up & Gaskets | 12 | 2 | sets | 600 |  |  |  |  | 112 | ea. |  | 224
| Bolt-up & Gaskets | 8 | 2 | sets | 600 |  |  |  |  | 53 | ea. |  | 106
Valves - Check |  | Size (O.D.) | qty | unit | ANSI |  | End |  |  | Amount | Unit |  | Total | 620
| Check Valve - Swing | 8 | 1 | ea. | 600 |  | F |  |  | 620 | ea. |  | 620
Reducers |  | Run x | qty | unit | Branch |  |  | Gr |  | Amount | Unit |  | Total | 125
| reducer | 16 | 1 | ea. | 12 |  |  | 42 |  | 125 | ea. |  | 125
TDW Items |  | Size (O.D.) | qty | unit | [5 empty] | Amount | Unit |  | Total | 8600
| TDW Split Tee w/ flange | 18 | 1 | ea. | [5 empty] | 4000 | ea. |  | 4000
| TDW Split Tee w/ flange | 24 | 1 | ea. | [5 empty] | 4600 | ea. |  | 4600

## MATL - Meter Sta
ENA Meter Station
Bill of Materials
[12 empty] | Project Total: |  | 258260.8805
[11 empty] | *Contractor Supplied |  |  | 3485.3391
Pipe |  | Size (O.D.) | qty | unit |  | wall |  | f p b | Gr | Amount | Unit |  | Total | 7727.7192
| Bare, 0.154 wall, Gr. B | 2 | 80 | ft |  | std |  | b | b | 2.0094 | ft |  | 160.7499
| Bare, 0.375 wall, Gr. B | 12 | 240 | ft |  | std |  | b | b | 24.7842 | ft |  | 5948.213
| Bare, 0.237 wall, Gr. B | 4 | 30 | ft |  | std |  | b | b | 6.1513 | ft |  | 184.5392
| Bare, 0.365 wall, Gr. B | 10 | 20 | ft |  | std |  | b | b | 23.0783 | ft |  | 461.5651
| Bare, 0.365 wall, Gr. B | 10 | 40 | ft |  | std |  | b | b | 23.0783 | ft |  | 923.1303
| Bare, 0.179 wall, Gr. B | 1 | 40 | ft |  | xs |  | b | b | 1.238 | ft |  | 49.5216
Valves - Ball |  | Size (O.D.) | qty | unit | ANSI |  | W/F |  |  | Amount | Unit |  | Total | 62140
| Valves - Ball | 4 | 3 | ea. | 600 |  | F |  |  | 3200 | ea. |  | 9600
| Valves - Ball | 12 | 2 | ea. | 600 |  | F |  |  | 10230 | ea. |  | 20460
| Valves - Ball | 2 | 1 | ea. | 600 |  | F |  |  | 1390 | ea. |  | 1390
| Valves - Ball | 12 | 3 | ea. | 600 |  | F |  |  | 10230 | ea. |  | 30690
Valves - Control |  | Size (O.D.) | qty | unit | Type |  |  |  |  | Amount | Unit |  | Total | 0
Valve Actuators |  | Size (O.D.) | qty | unit | Type |  |  |  |  | Amount | Unit |  | Total | 21700
| Valve Actuators | 12 | 2 | ea. | [5 empty] | 9700 | ea. |  | 19400
| Valve Actuators | 4 | 1 | ea. | [5 empty] | 2300 | ea. |  | 2300
Gas Filtering |  |  | qty | unit | (MM/d) |  |  |  |  | Amount | Unit |  | Total | 38000
| Coalescing Filter by Peerless |  | 1 | ea. | 125 |  |  |  |  | 38000 | ea. |  | 38000
Elbow |  | Size (O.D.) | qty | unit | Deg |  |  | Gr |  | Amount | Unit |  | Total | 967.6
| Elbow | 4 | 2 | ea. | 90 |  |  | b |  | 7.8 | ea. |  | 15.6
| Elbow | 12 | 10 | ea. | 90 |  |  | b |  | 94 | ea. |  | 940
| Elbow | 1 | 4 | ea. | 90 |  |  | b |  | 3 | ea. |  | 12
Reducers |  | Run x | qty | unit | Branch |  |  | Gr |  | Amount | Unit |  | Total | 360
| reducer | 12 x 10 | 2 | ea. |  |  |  | 42 |  | 110 | ea. |  | 220
| reducer | 16 x 12 | 1 | ea. |  |  |  | 42 |  | 140 | ea. |  | 140
Tees |  | O.D. | qty | unit |  |  |  | Gr |  | Amount | Unit |  | Total | 375
| Tee | 12 | 1 | ea. |  |  |  | b |  | 125 | ea. |  | 125
| Tee | 12 | 2 | ea. |  |  |  | b |  | 125 | ea. |  | 250
Meters |  | OD | qty | unit | ANSI |  | Style |  |  | Amount | Unit |  | Total | 2300
| Roots Rotary | 1 | 1 | ea. |  |  | M |  |  | 2300 | ea |  | 2300
Tees (Reducing) |  | Run x | qty | unit | Branch |  |  | Gr |  | Amount | Unit |  | Total | 1174.2222
| tee reducing | 16 | 2 | ea. | 4 |  |  | 42 |  | 476 | ea. |  | 952
| tee reducing | 12 | 2 | ea. | 4 |  |  | b |  | 111.1111 | ea. |  | 222.2222
Bolt-up & Gaskets |  | Size (O.D.) | qty | unit | ANSI |  |  |  |  | Amount | Unit |  | Total | 902
| Bolt-up & Gaskets | 4 | 4 | sets | 600 |  |  |  |  | 24 | ea. |  | 96
| Bolt-up & Gaskets | 12 | 5 | sets | 600 |  |  |  |  | 112 | ea. |  | 560
| Bolt-up & Gaskets | 10 | 3 | sets | 600 |  |  |  |  | 82 | ea. |  | 246
Flanges |  | Size (O.D.) | qty | unit | ANSI | wall |  |  |  | Amount | Unit |  | Total | 6110
| Flange | 4 | 6 | ea. | 600 | std |  |  |  | 65 | ea. |  | 390
| Flange | 12 | 6 | ea. | 600 | std |  |  |  | 350 | ea. |  | 2100
| Flange | 12 | 5 | ea. | 600 | std |  |  |  | 350 | ea. |  | 1750
| Flange | 10 | 6 | ea. | 600 | std |  |  |  | 240 | ea. |  | 1440
| Flange - Blind | 12 | 1 | ea. | 600 | std |  |  |  | 430 | ea. |  | 430
Transmitters |  |  | qty | unit | [5 empty] | Amount | Unit |  | Total | 4604
| Pressure 3051CG |  | 2 | ea. | [5 empty] | 1280 | ea. |  | 2560
| Temperature 3144 w/sensor |  | 2 | ea. | [5 empty] | 1022 | ea. |  | 2044
Measure Misc |  | Size (O.D.) | qty | unit | ANSI |  |  |  |  | Amount | Unit |  | Total | 4870
| Strainer T - type | 4 | 1 | ea. | 600 |  |  |  |  | 655 | ea |  | 655
| Gallagher Flow Conditioners | 10 | 1 | ea. | [5 empty] | 4215 | ea |  | 4215
Meters |  | OD/Model | qty | unit | ANSI |  |  |  |  | Amount | Unit |  | Total | 43160
| Q sonic | 10 | 1 | ea. | 600 |  |  |  |  | 29060 | ea |  | 29060
| Ultrasonic Meter Spools (3) | 10 | 1 | ea. | 600 |  |  |  |  | 5600 | ea |  | 5600
| Q Sonic Calibration | 10 | 1 | ea. | 600 |  |  |  |  | 8500 | ea |  | 8500
RTU / PLC |  |  | qty | unit | Hrs |  |  |  |  | Amount | Unit |  | Total | 3500
| Bristal 3335 |  | 1 | ea. | [5 empty] | 3500 | ea |  | 3500
| Bristal 3330 |  |  | ea. | [5 empty] | 6000 | ea
Pipe Supports |  | Nom. (O.D.) | qty | unit | [5 empty] | Amount | Unit |  | Total | 1370
| Pipe Supports (Adj.) | 12 | 4 | [6 empty] | 140 | ea. |  | 560
| Pipe Supports (Adj.) | 10 | 4 | [6 empty] | 120 | ea. |  | 480
| Pipe Supports (Adj.) | 4 | 6 | [6 empty] | 55 | ea. |  | 330
Fences |  | length | qty | unit | width |  |  |  |  | Amount | Unit |  | Total | 2450
| 8' fence w/ poles | 200 | 550 | ft | 75 |  |  |  |  | 10.5 | ft |  | 2100
| gate ( 16' drive) |  | 1 | ea. | [5 empty] | 350 | ea |  | 350
Rock/Dirt/Conc. |  | OD | qty | unit | [5 empty] | Amount | Unit |  | Total | 3735.3391
| concrete |  | 5 | yds | [5 empty] | 120 | yds |  | 600
| concrete (sonotubes) |  | 11.7286 | yds | [5 empty] | 140 | yds |  | 1642.0058
| concrete |  | 12.4444 | yds | [5 empty] | 120 | yds |  | 1493.3333
Tanks |  |  | qty | unit | Gallons |  |  |  |  | Amount | Unit |  | Total | 3500
| Atmos,dbl wall,horz | 4' dia. x 5.8' | 1 | ea. | 500 |  |  |  |  | 7 | gal |  | 3500
Structural Iron |  | Width(in) | ft | unit | [5 empty] | Amount | Unit |  | Total | 2880
| I Beam | 6 | 288 | ft | [5 empty] | 10 | ft |  | 2880
Buildings |  | length | qty | unit | width | eave |  | Ins |  | Amount | Unit |  | Total | 15140
| Building w/ ac, hvac | 10 | 80 | sq.ft. | 8 | 8 |  |  |  | 189.25 | sq ft |  | 15140
Elec Misc |  |  | qty | unit | [5 empty] | Amount | Unit |  | Total | 525
| Single Gang PushButton Ex Proof |  | 3 | ea. | [5 empty] | 175 | ea. |  | 525
Control Switches |  |  | qty | unit | [5 empty] | Amount | Unit |  | Total | 1330
| Level Switch DPDT |  | 1 | ea. | [5 empty] | 1330 | ea. |  | 1330
Measure Misc |  | Size (O.D.) | qty | unit | ANSI |  |  |  |  | Amount | Unit |  | Total | 80
| Pressure Gauges |  | 1 | ea. | [5 empty] | 80 | ea |  | 80
Chromatographs |  | OD | qty | unit | ANSI |  | Style |  |  | Amount | Unit |  | Total | 29360
| Insertion Probe | 12 | 1 | ea. | 600 |  |  |  |  | 2000 | ea |  | 2000
| Chromatograph - Danalyzer |  | 1 | ea. | [5 empty] | 19500 | ea |  | 19500
| Regulator for Cal Gas |  | 1 | ea. | [5 empty] | 325 | ea |  | 325
| Regulator for Carrier Gas |  | 1 | ea. | [5 empty] | 385 | ea |  | 385
| Mannifold for Carrier Gas |  | 1 | ea. | [5 empty] | 550 | ea |  | 550
| Heater for Cal Gas |  | 1 | ea. | [5 empty] | 3500 | ea |  | 3500
| Cyl of Cal Gas |  | 1 | ea. | [5 empty] | 1100 | ea |  | 1100
| Heat Traced SS Tubing | 0.125 | 100 | ea. | [5 empty] | 20 | ea |  | 2000