## 1001
Mill Run / Somerset Project Operational Report For October 2001
Executive Summary
This interim report was generated to comply with the contractual monthly reporting requirement from the Windsystem, Operations, & Maintenance Agreement.
The description of outages, safety near miss events, accidents, infrastructure work, and maintenance records are not included in this interim report.
All other required components are provided below.
Turbine Performance
|  |  |  | Operational Parameters |  | Operational Parameters
Site | Row | Pad | ReportingMonth | kWhGenerated | kWhConsumed | Net kWh Production | Capacity Factor | Availability1 | Operating Hrs
Mill Run | 1 | 1 | 2001-10-01 | 25770 | 445 | 25325 | 2.269% | 93.09% | 692.5896
Mill Run | 1 | 2 | 2001-10-01 | 48049 | 108 | 47941 | 4.296% | 88.52% | 658.5888
Mill Run | 1 | 3 | 2001-10-01 | 52071 | 12 | 52059 | 4.665% | 98.99% | 736.4856
Mill Run | 1 | 4 | 2001-10-01 | 291751 | 446 | 291305 | 26.1% | 90.94% | 676.5936
Mill Run | 1 | 5 | 2001-10-01 | 78927 | 392 | 78535 | 7.037% | 98.89% | 735.7416
Mill Run | 1 | 6 | 2001-10-01 | 221765 | 391 | 221374 | 19.84% | 89.55% | 666.252
Mill Run | 1 | 7 | 2001-10-01 | 266099 | 843 | 265256 | 23.77% | 96.84% | 720.4896
Mill Run | 1 | 8 | 2001-10-01 | 304810 | 651 | 304159 | 27.25% | 99.3% | 738.792
Mill Run | 1 | 9 | 2001-10-01 | 58069 | 265 | 57804 | 5.18% | 90.15% | 670.716
Mill Run | 1 | 10 | 2001-10-01 | 16352 | 341 | 16011 | 1.435% | 54.78% | 407.5632
|  | Project, before line loss | Month | 1363663 | 3894 | 1359769 | 12.18% | 90.11% | 6703.812
|  | Assumed Line Loss2 | Month | 27273.26 | 77.88 | 27195.38 | Not applicable | Not applicable | Not applicable
|  | Project, after line loss | Month | 1336389.74 | 3816.12 | 1332573.62 | 11.94% | 90.11% | 6703.812
|  | Project, after line loss | Year To Date | 1336389.74 | 3816.12 | 1332573.62 | 11.94% | 90.11% | 6703.812
Notes:
1) Current month availability is based on reads at turbine controller.
2) The line loss is assumed to be 2% until sufficient data is collected to statistically determine the actual line loss.
Power Outages
No of WTGs Affected | Time Off | Time On | Cause Of Relay Trip or Major Grid Fluctuation |  |  |  | WTG hrs Lost | Grid Availability Loss
|  |  | No outages reported. |  |  |  | 0 | 0%
Days in Month | 31 |  |  |  |  | Project Total | 0 | 0
[7 empty] | Grid Availability | 100%

## 1101
Mill Run / Somerset Project Operational Report For November 2001
Executive Summary
This interim report was generated to comply with the contractual monthly reporting requirement from the Windsystem, Operations, & Maintenance Agreement.
The description of outages, safety near miss events, accidents, infrastructure work, and maintenance records are not included in this interim report.
All other required components are provided below.
Turbine Performance
|  |  |  | Operational Parameters |  | Operational Parameters
Site | Row | Pad | ReportingMonth | kWhGenerated | kWhConsumed | Net kWh Production | Capacity Factor | Availability1 | Operating Hrs
Mill Run | 1 | 1 | 2001-11-01 | 327099 | 549 | 326550 | 30.24% | 86.7% | 645.048
Mill Run | 1 | 2 | 2001-11-01 | 159362 | 1499 | 157863 | 14.62% | 76.4% | 568.416
Mill Run | 1 | 3 | 2001-11-01 | 334495 | 37 | 334458 | 30.97% | 94.6% | 703.824
Mill Run | 1 | 4 | 2001-11-01 | 373688 | 222 | 373466 | 34.58% | 92.8% | 690.432
Mill Run | 1 | 5 | 2001-11-01 | 325038 | 1065 | 323973 | 30% | 85.3% | 634.632
Mill Run | 1 | 6 | 2001-11-01 | 310123 | 722 | 309401 | 28.65% | 91.3% | 679.272
Mill Run | 1 | 7 | 2001-11-01 | 197404 | 1405 | 195999 | 18.15% | 70.6% | 525.264
Mill Run | 1 | 8 | 2001-11-01 | 309596 | 808 | 308788 | 28.59% | 99.6% | 741.024
Mill Run | 1 | 9 | 2001-11-01 | 287294 | 814 | 286480 | 26.53% | 92.9% | 691.176
Mill Run | 1 | 10 | 2001-11-01 | 237082 | 793 | 236289 | 21.88% | 83% | 617.52
|  | Project, before line loss | Month | 2861181 | 7914 | 2853267 | 26.42% | 87.32% | 6496.608
|  | Assumed Line Loss2 | Month | 57223.62 | 158.28 | 57065.34 | Not applicable | Not applicable | Not applicable
|  | Project, after line loss | Month | 2803957.38 | 7755.72 | 2796201.66 | 25.89% | 87.32% | 6496.608
|  | Project, after line loss | Year To Date | 4140347.12 | 11571.84 | 4128775.28 | 18.92% | 88.71% | 13200.42
Notes:
1) Current month availability is based on reads at turbine controller.
2) The line loss is assumed to be 2% until sufficient data is collected to statistically determine the actual line loss.
Power Outages
No of WTGs Affected | Time Off | Time On | Cause Of Relay Trip or Major Grid Fluctuation |  |  | Elapsed Hrs | WTG hrs Lost | Grid Availability
10 | 2001-11-08 | 2001-11-08 | Overvoltage trip. |  |  | 6 | 60
10 | 2001-11-26 | 2001-11-26 | Overvoltage trip. |  |  | 6.5 | 65
10 | 2001-11-26 | 2001-11-26 | Owner trip. |  |  | 0.5 | 5
0
0
0
0
Days in Month | 30 |  |  |  |  | Project Total | 130 | 98.19%

## 1201
Mill Run Project Operational Report For December 2001
Executive Summary
This interim report was generated to comply with the contractual monthly reporting requirement from the Windsystem, Operations, & Maintenance Agreement.
The description of outages, safety near miss events, accidents, infrastructure work, and maintenance records are not included in this interim report.
All other required components are provided below.
Turbine Performance
|  |  |  | Operational Parameters |  | Operational Parameters
Site | Row | Pad | ReportingMonth | kWhGenerated | kWhConsumed | Net kWh Production | Capacity Factor | Availability1 | Operating Hrs
Mill Run | 1 | 1 | 2001-12-01 | 324439 | 854 | 323585 | 29% | 79.4% | 590.736
Mill Run | 1 | 2 | 2001-12-01 | 136018 | 1112 | 134906 | 12.09% | 95.5% | 710.52
Mill Run | 1 | 3 | 2001-12-01 | 369856 | 222 | 369634 | 33.12% | 96.6% | 718.704
Mill Run | 1 | 4 | 2001-12-01 | 459203 | 470 | 458733 | 41.11% | 96.3% | 716.472
Mill Run | 1 | 5 | 2001-12-01 | 461542 | 819 | 460723 | 41.28% | 92.8% | 690.432
Mill Run | 1 | 6 | 2001-12-01 | 461014 | 306 | 460708 | 41.28% | 98.5% | 732.84
Mill Run | 1 | 7 | 2001-12-01 | 129466 | 2419 | 127047 | 11.38% | 46.6% | 346.704
Mill Run | 1 | 8 | 2001-12-01 | 399723 | 754 | 398969 | 35.75% | 85.8% | 638.352
Mill Run | 1 | 9 | 2001-12-01 | 491056 | 332 | 490724 | 43.97% | 98.2% | 730.608
Mill Run | 1 | 10 | 2001-12-01 | 322212 | 1241 | 320971 | 28.76% | 69.2% | 514.848
|  | Project, before line loss | Month | 3554529 | 8529 | 3546000 | 31.77% | 85.89% | 6390.216
|  | Assumed Line Loss2 | Month | 71090.58 | 170.58 | 70920 | Not applicable | Not applicable | Not applicable
|  | Project, after line loss | Month | 3483438.42 | 8358.42 | 3475080 | 31.14% | 85.89% | 6390.216
|  | Project, after line loss | Year To Date | 7623785.54 | 19930.26 | 7603855.28 | 22.99% | 87.77% | 19590.636
Notes:
1) Current month availability is based on reads at turbine controller.
2) The line loss is assumed to be 2% until sufficient data is collected to statistically determine the actual line loss.
Power Outages
No of WTGs Affected | Time Off | Time On | Cause Of Relay Trip or Major Grid Fluctuation |  |  | Elapsed Hrs | WTG hrs Lost | Grid Availability
10 | 2001-12-15 | 2001-12-15 | Undervoltage trip due to DVAR. |  |  | 5.75 | 57.5
10 | 2001-12-18 | 2001-12-18 | Overvoltage trip and utility scheduled line maintenance. |  |  | 11.25 | 112.5
10 | 2001-12-18 | 2001-12-18 | Overvoltage trip due to DVAR. |  |  | 0.25 | 2.5
10 | 2001-12-18 | 2001-12-18 | Overcurrent trip. |  |  | 3.25 | 32.5
10 | 2001-12-18 | 2001-12-19 | Overcurrent trip. |  |  | 8.5 | 85
10 | 2001-12-20 | 2001-12-20 | Overcurrent trip. |  |  | 2.5 | 25
10 | [6 empty] | 0
Days in Month | 31 |  |  |  |  | Project Total | 315 | 95.77%

## 0102
Mill Run Project Operational Report For January 2002
Executive Summary
This interim report was generated to comply with the contractual monthly reporting requirement from the Windsystem, Operations, & Maintenance Agreement.
The description of outages, safety near miss events, accidents, infrastructure work, and maintenance records are not included in this interim report.
All other required components are provided below.
Turbine Performance
|  |  |  | Operational Parameters | [30 empty] | Net | Net | Net | Net | Clock | Robust | Enron |  |  |  | Robust
Site | Row | Pad | Reporting Month | kWhGenerated | kWhConsumed | Net kWh Production | Capacity Factor | Availability w/ constant MH | Availability w/o MH | Operating Hrs | StartDate | StartProd | StartCon | StartOTT | StartSOTT | StartDTT | StartLOTT | StartWOTT | StartESTT | StartMTT | StartRTT | StopDate | StopProd | StopCon | StopOTT | StopSOTT | StopDTT | StopLOTT | StopWOTT | StopESTT | StopMTT | StartRTT | Survey | St | DTT | RTT | MT | LOT | Coverage | Avail | Avail | DownTime % | RepairTime % | MaintTime % | Avail w/o mh
Mill Run | 1 | 1 | 2002-01-01 | 514300 | 165 | 514135 | 48.77% | 99.96% | 99.4% | 702.4836 | 2002-01-02 17:14 | 851801 | 2099 | 4679818 | 5304166 | 1083331 | 441197 | 200325 | 0 | 38191 | 113360 | 2002-01-31 23:58 | 1366101 | 2264 | 7086392 | 7786323 | 1098628 | 467683 | 206197 | 0 | 38191 | 113360 | 702.7342 | 702.7256 | 15297 | 0 | 0 | 7.3572 | 0.99999 | 0.99964 | 0.99964 | 0.6047% | 0% | 0% | 0.99395
Mill Run | 1 | 2 | 2002-01-01 | 499214 | 468 | 498746 | 46.5% | 92.33% | 91.8% | 660.1609 | 2002-01-01 04:59 | 453811 | 2718 | 2424508 | 3820855 | 523533 | 156525 | 357804 | 0 | 271376 | 182167 | 2002-01-31 | 953025 | 3186 | 4636456 | 6191796 | 683097 | 186457 | 370334 | 0 | 272475 | 182167 | 715.0169 | 715.0183 | 159564 | 0 | 1099 | 8.3144 | 1 | 0.94286 | 0.94286 | 0.02778% | 0% | 0.0001913% | 0.93758
Mill Run | 1 | 3 | 2002-01-01 | 541974 | 247 | 541727 | 48.94% | 98.91% | 98.38% | 729.9697 | 2002-01-01 06:02 | 796030 | 541 | 4408203 | 4657694 | 217860 | 146478 | 168282 | 0 | 21683 | 6908 | 2002-02-01 00:01 | 1338004 | 788 | 6876004 | 7245188 | 250177 | 173203 | 178452 | 0 | 21729 | 6908 | 737.9847 | 737.9867 | 32317 | 0 | 46 | 7.4236 | 1 | 0.9932 | 0.9932 | 0.02778% | 0% | 3.954e-05% | 0.98782
Mill Run | 1 | 4 | 2002-01-01 | 571546 | 363 | 571183 | 51.53% | 97.85% | 97.32% | 723.1518 | 2002-01-01 04:59 | 1067894 | 1384 | 5478406 | 5905236 | 468359 | 326203 | 297048 | 0 | 14833 | 4082 | 2002-02-01 00:01 | 1639440 | 1747 | 7898070 | 8457747 | 508921 | 353084 | 314073 | 0 | 34956 | 7450 | 739.0181 | 739.0194 | 40562 | 3368 | 20123 | 7.4669 | 1 | 0.98124 | 0.98124 | 0.02778% | 0.002306% | 0.01378% | 0.97592
Mill Run | 1 | 5 | 2002-01-01 | 574172 | 418 | 573754 | 51.76% | 99.29% | 98.75% | 733.7448 | 2002-01-01 05:02 | 814098 | 2263 | 4278683 | 4861612 | 601703 | 165825 | 159085 | 0 | 41383 | 1 | 2002-02-01 00:01 | 1388270 | 2681 | 6778664 | 7458393 | 628770 | 193351 | 167929 | 0 | 41507 | 1 | 738.9814 | 738.9839 | 27067 | 0 | 124 | 7.6461 | 1 | 0.99517 | 0.99517 | 0.02778% | 0% | 0.0001273% | 0.98978
Mill Run | 1 | 6 | 2002-01-01 | 539907 | 281 | 539626 | 48.68% | 97.87% | 97.34% | 723.2996 | 2002-01-01 04:59 | 943419 | 1397 | 5337018 | 5883387 | 464346 | 310490 | 192953 | 0 | 83270 | 16488 | 2002-02-01 | 1483326 | 1678 | 7789418 | 8434009 | 532072 | 346408 | 199182 | 0 | 83270 | 16488 | 739.0247 | 739.0264 | 67726 | 0 | 0 | 9.9772 | 1 | 0.97985 | 0.97985 | 0.02778% | 0% | 0% | 0.97454
Mill Run | 1 | 7 3 | 2002-01-01 | 163125 | 3033 | 160092 | 13.94% | 50.08% | 49.76% | 383.4238 | 2002-01-01 00:01 | 535599 | 5245 | 2948441 | 3798783 | 2411154 | 793953 | 150098 | 0 | 43398 | 1564 | 2002-02-01 21:39 | 698724 | 8278 | 3753459 | 5981466 | 2629003 | 908909 | 191260 | 0 | 78870 | 79406 | 765.6486 | 741.6567 | 217849 | 833842 | 35472 | 31.9322 | 0.96866 | 0.60875 | 0.59603 | 0.02778% | 0.1063% | 0.004523% | 0.60557
Mill Run | 1 | 8 | 2002-01-01 | 593380 | 338 | 593042 | 53.5% | 96.4% | 95.87% | 712.3782 | 2002-01-01 04:59 | 994065 | 2263 | 5056500 | 5447766 | 647344 | 359891 | 248404 | 0 | 418875 | 10109 | 2002-02-01 | 1587445 | 2601 | 7486999 | 7962011 | 757102 | 386318 | 258413 | 0 | 418875 | 10109 | 739.0097 | 739.0108 | 109758 | 0 | 0 | 7.3408 | 1 | 0.96396 | 0.96396 | 0.02778% | 0% | 0% | 0.95874
Mill Run | 1 | 9 | 2002-01-01 | 572519 | 315 | 572204 | 51.62% | 97.99% | 97.46% | 724.1211 | 2002-01-01 05:04 | 796439 | 1423 | 4286211 | 4895858 | 245396 | 166056 | 197896 | 0 | 21863 | 29415 | 2002-02-01 00:01 | 1368958 | 1738 | 6769795 | 7455863 | 311677 | 192507 | 204165 | 0 | 21863 | 30632 | 738.95 | 738.9508 | 66281 | 1217 | 0 | 7.3475 | 1 | 0.97993 | 0.97993 | 0.02778% | 0.00051% | 0% | 0.97463
Mill Run | 1 | 10 | 2002-01-01 | 516718 | 589 | 516129 | 48.88% | 87.06% | 86.55% | 612.8004 | 2002-01-01 04:57 | 562191 | 2254 | 3032645 | 3605747 | 1238375 | 167105 | 158332 | 0 | 209795 | 15069 | 2002-01-30 12:50 | 1078909 | 2843 | 5091019 | 5804738 | 1528630 | 197298 | 172213 | 0 | 210472 | 15069 | 703.8833 | 703.8881 | 290255 | 0 | 677 | 8.3869 | 1 | 0.89025 | 0.89025 | 11.45% | 0% | 0.02672% | 0.88519
|  | Project, before line loss | 2002-01-01 | 5086855 | 6217 | 5080638 | 46.41% | 91.77% | 91.26% | 6705.5338 | [22 empty] | 7320.2517
|  | Assumed Line Loss2 | 2002-01-01 | 101737.1 | 124.34 | 101612.76 | Not applicable | Not applicable | Not applicable | Not applicable | [25 empty] | Turbine 7 had (31-18) days of offline time added in to correct availability.
|  | Project, after line loss | 2002-01-01 | 4985117.9 | 6092.66 | 4979025.24 | 46.41% | 91.77% | 91.26% | 6705.5338
|  | Project, after line loss | Year To Date | 4985117.9 | 6092.66 | 4979025.24 | 46.41% | 91.77% | 91.26% | 19905.9538
Notes:
1) Current month availability is based on values in Monthly file (labeled Monyymm where yy is year and mm is month) instead of SCADA screens.
2) The line loss is assumed to be 2% until sufficient data is collected to statistically determine the actual line loss.
3) Turbine 7 was offline from 1/18/02 to 2/1/02 but not set to repair time. Repair time in availability computation above was increased to correct for offline.
Hours Where WTG w/No kW in Good Winds
[7 empty] | 1 | 0
[7 empty] | 2 | 14
[7 empty] | 3 | 3
[7 empty] | 4 | 2
[7 empty] | 5 | 1.6667
[7 empty] | 6 | 0.83333
[7 empty] | 7 | 82.6667
[7 empty] | 8 | 0
[7 empty] | 9 | 0
[7 empty] | 10 | 13.8333

## 0202
Mill Run Project Operational Report For February 2002
Executive Summary
This interim report was generated to comply with the contractual monthly reporting requirement from the Windsystem, Operations, & Maintenance Agreement.
The description of safety near miss events, accidents, infrastructure work, and maintenance records are not included in this interim report.
All other required components are provided below. The Visupro data recovery was good at all turbines.
Turbine Performance
Operational Parameters
Site | Row | Pad | Reporting Month | kWhGenerated | kWhConsumed | Net kWh Production | Capacity Factor | Availability w/ constant MH | Availability w/o MH | Operating Hrs | AvailNumer | Availdenom
Mill Run | 1 | 1 | 2002-02-01 | 451762 | 389 | 451373 | 44.82% | 96.81% | 96.24% | 650.5546 | 643.8447 | 662.4545
Mill Run | 1 | 2 | 2002-02-01 | 367936 | 972 | 366964 | 36.5% | 88.6% | 88.08% | 595.3879 | 626.8536 | 664.2181
Mill Run | 1 | 3 | 2002-02-01 | 474658 | 280 | 474378 | 47.09% | 96.73% | 96.16% | 650.0546 | 665.0019 | 664.2439
Mill Run | 1 | 4 | 2002-02-01 | 487863 | 409 | 487454 | 48.4% | 96.61% | 96.04% | 649.2213 | 651.4461 | 660.8995
Mill Run | 1 | 5 | 2002-02-01 | 488884 | 331 | 488553 | 48.5% | 96.61% | 96.04% | 649.2213 | 638.3197 | 648.7084
Mill Run | 1 | 6 | 2002-02-01 | 417916 | 574 | 417342 | 41.46% | 96.64% | 96.06% | 649.3879 | 599.1494 | 663.7075
Mill Run | 1 | 7 | 2002-02-01 | 219110 | 2106 | 217004 | 21.74% | 94.06% | 93.5% | 632.0546 | 612.0981 | 664.1334
Mill Run | 1 | 8 3 | 2002-02-01 | 489475 | 546 | 488929 | 48.56% | 96.73% | 96.16% | 650.0546 | 1103.4772 | 774.935
Mill Run | 1 | 9 | 2002-02-01 | 501580 | 416 | 501164 | 49.76% | 96.73% | 96.16% | 650.0546 | 655.6136 | 664.2209
Mill Run | 1 | 10 | 2002-02-01 | 500093 | 333 | 499760 | 49.61% | 96.81% | 96.24% | 650.5546 | 649.8606 | 664.2792
|  | Project, before line loss | 2002-02-01 | 4399277 | 6356 | 4392921 | 43.64% | 95.63% | 95.07% | 6426.5459
|  | Assumed Line Loss2 | 2002-02-01 | 87985.54 | 127.12 | 87858.42 | Not applicable | Not applicable | Not applicable | Not applicable
|  | Project, after line loss | 2002-02-01 | 4311291.46 | 6228.88 | 4305062.58 | 43.64% | 95.63% | Not applicable | 6426.5459
|  | Project, after line loss | Year To Date | 9296409.36 | 12321.54 | 9284087.82 | 45.03% | 93.7% | 93.17% | 13132.0798
Notes:
1) Current month availability is based on values in Monthly file (labeled Monyymm where yy is year and mm is month) instead of SCADA screens.
Approximately 16 hours of data was not stored in SCADA due to grid outages given in the lower table. Line outages do not penalize contractual availability.
2) The line loss is assumed to be 2% until sufficient data is collected to statistically determine the actual line loss.
3) Turbine 8 was corrected for multiple meter resets in mid month. Data recovery was still high.
Hours of Avail Loss from Virtual Mode
[7 empty] | 1 | 0
[7 empty] | 2 | 55.1667
[7 empty] | 3 | 0.5
[7 empty] | 4 | 1.3333
[7 empty] | 5 | 1.3333
[7 empty] | 6 | 1.1667
[7 empty] | 7 | 18.5
[7 empty] | 8 | 0.5
[7 empty] | 9 | 0.5
[7 empty] | 10 | 0
Mill Run/Somerset
Line Outages
Chargeable to: A=AEP, N=Force Majeure, E=Enron, T= TXU
Month: | 2002-01-02 |  |  | Reason: U=unscheduled outage, S= scheduled outage, F=fluctuation
Charge | Date off | Time off | Date on | Time on | Hrs. | Reason | Comments
| 2002-02-09 | 1330 | 2002-02-09 | 0130 | 12 | U | A Phase fuse blown
| 12-Feb. | 1800 | 12-Feb. | 230 | 8.5 | U | C Phase fuse blown

## 0302
Mill Run Project Operational Report For March 2002
Executive Summary
This interim report was generated to comply with the contractual monthly reporting requirement from the Windsystem, Operations, & Maintenance Agreement.
The description of safety near miss events, accidents, infrastructure work, and maintenance records are not included in this interim report.
All other required components are provided below. The Visupro data recovery was good at all turbines. There were no curtailments or order out events.
Turbine Performance
|  |  |  | Operational Parameters | [7 empty] | Raw |  |  |  | Corrections
Site | Row | Pad | Reporting Month | kWhGenerated | kWhConsumed | Net kWh Production | Capacity Factor | Availability w/ constant MH | Availability w/o MH | Operating Hrs | Data Recovery | kWhgen | kWhcons | Avail,num | Avail, denom | kWhgen | kWhcons | Avail,num | Avail, denom
Mill Run | 1 | 1 | 2002-03-01 | 499742 | 394 | 499348 | 44.74% | 96.19% | 95.66% | 715.6447 | 100% | 499742 | 394 | 693.7978 | 721.2875
Mill Run | 1 | 2 | 2002-03-01 | 456593 | 569 | 456024 | 40.86% | 91.41% | 90.91% | 680.0868 | 100% | 456593 | 569 | 672.6578 | 722.9275
Mill Run | 1 | 3 | 2002-03-01 | 359103 | 617 | 358486 | 32.12% | 80.77% | 80.32% | 600.8958 | 100% | 359103 | 617 | 582.7167 | 720.8725
Mill Run | 1 | 4 | 2002-03-01 | 481180 | 722 | 480458 | 43.05% | 91.86% | 91.35% | 683.4068 | 100% | 481180 | 722 | 664.3622 | 722.5411
Mill Run | 1 | 5 | 2002-03-01 | 526562 | 394 | 526168 | 47.15% | 98.23% | 97.68% | 730.797 | 100% | 526562 | 394 | 706.3361 | 719.0972
Mill Run | 1 | 6 | 2002-03-01 | 506590 | 418 | 506172 | 45.36% | 97.04% | 96.51% | 722.01 | 100% | 506590 | 418 | 699.2883 | 720.5863
Mill Run | 1 | 7 | 2002-03-01 | 297493 | 2147 | 295346 | 26.46% | 88.01% | 87.52% | 654.7797 | 100% | 297493 | 2147 | 641.0261 | 721.1761
Mill Run | 1 | 8 3 | 2002-03-01 | 550994 | 647 | 550347 | 49.31% | 97.38% | 96.84% | 724.5205 | 100% | 2512228 | 3620 | 354.7228 | 721.4086 | -1961234 | -2973 | 349.4644 | -1e-06
Mill Run | 1 | 9 | 2002-03-01 | 520242 | 482 | 519760 | 46.57% | 96.2% | 95.67% | 715.7574 | 100% | 17525236 | 496 | 634.4381 | 661.2277 | -17004994 | -14 | 51.0408 | 50.4328
Mill Run | 1 | 10 | 2002-03-01 | 531940 | 438 | 531502 | 47.63% | 95.82% | 95.29% | 712.9193 | 100% | 531940 | 438 | 691.5056 | 719.5655
|  | Project, before line loss | 2002-03-01 | 4730439 | 6828 | 4723611 | 42.33% | 93.29% | 92.78% | 6940.8179
|  | Assumed Line Loss2 | 2002-03-01 | 94608.78 | 136.56 | 94472.22 | Not applicable | Not applicable | Not applicable | Not applicable
|  | Project, after line loss | 2002-03-01 | 4635830.22 | 6691.44 | 4629138.78 | Not applicable | Not applicable | Not applicable | 6940.8179
|  | Project, after line loss | Year To Date | 13932239.58 | 19012.98 | 13913226.6 | 44.13% | 93.57% | 93.04% | 20072.8977
Notes:
1) Current month availability is based on values in Monthly file (labeled Monyymm where yy is year and mm is month) instead of SCADA screens.
Approximately 16 hours of data was not stored in SCADA due to grid outages given in the lower table. Line outages do not penalize contractual availability.
2) The line loss is assumed to be 2% until sufficient data is collected to statistically determine the actual line loss.
3) Turbine 8 & 9 data were corrected to compensate for large jump in kWh meter readings between 3/1/02 and 3/2/02.
4) Turbine availability lowered due to shutting turbines down to limit noise.
Hours of Avail Loss from Virtual Mode
[7 empty] | 1 | 0
[7 empty] | 2 | 11.8333
[7 empty] | 3 | 0.5
[7 empty] | 4 | 0.66667
[7 empty] | 5 | 0
[7 empty] | 6 | 0
[7 empty] | 7 | 6.3333
[7 empty] | 8 | 1.6667
[7 empty] | 9 | 0.83333
[7 empty] | 10 | 2
Mill Run/Somerset
Line Outages
Month: | 2002-03-02 |  |  | Reason: U=unscheduled outage, S= scheduled outage, F=fluctuation
Charge | Date off | Time off | Date on | Time on | Hrs. | Reason | Comments
| 2002-03-17 19:00 | 19:00 | 2002-03-18 09:40 | 9:40 | 14.6667 | U | Severe Ice Storm
Grid Availability = |  | 98.03%

## 0402
Mill Run Project Operational Report For April 2002
Executive Summary
This interim report was generated to comply with the contractual monthly reporting requirement from the Windsystem, Operations, & Maintenance Agreement.
The description of safety near miss events, accidents, infrastructure work, and maintenance records are not included in this interim report.
All other required components are provided below. The Visupro data recovery was good at all turbines. There were no utility curtailments or grid outages.
Turbine Performance
|  |  |  | Operational Parameters | [7 empty] | Raw |  |  |  | Corrections
Site | Row | Pad | Reporting Month | kWhGenerated | kWhConsumed | Net kWh Production | Capacity Factor | Availability w/ constant MH | Availability w/o MH | Operating Hrs | Data Recovery | kWhgen | kWhcons | Avail,num | Avail, denom | kWhgen | kWhcons | Avail,num | Avail, denom
Mill Run | 1 | 1 | 2002-04-01 | 372027 | 342 | 371685 | 34.42% | 98.2% | 97.65% | 707.0271 | 1 | 372027 | 342 | 704.6461 | 716.0479
Mill Run | 1 | 2 | 2002-04-01 | 352917 | 425 | 352492 | 32.64% | 98.36% | 97.82% | 708.2244 | 1 | 352917 | 425 | 704.8481 | 715.5509
Mill Run | 1 | 3 | 2002-04-01 | 340084 | 382 | 339702 | 31.45% | 95.96% | 95.43% | 690.9181 | 1 | 340084 | 382 | 688.2219 | 715.8009
Mill Run | 1 | 4 | 2002-04-01 | 386590 | 483 | 386107 | 35.75% | 99.16% | 98.61% | 713.9467 | 0.96667 | 386590 | 483 | 711.69 | 716.0434
Mill Run | 1 | 5 | 2002-04-01 | 401449 | 334 | 401115 | 37.14% | 99% | 98.45% | 712.8223 | 1 | 401449 | 334 | 708.2869 | 715.419
Mill Run | 1 | 6 | 2002-04-01 | 381741 | 425 | 381316 | 35.31% | 98.96% | 98.41% | 712.4865 | 0.96667 | 381741 | 425 | 708.8089 | 715.9467
Mill Run | 1 | 7 3 | 2002-04-01 | 235673 | 2204 | 233469 | 21.62% | 96.79% | 96.25% | 696.9094 | 1 | 235673 | 2204 | 692.8597 | 710.134
Mill Run | 1 | 8 | 2002-04-01 | 380148 | 771 | 379377 | 35.13% | 91.39% | 90.88% | 658.0188 | 1 | 380148 | 771 | 654.3967 | 716.0367
Mill Run | 1 | 9 | 2002-04-01 | 328009 | 821 | 327188 | 30.3% | 78.59% | 78.16% | 565.8751 | 1 | 328009 | 821 | 562.615 | 715.852
Mill Run | 1 | 10 | 2002-04-01 | 424012 | 317 | 423695 | 39.23% | 99.28% | 98.73% | 714.7996 | 1 | 424012 | 317 | 711.6969 | 716.0354
|  | Project, before line loss | 2002-04-01 | 3602650 | 6504 | 3596146 | 33.3% | 95.57% | 95.04% | 6881.0278
|  | Assumed Line Loss2 | 2002-04-01 | 72053 | 130.08 | 71922.92 | Not applicable | Not applicable | Not applicable | Not applicable
|  | Project, after line loss | 2002-04-01 | 3530597 | 6373.92 | 3524223.08 | Not applicable | Not applicable | Not applicable | 6881.0278
|  | Project, after line loss | Year To Date | 17462836.58 | 25386.9 | 17437449.68 | 41.42% | 94.07% | 93.54% | 26953.9255
Notes:
1) Current month availability is based on values in Monthly file (labeled Monyymm where yy is year and mm is month) instead of SCADA screens.
2) The line loss is assumed to be 2% until sufficient data is collected to statistically determine the actual line loss.
3) Turbine 7 is ordered offline each day, from 8 PM to 6 AM next moring, to limit noise emissions.
Hours of Avail Loss from Virtual Mode
[7 empty] | 1 | 1.5
[7 empty] | 2 | 1
[7 empty] | 3 | 1.3333
[7 empty] | 4 | 1.6667
[7 empty] | 5 | 0
[7 empty] | 6 | 0.33333
[7 empty] | 7 | 5.5
[7 empty] | 8 | 0
[7 empty] | 9 | 0
Mill Run/Somerset | [6 empty] | 10 | 0.83333
Line Outages
Month: | 2002-03-02 |  |  | Reason: U=unscheduled outage, S= scheduled outage, F=fluctuation
Charge | Date off | Time off | Date on | Time on | Hrs. | Reason | Comments
| 2002-03-17 19:00 | 19:00 | 2002-03-18 09:40 | 9:40 | 14.6667 | U | Severe Ice Storm

## 0502
Mill Run Project Operational Report For May 2002
Executive Summary
This interim report was generated to comply with the contractual monthly reporting requirement from the Windsystem, Operations, & Maintenance Agreement.
The description of safety near miss events, accidents, infrastructure work, and maintenance records are not included in this interim report.
All other required components are provided below. The Visupro data recovery was good at all turbines. There were no utility curtailments or grid outages.
Turbine Performance
|  |  |  | Operational Parameters | [7 empty] | Raw |  |  |  | Corrections
Site | Row | Pad | Reporting Month | kWhGenerated | kWhConsumed | Net kWh Production | Capacity Factor | Availability w/ constant MH | Availability w/o MH | Operating Hrs | Data Recovery | kWhgen | kWhcons | Avail,num | Avail, denom | kWhgen | kWhcons | Avail,num | Avail, denom | Eanum | corr | EA
Mill Run | 1 | 1 | 2002-04-01 | 322471 | 661 | 321810 | 29.8% | 96.37% | 95.85% | 693.8303 | 1 | 322471 | 661 | 716.0233 | 739.9169 |  |  |  |  | 716.0297 | 0 | 0.96241
Mill Run | 1 | 2 | 2002-04-01 | 330081 | 643 | 329438 | 30.5% | 98.02% | 97.5% | 705.7622 | 0.96774 | 330081 | 643 | 728.7689 | 739.9002 |  |  |  |  | 728.7919 | 0 | 0.97956
Mill Run | 1 | 3 | 2002-04-01 | 312796 | 591 | 312205 | 28.91% | 93.63% | 93.13% | 674.1713 | 1 | 312796 | 591 | 695.425 | 739.8505 |  |  |  |  | 695.4978 | 0 | 0.93481
Mill Run | 1 | 4 | 2002-04-01 | 351658 | 801 | 350857 | 32.49% | 97.01% | 96.49% | 698.4621 | 1 | 351658 | 801 | 723.9381 | 739.9047 |  |  |  |  | 723.9567 | 0 | 0.97306
Mill Run | 1 | 5 | 2002-04-01 | 277231 | 1037 | 276194 | 25.57% | 86.43% | 85.97% | 622.2977 | 1 | 277231 | 1037 | 642.3469 | 739.9188 |  |  |  |  | 642.3514 | 0 | 0.86338
Mill Run | 1 | 6 | 2002-04-01 | 328215 | 799 | 327416 | 30.32% | 95.8% | 95.29% | 689.7634 | 1 | 328215 | 799 | 714.3442 | 739.9172 |  |  |  |  | 714.3503 | 0 | 0.96015
Mill Run | 1 | 7 3 | 2002-04-01 | 207965 | 2527 | 205438 | 19.02% | 97.68% | 97.15% | 703.2798 | 1 | 207965 | 2527 | 729.9028 | 739.9188 |  |  |  |  | 729.9072 | 0 | 0.98106
Mill Run | 1 | 8 | 2002-04-01 | 252459 | 1947 | 250512 | 23.2% | 70.52% | 70.14% | 507.737 | 1 | 252459 | 1947 | 525.085 | 739.8736 |  |  |  |  | 525.1347 | 0 | 0.70583
Mill Run | 1 | 9 | 2002-04-01 | 378187 | 669 | 377518 | 34.96% | 97.68% | 97.16% | 703.3286 | 1 | 378187 | 669 | 726.4361 | 739.9016 |  |  |  |  | 726.4578 | 0 | 0.97642
Mill Run | 1 | 10 | 2002-04-01 | 379624 | 505 | 379119 | 35.1% | 97.04% | 96.52% | 698.6907 | 1 | 379624 | 505 | 725.0008 | 739.8991 |  |  |  |  | 725.025 | 0 | 0.9745
|  | Project, before line loss | 2002-04-01 | 3140687 | 10180 | 3130507 | 28.99% | 93.02% | 92.52% | 6697.3233 | [11 empty] | 93.11%
|  | Assumed Line Loss2 | 2002-04-01 | 62813.74 | 203.6 | 62610.14 | Not applicable | Not applicable | Not applicable | Not applicable
|  | Project, after line loss | 2002-04-01 | 3077873.26 | 9976.4 | 3067896.86 | Not applicable | Not applicable | Not applicable | 6697.3233
|  | Project, after line loss | Year To Date | 20540709.84 | 35363.3 | 20505346.54 | 38.93% | 93.86% | 93.33% | 26770.2209
Notes:
1) Current month availability is based on values in Monthly file (labeled Monyymm where yy is year and mm is month) instead of SCADA screens.
2) The line loss is assumed to be 2% until sufficient data is collected to statistically determine the actual line loss.
3) Turbine 7 is ordered offline each day, from 8 PM to 6 AM next moring, to limit noise emissions.
Hours of Avail Loss from Virtual Mode
[7 empty] | 1 | 3
[7 empty] | 2 | 3.5
[7 empty] | 3 | 2.6667
[7 empty] | 4 | 6.1667
[7 empty] | 5 | 2.8333
[7 empty] | 6 | 5.5
[7 empty] | 7 | 7.1667
[7 empty] | 8 | 3.3333
[7 empty] | 9 | 3.6667
[7 empty] | 10 | 7
Mill Run/Somerset
Line Outages
Month: | 2002-03-02 |  |  | Reason: U=unscheduled outage, S= scheduled outage, F=fluctuation
Charge | Date off | Time off | Date on | Time on | Hrs. | Reason | Comments
| 2002-03-17 19:00 | 19:00 | 2002-03-18 09:40 | 9:40 | 14.6667 | U | Severe Ice Storm

## Summary
Mill Run Project Summary
Month | 2001-10-01 | 2001-11-01 | 2001-12-01 | 2002-01-01 | 2002-02-01 | 2002-03-01 | 2002-04-01 | 2002-05-01
Production, kWh
Monthly Generated kWh, Before Line Loss | 1363663 | 2861181 | 3554529 | 5086855 | 4399277 | 4730439 | 3602650 | 3140687
Monthly Assumed (2%) Line Loss | 27273.26 | 57223.62 | 71090.58 | 101737.1 | 87985.54 | 94608.78 | 72053 | 62813.74
Monthly Generated kWh, After Line Loss | 1336389.74 | 2803957.38 | 3483438.42 | 4985117.9 | 4311291.46 | 4635830.22 | 3530597 | 3077873.26
Monthly Generated MWh, After Line Loss | 1336.3897 | 2803.9574 | 3483.4384 | 4985.1179 | 4311.2915 | 4635.8302 | 3530.597 | 3077.8733
Projected Generated MWh, After Line Loss 1 | Not avail | Not avail | Not avail | Not avail | Not avail | Not avail | Not avail | Not avail
Production MWh Variance, From Projected | Not avail | Not avail | Not avail | Not avail | Not avail | Not avail | Not avail | Not avail
YTD Generated kWh, After Line Loss | 1336389.74 | 4140347.12 | 7623785.54 | 4985117.9 | 9296409.36 | 13932239.58 | 17462836.58 | 20540709.84
YTD Generated MWh, After Line Loss | 1336.3897 | 4140.3471 | 7623.7855 | 4985.1179 | 9296.4094 | 13932.2396 | 17462.8366 | 20540.7098
Availability
Monthly Contractual Availability | 90.11% | 87.32% | 85.89% | 91.77% | 95.63% | 93.29% | 95.57% | 93.02%
YTD Contractual Availability | 90.11% | 88.71% | 87.77% | 91.77% | 93.7% | 93.57% | 94.07% | 93.86%
Projected Contractual Availability 2
The 2002 availability data was lowered due to Virtual mode corrections.