## Template
ENRON NORTH AMERICA
TECHNICAL RISK REPORT
Business Unit | Project Name | Responsible Party | Project Type | $$ Exposure | Assessment of Risk | Updated | Update/Comments
OEC | New Albany | Dobler | Operation | $0.25 - $0.5 MM | Incremental expense to maintain refurbished Unit(s) to acceptable availability criteria. | 2000-07-31 | Potential problem with generator field on one unit similar to the failure experienced in May 00'.
OEC | Caledonia | Dobler | Operation |  | None present | 2000-07-31
OEC | Brownsville | Dobler | Operation |  | TN Air Pollution Board allocation of Nox credits. | 2000-07-31 | Increases in plant available run time could be impacted by unavailability of Nox credits beginning in 2Q 2003.
OEC | Gleason | Dobler | Operation | ? | 1) Inherent risk exposure to 501 F technology machines and any/all underlying design deficiencies that arise. 2)TN Air Pollution Board allocation of Nox credits. | 2000-07-31 | 1) Compressor diaphragm problem has resulted in significant delays to commercial operation and Mwe limits imposed on machines due to potential blade flutter problem could present difficulties in the near future. 2) Increases in plant available run time could be impacted by unavailability of Nox credits beginning in 2Q 2003.
OEC | Wheatland | Dobler | Operation |  | None present | 2000-07-31
OEC | Lincoln | Dobler | Operation | ? | 1) Final resolution of DLN combustion system capabilities to maintain acceptable emmision limits. 2)Brush generator failure on Unit 7. | 2000-07-31 | GE is in final stages of RCA and appear to have discovered some differences with our units versus the fleet. Potential solution will be forth coming. GE/Brush currently performing RCA for generator failure, due by September 00'.
OEC | Doyle | Dobler | Operation | $ 1 - $ 2 MM | 1) Continued difficulties with H2 cooled generator on Unit 1 leakage rates that could hamper economical operation. 2) Ongoing cost associated with refurbished turbines (Units 1,2 & 3) to maintain acceptable availability levels. | 2000-07-31 | Significant delays for commercial operation has resulted from generator deficiencies and numerous minor components continue to cause unexpected outages.