## Drip Samples
Drip Sampling Log
Routing; Johnson K, Anderson D, Boschee R, Garcia J, Lytle D, Russell C, Wong M, McCurdy R, Estrada T, Bell R, Waligora R, lcampbe@enron.com
Date Sample Taken | Location of Sample | Laboratory Used | Date Shipped | Date Results Received | Tested for Title 22 Metals | PG&E PCB Test Results/ppm | PG&E PCB Aroclor Type | TW PCB Test Result/ppm | Total Volume Removed | Average PCB Concentration | Comments
2000-01-19 | PGE MP 103B Mist 1-19-00-L | Sherwood | 2000-01-20 | 2000-01-26 |  | ND | na | na | na | na
2000-01-19 | PGE MP 103B MLV 1-19-00-W | Sherwood | 2000-01-20 | 2000-01-26 |  | ND | na | na | na | na | Wipe Sample
2000-01-19 | PGE MP 103A PG Mist 1-19-00-L | Sherwood | 2000-01-20 | 2000-01-26 |  | <1 | na | na | na | na
2000-01-19 | PGE MP 103A V-3 1-19-00-W | Sherwood | 2000-01-20 | 2000-01-26 |  | <1 ug/100 sqcm | na | na | na | na | Wipe Sample
2000-01-19 | PGE Mp 40.49B PG Mist 1-19-00-L | Sherwood | 2000-01-20 | 2000-01-26 |  | ND | na | na | na | na
2000-01-19 | PGE MP 40.49B V-6 1-19-00-W | Sherwood | 2000-01-20 | 2000-01-26 |  | 1.2 ug/100 sqcm | 1016 | na | na | na | Wipe Sample
2000-01-19 | PGE MP 40.87A PG Mist 1-19-00-L | Sherwood | 2000-01-20 | 2000-01-26 |  | ND | na | na | na | na
2000-01-19 | PGE MP 40.87A V-3 1-19-00-W | Sherwood | 2000-01-20 | 2000-01-26 |  | <1 ug/100 sqcm | na | na | na | na | Wipe Sampe
2000-01-19 | PGE NeedlesTapIntakePot 1-19-00*W | Sherwood | 2000-01-20 | 2000-01-26 |  | 8 ug/100 sq cm | 1016/1260 | na | na | na | Wipe Samples
2000-01-19 | PGE-TW2 01-19-00-L | na | na | na |  | na | na | na | na | na
2000-01-19 | PGE TOP3 01-19-00-L | na | na | na |  | na | na | na | na | na
2000-01-19 | PGE TOP4 01-19-00-L | na | na | na |  | na | na | na | na | na
2000-01-19 | PGE 0.55B 01-19-00-L | Sherwood | 2000-01-19 | 2000-01-21 |  | 17 | 1016 | 32 | 7 oz | 24.5
2000-01-19 | PGE 10.84A 01-19-00-L | Sherwood | 2000-01-19 | 2000-01-21 |  | 8 | 1016 | 18 | 2 oz | 13
2000-01-19 | PGE 10.47B 01-19-00-L | Sherwood | 2000-01-19 | 2000-01-21 |  | 1 | 1016 | 2 | 1 oz | 1.5
2000-01-19 | PGE 15.33A 01-19-00-L | Sherwood | 2000-01-19 | 2000-01-21 |  | 24 | 1016 | 28 | 20 oz | 26
2000-01-07 | PGE MP71.98A Reg 1-7-00-W | Sherwood | 2000-01-07 | 2000-01-11 |  | <2 ug/100 sqcm |  | na | na | na | Wipe Sample detection limit raised due to matrix effects. Aroclor 1260 present at <1 ug/100 sqcm
2000-01-07 | PGE MP65A Tap 1-7-00-W | Sherwood | 2000-01-07 | 2000-01-11 |  | ND |  | na | na | na | Wipe Sample
2000-01-07 | PGE MP63.36A Tap 1-7-00-W | Sherwood | 2000-01-07 | 2000-01-11 |  | 3 ug/100 sqsm | 1260 | na | na | na | Wipe Sample
2000-01-07 | PGE MP62.98A Tap 1-7-00-W | Sherwood | 2000-01-07 | 2000-01-11 |  | ND |  | na | na | na | Wipe Sample
2000-01-07 | PGE MP40.49B PGMist 1-7-00-L | Sherwood | 2000-01-07 | 2000-01-11 |  | <1 |  | na | na | na
2000-01-07 | PGE MP40.49B V-6 1-7-00-W | Sherwood | 2000-01-07 | 2000-01-11 |  | ND<2 ug/100 sqcm |  | na | na | na | Wipe Sample detection limit raised due to matrix interference
2000-01-07 | PGE MP40.87A PGMist 1-7-00-L | Sherwood | 2000-01-07 | 2000-01-11 |  | ND |  | na | na | na
2000-01-07 | PGE MP40.87A MLV 1-7-00-W | Sherwood | 2000-01-07 | 2000-01-11 |  | ND<3 ug/100 sqcm |  | na | na | na | Wipe Sample detection limit raised due to matrix interference
2000-01-07 | Needles Tap Intake Pot - W | Sherwood | 2000-01-07 | 2000-01-11 |  | <7 ug/100 sqcm |  | na | na | na | Wipe Sample detection limit raised due to matrix effects. Aroclor 1260 present at <1 ug/100 sqcm
2000-01-05 | PGE 103A PG Mist 1-5-00-L | Sherwood | 2000-01-07 | 2000-01-11 |  | ND |  | na |  | na
2000-01-06 | PGE 103B PG Mist 1-6-00-L | Sherwood | 2000-01-07 | 2000-01-11 |  | ND |  | na |  | na
2000-01-06 | PGE MP62 All-Amer-W | Sherwood | 2000-01-07 | 2000-01-11 |  | ND<7 ug/100sqcm | 1016 | na |  | na | Wipe Samples detection limit raised due to matrix interference. Peak pattern not consistent with known Aroclors
2000-01-06 | PGE MP62 All-Amer-L | Sherwood | 2000-01-07 | 2000-01-11 |  | 1 |  | na |  | na
2000-01-06 | Amboy Secondary Reg Station | Sherwood | 2000-01-07 | 2000-01-11 |  | ND |  | na |  | na | Wipe Samples
2000-01-06 | PGE MP103A Heater | Sherwood | 2000-01-07 | 2000-01-11 |  | ND<20 ug/100sqcm |  | na |  | na | Wipe Samples detection limit raised due to matrix interference. Peak pattern not consistent with known Aroclors
2000-01-06 | PGE MP103A Heater Lid | Sherwood | 2000-01-07 | 2000-01-11 |  | ND<10 ug/100 sqcm |  | na |  | na | Wipe Samples detection limit raised due to matrix interference. Peak pattern not consistent with known Aroclors
2000-01-06 | PGE MP74A Amboy Primary | Sherwood | 2000-01-07 | 2000-01-11 |  | ND<2 ug/100 sqcm |  | na |  | na | Wipe Samples detection limit raised due to matrix interference. Peak pattern not consistent with known Aroclors
2000-01-05 | PGE-TW2 12-29-99-L | na | na | na | na | na |  | na | na | na
2000-01-05 | PGE TOP3 12-29-99-L | na | na | na | na | na |  | na | na | na
2000-01-05 | PGE TOP4 12-29-99-L | na | na | na | na | na |  | na | na | na
2000-01-05 | PGE 0.55B 12-29-99-L | Sherwood | 2000-01-07 | 2000-01-11 |  | 17 | 1016 | 21 |  | 19
2000-01-05 | PGE 10.84A 12-29-99-L | Sherwood | 2000-01-07 | 2000-01-11 |  | 9 | 1016 | 7 |  | 8
2000-01-05 | PGE 10.47B 12-29-99-L | na | na | na |  | na |  | na | na | na
2000-01-05 | PGE 15.33A 12-29-99-L | Sherwood | 2000-01-07 | 2000-01-11 |  | 33 | 1016 | 32 |  | 32.5
1999-12-31 | PGE MP 103A Valve | Sherwood | 2000-01-03 | 2000-01-05 |  | ND |  | na | na | na | Wipe Samples
1999-12-31 | PGE MP 103A Insertion Meter | Sherwood | 2000-01-03 | 2000-01-05 |  | ND |  | na | na | na | Wipe Samples
1999-12-31 | PGE MP103B Valve | Sherwood | 2000-01-03 | 2000-01-05 |  | ND<2 ug/100 sqcm |  | na | na | na | Wipe Samples detection limit raised due to matrix interference
1999-12-31 | PGE MP 103B Insertion Meter | Sherwood | 2000-01-03 | 2000-01-05 |  | ND<2 ug/100 sqcm |  | na | na | na | Wipe Samples detection limit raised due to matrix interference
1999-12-30 | PGE MP 40B Insertion Meter | Sherwood | 1999-12-31 | 2000-01-04 |  | ND <5 ug/100sqcm |  | na | na | na | Wipe Samples detection limit raised due to matrix interference
1999-12-30 | PGE MP 40B Valve | Sherwood | 1999-12-31 | 2000-01-04 |  | ND <5 ug/100sqcm |  | na | na | na | Wipe Samples detection limit raised due to matrix interference
1999-12-30 | PGE MP 40A Insertion Meter | Sherwood | 1999-12-31 | 2000-01-04 |  | ND <5 ug/100sqcm |  | na | na | na | Wipe Samples detection limit raised due to matrix interference
1999-12-30 | PGE MP 40A Valve | Sherwood | 1999-12-31 | 2000-01-04 |  | ND <5 ug/100sqcm |  | na | na | na | Wipe Samples detection limit raised due to matrix interference
1999-12-29 | Southwest Gas Meter Park Moabi Mtr# 116902 | Sherwood | 1999-12-31 | 2000-01-04 |  | ND |  | nD | na | ND | Wipe Samples
1999-12-29 | Southwest Gas Meter Needles Mtr # R384072 | Sherwood | 1999-12-31 | 2000-01-04 |  | ND |  | ND | na | ND | Wipe Samples
1999-12-29 | PGE-TW2 12-29-99-L | na | na | na | na | na |  | na | na | na
1999-12-29 | PGE TOP3 12-29-99-L | na | na | na | na | na |  | na | na | na
1999-12-29 | PGE TOP4 12-29-99-L | na | na | na | na | na |  | na | na | na
1999-12-29 | PGE 0.55B 12-29-99-L | Sherwood | 1999-12-31 | 2000-01-04 |  | 29 |  | 31 | 8 oz | 30
1999-12-29 | PGE 10.84A 12-29-99-L | Sherwood | 1999-12-31 | 2000-01-04 |  | 16 |  | 14 | 4 oz | 15
1999-12-29 | PGE 10.47B 12-29-99-L | Sherwood | 1999-12-31 | 2000-01-04 |  | 2 |  | 2 | 1 oz | 2
1999-12-29 | PGE 15.33A 12-29-99-L | Sherwood | 1999-12-31 | 2000-01-04 |  | 30 |  | 27 | 10 oz | 28.5
1999-12-24 | Needles Tap Pot Intake | Sherwood | 1999-12-24 | 1999-12-28 |  | 2.4 ug/100sqcm | 1016/60 | na | na | na | Wipe Samples
1999-12-24 | Needles Tap Pot | Sherwood | 1999-12-24 | 1999-12-28 |  | <1 ug/100sqcm |  | na | na | na | Wipe Samples
1999-12-24 | Needles Tap Pot Discharge | Sherwood | 1999-12-24 | 1999-12-28 |  | 1.7 ug/100sqcm | 1016/60 | na | na | na | Wipe Samples
1999-12-24 | Needles Tap Meter | Sherwood | 1999-12-24 | 1999-12-28 |  | 5.7 ug/100sqcm | 1016/60 | na | na | na | Wipe Samples
1999-12-24 | Needles Tap Meter Discharge | Sherwood | 1999-12-24 | 1999-12-28 |  | 2.5 ug/100sqcm | 1016/60 | na | na | na | Wipe Samples
1999-12-21 | Needles Tap Pot Intake | Sherwood | 1999-12-22 | 1999-12-23 |  | 4 ug/100sqcm | 1016/60 | na | na | na | Wipe Samples
1999-12-21 | Needles Tap Pot | Sherwood | 1999-12-22 | 1999-12-23 |  | 1.7 ug/100sqcm | 1016/60 | na | na | na | Wipe Samples
1999-12-21 | Needles Tap Pot Discharge | Sherwood | 1999-12-22 | 1999-12-23 |  | <1 ug/100sqcm |  | na | na | na | Wipe Samples
1999-12-21 | Needles Tap Screen | Sherwood | 1999-12-22 | 1999-12-23 |  | 17 | 1016/60 | na | na | na
1999-12-14 | PGE-TW2 12-14-99-L | na | na | na |  | na |  | na | na | na | No liqiud
1999-12-14 | PGE TOP3 12-14-99-L | na | na | na |  | na |  | na | na | na | No liqiud
1999-12-14 | PGE TOP4 12-14-99-L | na | na | na |  | na |  | na | na | na | No liqiud
1999-12-14 | PGE 0.55B 12-14-99-L | Sherwood | 1999-12-14 | 1999-12-16 |  | 21 | 1016 | 23 | 3 oz | 22
1999-12-14 | PGE 10.84A 12-14-99-L | Sherwood | 1999-12-14 | 1999-12-16 |  | 9 | 1016 | 15 | 2 oz | 12
1999-12-14 | PGE 10.47B 12-14-99-L | na | na | na |  | na |  | na | na | na | No liqiud
1999-12-14 | PGE 15.33A 12-14-99-L | Sherwood | 1999-12-14 | 1999-12-16 |  | 39 | 1016 | 39 |  | 39
1999-12-08 | PGE-TW2 12-08-99-L | na | na | na |  | na |  | na | na | na | No liqiud
1999-12-08 | PGE TOP3 12-08-99-L | na | na | na |  | na |  | na | na | na | No liqiud
1999-12-08 | PGE TOP4 12-08-99-L | na | na | na |  | na |  | na | na | na | No liqiud
1999-12-08 | PGE 0.55B 12-08-99-L | Sherwood | 1999-12-09 | 1999-12-13 |  | 30 |  | 33 |  | 31.5
1999-12-08 | PGE 10.84A 12-08-99-L | Sherwood | 1999-12-09 | 1999-12-13 |  | 13 |  | 13 |  | 13
1999-12-08 | PGE 10.47B 12-08-99-L | na | na | na |  | na |  | na | na | na | No liqiud
1999-12-08 | PGE 15.33A 12-08-99-L | Sherwood | 1999-12-09 | 1999-12-13 |  | 35 |  | 36 |  | 35.5
1999-12-03 | PGE MP 103A Valve | Sherwood | 1999-12-06 | 1999-12-08 |  | <1 ug/100sqcm |  | na | na | na | Wipe Samples
1999-12-03 | PGE MP 103A Insertion Meter | Sherwood | 1999-12-06 | 1999-12-08 |  | <1 ug/100sqcm |  | na | na | na | Wipe Samples
1999-12-03 | PGE MP 103 A & B Blank | Sherwood | 1999-12-06 | 1999-12-08 |  | ND |  | na | na | na | Wipe Samples
1999-12-03 | PGE MP 103B Insertion Meter | Sherwood | 1999-12-06 | 1999-12-08 |  | <1 ug/100sqcm |  | na | na | na | Wipe Samples
1999-12-03 | PGE MP 103B Valve | Sherwood | 1999-12-06 | 1999-12-08 |  | 1.3 ug/100sqcm | 1016 | na | na | na | Wipe Samples
1999-12-03 | PGE MP 40A Valve | Sherwood | 1999-12-06 | 1999-12-08 |  | 1.8 ug/100sqcm | 1016 | na | na | na | Wipe Samples
1999-12-03 | PGE MP40 A & B Blank | Sherwood | 1999-12-06 | 1999-12-08 |  | ND |  | na | na | na | Wipe Samples
1999-12-03 | PGE MP 40A Insertion Meter | Sherwood | 1999-12-06 | 1999-12-08 |  | 1.0 ug/100sqcm | 1016 | na | na | na | Wipe Samples
1999-12-03 | PGE MP 40B Valve | Sherwood | 1999-12-06 | 1999-12-08 |  | 1.6 ug/100sqcm |  | na | na | na | Wipe Samples
1999-12-03 | PGE MP 40B Insertion Meter | Sherwood | 1999-12-06 | 1999-12-08 |  | 1.7 ug/100sqcm |  | na | na | na | Wipe Samples
1999-12-01 | PGE MP 169.95B 12-1-99-L | Sherwood | 1999-12-06 | 1999-12-08 |  | <1 |  | na | na | na
1999-10-29 | A Tower Valve A16 Intake | Sherwood | 1999-10-29 | 1999-11-02 |  | 31 ug/100sqcm |  | na | na | na | Wipe Samples
1999-10-29 | A Tower Bundle Discharge | Sherwood | 1999-10-29 | 1999-11-02 |  | 32 ug/100sqcm |  | na | na | na | Wipe Samples
1999-10-29 | A Tower Bundle Intake | Sherwood | 1999-10-29 | 1999-11-02 |  | 19 ug/100sqcm |  | na | na | na | Wipe Samples
1999-10-29 | A Tower Valve A30 Discharge | Sherwood | 1999-10-29 | 1999-11-02 |  | 3 ug/100sqcm |  | na | na | na | Wipe Samples
1999-10-29 | A Tower Valve 28 Bundle Intake | Sherwood | 1999-10-29 | 1999-11-02 |  | 18 ug/100sqcm |  | na | na | na | Wipe Samples
1999-10-29 | A Tower Valve 44 Bundle Intake | Sherwood | 1999-10-29 | 1999-11-02 |  | 34 ug/100sqcm |  | na | na | na | Wipe Samples
1999-10-29 | A Tower Valve A76 Intake | Sherwood | 1999-10-29 | 1999-11-02 |  | 12 ug/100sqcm |  | na | na | na | Wipe Samples
1999-10-29 | A Tower Valve A78 Discharge | Sherwood | 1999-10-29 | 1999-11-02 |  | 59 ug/100sqcm |  | na | na | na | Wipe Samples
1999-10-29 | A Tower Intake | Sherwood | 1999-10-29 | 1999-11-02 |  | <1 ug/100sqcm |  | na | na | na | Wipe Samples
1999-10-29 | A Tower Blank | Sherwood | 1999-10-29 | 1999-11-02 |  | ND |  | na | na | na | Wipe Samples
1999-12-01 | PGE-TW2 12-01-99-L | na | na | na |  | na |  | na | na | na | No liqiud
1999-12-01 | PGE TOP3 12-01-99-L | na | na | na |  | na |  | na | na | na | No liqiud
1999-12-01 | PGE TOP4 12-01-99-L | na | na | na |  | na |  | na | na | na | No liqiud
1999-12-01 | PGE 0.55B 12-01-99-L | Sherwood | 1999-12-01 | 1999-12-06 |  | 47 |  | 38 | 16 oz | 42.5
1999-12-01 | PGE 10.84A 12-01-99-L | Sherwood | 1999-12-01 | 1999-12-06 |  | 11 |  | 11 | 2 oz | 11
1999-12-01 | PGE 10.47B 12-01-99-L | Sherwood | 1999-12-01 | 1999-12-06 |  | 3 |  | 3 | 1 oz | 3
1999-12-01 | PGE 15.33A 12-01-99-L | Sherwood | 1999-12-01 | 1999-12-06 |  | 25 |  | 26 | 16 oz | 25.5
1999-11-24 | PGE-TW2 11-24-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-11-24 | PGE TOP3 11-24-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-11-24 | PGE TOP4 11-24-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-11-24 | PGE 0.55B 11-24-99-L | Sherwood | 1999-11-24 | 1999-11-30 |  | 44 |  | 41 | 4 oz | 42.5
1999-11-24 | PGE 10.84A 11-24-99-L | Sherwood | 1999-11-24 | 1999-11-30 |  | 13 |  | 11 | 6 oz | 12
1999-11-24 | PGE 10.47B 11-24-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-11-24 | PGE 15.33A 11-24-99-L | Sherwood | 1999-11-24 | 1999-11-30 |  | 10 |  | 20 | 16 oz | 15
1999-11-18 | PGE-TW 2 11-18-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-11-18 | PGE TOP 3 11-18-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-11-18 | PGE TOP4 11-18-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-11-18 | PGE 0.55B 11-18-99-L | Sherwood | 1999-11-19 | 1999-11-23 |  | 26 |  | 29 | 4 oz | 27.5
1999-11-18 | PGE 10.84A 11-18-99-L | Sherwood | 1999-11-19 | 1999-11-23 |  | 22 |  | 22 | 2 oz | 22
1999-11-18 | PGE 10.47B 11-18-99-L | na | na | na |  | na |  | na | na | na | No liqiud
1999-11-18 | PGE 15.33A 11-18-99-L | Sherwood | 1999-11-19 | 1999-11-23 |  | 18 |  | 20 | 1 oz | 19
1999-11-03 | PGE-TW2 11-03-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-11-03 | PGE TOP3 11-03-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-11-03 | PGE TOP4 11-03-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-11-03 | PGE 0.55B 11-2-99-L | Sherwood | 1999-11-03 | 1999-11-05 |  | 14 |  | na | na | 14
1999-11-03 | PGE 10.84A 11-03-99-L | Sherwood | 1999-11-03 | 1999-11-05 |  | 16 |  | 17 | 2oz | 16.5
1999-11-03 | PGE 10.47B 11-03-99-L | Sherwood | 1999-11-03 | 1999-11-05 |  | <1 |  | 1 | 2oz | 1
1999-11-03 | PGE 15.33A 11-03-99-L | Sherwood | 1999-11-03 | 1999-11-05 |  | 18 |  | 18 | 10oz | 18
1999-10-27 | PGE TW 2 10-27-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-10-27 | PGE TOP3 10-27-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-10-27 | PGE TOP4 10-27-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-10-27 | PGE 10.84A 10-27-99-L | Sherwood | 1999-10-28 | 1999-11-02 |  | 19 |  | 18 | 4 oz | 18.5
1999-10-27 | PGE 10.47B 10-27-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-10-27 | PGE 15.33A 10-27-99-L | Sherwood | 1999-10-28 | 1999-11-02 |  | 27 |  | 22 | 30 oz | 24.5
1999-10-20 | PGE TW2 10-20-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-10-20 | PGE TOP3 10-20-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-10-20 | PGE TOP4 10-20-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-10-20 | PGE 10.84A 10-20-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-10-20 | PGE 10.47B 10-20-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-10-20 | PGE 15.33A 10-20-99-L | Sherwood | 1999-10-21 | 1999-10-25 |  | 28 |  | 29 | 10oz | 28.5
1999-10-14 | PGE TW2 10-14-99-L | na | na | na | na | na |  | na | na | 0 | No liqiud
1999-10-14 | PGE TOP3 10-14-99-L | na | na | na | na | na |  | na | na | 0 | No liqiud
1999-10-14 | PGE TOP4 10-14-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-10-14 | PGE 10.84A 10-14-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-10-14 | PGE 10.47B 10-14-99-L | Sherwood | 1999-10-14 | 1999-10-18 |  | 2 |  | 1 | 1/2oz | 1.5
1999-10-14 | PGE 15.33A 10-14-99-L | Sherwood | 1999-10-14 | 1999-10-18 |  | 10 |  | 15 | 30oz | 12.5
1999-10-06 | PGE-TW2 10-6-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-10-06 | PGE TOP3 10-6-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-10-06 | PGE TOP4 10-6-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-10-06 | PGE 10.84A 10-6-99-L | Sherwood | 1999-10-06 | 1999-10-12 |  | 9 |  | 8 | 2oz | 8.5
1999-10-06 | PGE 10.47B 10-6-99-L | na | na | na |  | na |  | na | na | na | No liqiud
1999-10-06 | PGE 15.33A 10-6-99-L | Sherwood | 1999-10-06 | 1999-10-12 |  | 8 |  | 9 | 1oz | 8.5
1999-09-30 | PGE-TW2 9-30-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-09-30 | PGE TOP3 9-30-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-09-30 | PGE TOP4 9-30-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-09-30 | PGE 10.84A 9-30-99-L | Sherwood | 1999-09-30 | 1999-10-05 |  | 4 |  | 4 | 1oz | 4
1999-09-30 | PGE 10.47B 9-30-99-L | Sherwood | 1999-09-30 | 1999-10-05 |  | <1 |  | <1 | 2oz | <1
1999-09-30 | PGE 15.33A 9-30-99-L | Sherwood | 1999-09-30 | 1999-10-05 |  | 7 |  | 8 | 10oz | 7.5
1999-09-23 | PGE TW2 9-23-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-09-23 | PGE TOP3 9-23-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-09-23 | PGE TOP4 9-23-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-09-23 | PGE 10.84A 9-23-99-L | Sherwood | 1999-09-24 | 1999-09-28 |  | 5 |  | 4 | 2 oz | 4.5
1999-09-23 | PGE 10.47B 9-23-99-L | Sherwood | 1999-09-24 | 1999-09-28 |  | 1 |  | 2 | 1 oz | 1.5
1999-09-23 | PGE 15.33A 9-23-99-L | Sherwood | 1999-09-24 | 1999-09-28 |  | 5 |  | 5 | 8 oz | 5
1999-09-23 | PGE 8.58A 9-23-99-L | Sherwood | 1999-09-24 | 1999-09-28 |  | 6 |  | na | 1/2 Gal | 6
1999-09-23 | PGE 5.08A 9-23-99-L | Sherwood | 1999-09-24 | 1999-09-28 |  | 6 |  | na | 1 Gal | 6
1999-09-23 | PGE 3.16A 9-23-99-L | Sherwood | 1999-09-24 | 1999-09-28 |  | 6 |  | na | 2 Gal | 6
1999-09-23 | PGE 0.13A 9-23-99-L | Sherwood | 1999-09-24 | 1999-09-28 |  | 0 |  | na | 20 Gal | 0 | El Paso Intake only
1999-09-16 | PGE-TW 2 9-16-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-09-16 | PGE Top3 9-16-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-09-16 | PGE TOP4 9-16-99-L | na | na | na | na | na |  | na | na | na | No liqiud
1999-09-16 | PGE 10.84A 9-16-99-L | Sherwood | 1999-09-16 | 1999-09-20 |  | 4 |  | 4 | 4 oz | 4
1999-09-16 | PGE 10.47B 9-16-99-L | Sherwood | 1999-09-16 | 1999-09-20 |  | <1 |  | <1 | 1 oz | <1
1999-09-16 | PGE 15.33A 9-16-99-L | Sherwood | 1999-09-16 | 1999-09-20 |  | 4 |  | 4 | 6 oz | 4
1999-09-14 | PGE TOP4 9-14-99-L | Sherwood | 1999-09-16 | 1999-09-20 |  | 35 |  |  | 4 oz | 35 | PGE Only
1999-09-12 | PGE TOP6 9-12-99-L | Sherwood | 1999-09-16 | 1999-09-20 |  | 71 |  |  | 4 oz | 71 | PGE Only