## Drip Samples
Drip Sampling Log
Routing; Anderson D, Boschee R, Blevins W, Lytle D, Wong M, McCurdy R, Bell R, lcampbe@enron.com
Date Sample Taken | Location of Sample | Laboratory Used | Date Shipped | Date Results Received | Tested for Title 22 Metals | PG&E PCB Test Results/ppm | PG&E PCB Aroclor Type | TW PCB Test Result/ppm | Total Volume Removed | Average PCB Concentration | Comments
2000-11-08 | PGE-TW2 | na | na | na | na | na | na | na | na | na
2000-11-08 | PGE TOP3 | na | na | na | na | na | na | na | na | na
2000-11-08 | PGE TOP4 | na | na | na | na | na | na | na | na | na
2000-11-08 | PGE 0.55B | na | na | na | na | na | na | na | na | na
2000-11-08 | PGE 10.84A 11-8-00-L | Sherwood | 2000-11-10 | 2000-11-15 |  | 15 | 1242 | 15 | 3 oz | 15
2000-11-08 | PGE 10.47B | na | na | na | na | na | na | na | na | na
2000-11-08 | PGE 15.33A 11-8-00-L | Sherwood | 2000-11-10 | 2000-11-15 |  | 12 | 1242 | 11 | 4 oz | 11.5
2000-11-08 | PGE 27.15A | na | na | na | na | na | na | na | na | na
2000-11-08 | PGE 27.15B | na | na | na | na | na | na | na | na | na
2000-11-08 | PGE 63.26A 11-8-00-L | Sherwood | 2000-11-10 | 2000-11-15 |  | 18 | 1242 | 17 | 1 oz | 17.5
2000-11-08 | PGE 63.26B 11-8-00-L | Sherwood | 2000-11-10 | 2000-11-15 |  | 18 | 1242 | 18 | 2 oz | 18
2000-11-08 | PGE 84.10A | na | na | na | na | na | na | na | na | na
2000-10-18 | PGE-TW2 | na | na | na | na | na | na | na | na | na
2000-10-18 | PGE TOP3 | na | na | na | na | na | na | na | na | na
2000-10-18 | PGE TOP4 | na | na | na | na | na | na | na | na | na
2000-10-18 | PGE 0.55B 10-18-00-L | Sherwood | 2000-10-19 | 2000-10-23 |  | 5 | 1242 | 5 | 1/2 oz | 5
2000-10-18 | PGE 10.84A 10-18-00-L | Sherwood | 2000-10-19 | 2000-10-23 |  | 16 | 1242 | 16 | 1 oz | 16
2000-10-18 | PGE 10.47B | na | na | na | na | na | na | na | na | na
2000-10-18 | PGE 15.33A | na | na | na | na | na | na | na | na | na
2000-10-18 | PGE 27.15A | na | na | na | na | na | na | na | na | na
2000-10-18 | PGE 27.15B | na | na | na | na | na | na | na | na | na
2000-10-18 | PGE 63.26A 10-18-00-L | Sherwood | 2000-10-19 | 2000-10-23 |  | 14 | 1242 | 13 | 1 oz | 13.5
2000-10-18 | PGE 63.26B 10-18-00-L | Sherwood | 2000-10-19 | 2000-10-23 |  | 14 | 1242 | 15 | 1 3/4 oz | 14.5
2000-10-18 | PGE 84.10A 10-18-00-L | Sherwood | 2000-10-19 | 2000-10-23 |  | 14 | 1242 | 14 | 2 oz | 14
2000-10-04 | PGE-TW2 | na | na | na | na | na | na | na | na | na
2000-10-04 | PGE TOP3 | na | na | na | na | na | na | na | na | na
2000-10-04 | PGE TOP4 | na | na | na | na | na | na | na | na | na
2000-10-04 | PGE 0.55B 10-04-00-L | Sherwood | 2000-10-05 | 2000-10-09 |  | 5 | 1242 | 6 | 1 oz | 5.5
2000-10-04 | PGE 10.84A 10-04-00-L | Sherwood | 2000-10-05 | 2000-10-09 |  | 18 | 1242 | 19 | 1 oz | 18.5
2000-10-04 | PGE 10.47B | na | na | na | na | na | na | na | na | na
2000-10-04 | PGE 15.33A 10-04-00-L | Sherwood | 2000-10-05 | 2000-10-09 |  | 15 | 1242 | 14 | 2 oz | 14.5
2000-10-04 | PGE 27.15A | na | na | na | na | na | na | na | na | na
2000-10-04 | PGE 27.15B | na | na | na | na | na | na | na | na | na
2000-10-04 | PGE 63.26A 10-04-00-L | Sherwood | 2000-10-05 | 2000-10-09 |  | 15 | 1242 | 15 | 2 oz | 15
2000-10-04 | PGE 63.26B 10-04-00-L | Sherwood | 2000-10-05 | 2000-10-09 |  | 16 | 1242 | 16 | 1 oz | 16
2000-10-04 | PGE 84.10A 10-04-000-L | Sherwood | 2000-10-05 | 2000-10-09 |  | 17 | 1242 | 17 | 8 oz | 17
2000-09-20 | PGE-TW2 | na | na | na | na | na | na | na | na | na
2000-09-20 | PGE TOP3 | na | na | na | na | na | na | na | na | na
2000-09-20 | PGE TOP4 | na | na | na | na | na | na | na | na | na
2000-09-20 | PGE 0.55B 09-20-00-L | Sherwood | 2000-09-22 | 2000-09-25 |  | 8 | 1242 | 7 | 4 oz | 7.5
2000-09-20 | PGE 10.84A | na | na | na | na | na | na | na | na | na
2000-09-20 | PGE 10.47B | na | na | na | na | na | na | na | na | na
2000-09-20 | PGE 15.33A 09-20-00-L | Sherwood | 2000-09-22 | 2000-09-25 |  | 14 | 1242 | 14 | 4 oz | 14
2000-09-20 | PGE 27.15A | na | na | na | na | na | na | na | na | na
2000-09-20 | PGE 27.15B | na | na | na | na | na | na | na | na | na
2000-09-20 | PGE 63.26A | na | na | na | na | na | na | na | na | na
2000-09-20 | PGE 63.26B 9-20-00-L | Sherwood | 2000-09-22 | 2000-09-25 |  | 15 | 1242 | 14 | 4 oz | 14.5
2000-09-20 | PGE 84.10A | na | na | na | na | na | na | na | na | na
2000-09-06 | PGE-TW2 | na | na | na | na | na | na | na | na | na
2000-09-06 | PGE TOP3 | na | na | na | na | na | na | na | na | na
2000-09-06 | PGE TOP4 | na | na | na | na | na | na | na | na | na
2000-09-06 | PGE 0.55B | na | na | na | na | na | na | na | na | na
2000-09-06 | PGE 10.84A | na | na | na | na | na | na | na | na | na
2000-09-06 | PGE 10.47B | na | na | na | na | na | na | na | na | na
2000-09-06 | PGE 15.33A | na | na | na | na | na | na | na | na | na
2000-09-06 | PGE 27.15A | na | na | na | na | na | na | na | na | na
2000-09-06 | PGE 27.15B | na | na | na | na | na | na | na | na | na
2000-09-06 | PGE 63.26A 9-6-00-L | Sherwood | 2000-09-07 | 2000-09-10 |  | 14 | 1016 | 14 | 5 oz | 14
2000-09-06 | PGE 63.26B 9-6-00-L | Sherwood | 2000-09-07 | 2000-09-10 |  | 16 | 1016 | 16 | 4 oz | 16
2000-09-06 | PGE 84.10A | Sherwood | 2000-09-07 | 2000-09-10 |  | 17 | 1016 | 17 | 4.5 oz | 17
2000-08-23 | PGE-TW2 | na | na | na | na | na | na | na | na | na
2000-08-23 | PGE TOP3 | na | na | na | na | na | na | na | na | na
2000-08-23 | PGE TOP4 | na | na | na | na | na | na | na | na | na
2000-08-23 | PGE 0.55B | na | na | na | na | na | na | na | na | na
2000-08-23 | PGE 10.84A | na | na | na | na | na | na | na | na | na
2000-08-23 | PGE 10.47B | na | na | na | na | na | na | na | na | na
2000-08-23 | PGE 15.33A 8-23-00-L | Sherwood | 2000-08-24 | 2000-08-28 |  | 19 | 1242 | 18 | 5 oz | 18.5
2000-08-23 | PGE 27.15A | na | na | na | na | na | na | na | na | na
2000-08-23 | PGE 27.15B | na | na | na | na | na | na | na | na | na
2000-08-23 | PGE 63.26A 8-23-00-L | Sherwood | 2000-08-24 | 2000-08-28 |  | 16 | 1242 | 15 | 2 oz | 15.5
2000-08-23 | PGE 63.26B 8-23-00-L | Sherwood | 2000-08-24 | 2000-08-28 |  | 15 | 1242 | 15 | 1 oz | 15
2000-08-23 | PGE 84.10A 8-23-00-L | Sherwood | 2000-08-24 | 2000-08-28 |  | 16 | 1242 | 16 | 12 oz | 16
2000-08-09 | PGE-TW2 | na | na | na | na | na | na | na | na | na
2000-08-09 | PGE TOP3 | na | na | na | na | na | na | na | na | na
2000-08-09 | PGE TOP4 | na | na | na | na | na | na | na | na | na
2000-08-09 | PGE 0.55B 8-9-00-L | Sherwood | 2000-08-10 | 2000-08-14 |  | 13 | 1242 | na | 1 oz | na
2000-08-09 | PGE 10.84A 8-9-00-L | Sherwood | 2000-08-10 | 2000-08-14 |  | 18 | 1242 | na | 1 oz | na
2000-08-09 | PGE 10.47B | na | na | na | na | na | na | na | na | na
2000-08-09 | PGE 15.33A 8-9-00-L | Sherwood | 2000-08-10 | 2000-08-14 |  | 18 | 1242 | 19 | 4 oz | 18.5
2000-08-09 | PGE 27.15A | na | na | na | na | na | na | na | na | na
2000-08-09 | PGE 27.15B | na | na | na | na | na | na | na | na | na
2000-08-09 | PGE 63.26A | na | na | na | na | na | na | na | na | na
2000-08-09 | PGE 63.26B 8-9-00-L | Sherwood | 2000-08-10 | 2000-08-14 |  | 17 | 1242 | 16 | 3 oz | 16.5
2000-08-09 | PGE 84.10A 8-9-00-L | Sherwood | 2000-08-10 | 2000-08-14 |  | 16 | 1242 | 16 | 8 oz | 16
2000-07-26 | PGE-TW2 | na | na | na | na | na | na | na | na | na
2000-07-26 | PGE TOP3 | na | na | na | na | na | na | na | na | na
2000-07-26 | PGE TOP4 | na | na | na | na | na | na | na | na | na
2000-07-26 | PGE 0.55B | na | na | na | na | na | na | na | na | na
2000-07-26 | PGE 10.84A 7-26-00-L | Sherwood | 2000-07-27 | 2000-07-31 |  | 20 | 1242 | 19 | 1/2 oz | 19.5
2000-07-26 | PGE 10.47B | na | na | na | na | na | na | na | na | na
2000-07-26 | PGE 15.33A 7-26-00-L | Sherwood | 2000-07-27 | 2000-07-31 |  | 15 | 1242 | 14 | 4 oz | 14.5
2000-07-26 | PGE 27.15A | na | na | na | na | na | na | na | na | na
2000-07-26 | PGE 27.15B | na | na | na | na | na | na | na | na | na
2000-07-26 | PGE 63.26A 7-26-00-L | Sherwood | 2000-07-27 | 2000-07-31 |  | 18 | 1242 | 17 | 2 oz | 17.5
2000-07-26 | PGE 63.26B 7-26-00-L | Sherwood | 2000-07-27 | 2000-07-31 |  | 18 | 1242 | 17 | 2 oz | 17.5
2000-07-26 | PGE 84.10A | na | na | na | na | na | na | na | na | na
2000-07-12 | PGE-TW2 | na | na | na | na | na | na | na | na | na
2000-07-12 | PGE TOP3 | na | na | na | na | na | na | na | na | na
2000-07-12 | PGE TOP4 | na | na | na | na | na | na | na | na | na
2000-07-12 | PGE 0.55B | na | na | na | na | na | na | na | na | na
2000-07-12 | PGE 10.84A | na | na | na | na | na | na | na | na | na
2000-07-12 | PGE 10.47B | na | na | na | na | na | na | na | na | na
2000-07-12 | PGE 15.33A 7-12-00-L | Sherwood | 2000-07-13 | 2000-07-17 |  | 14 | 1242 |  | 10 oz
2000-07-12 | PGE 27.15A | na | na | na | na | na | na | na | na | na
2000-07-12 | PGE 27.15B | na | na | na | na | na | na | na | na | na
2000-07-12 | PGE 63.26A | na | na | na | na | na | na | na | na | na
2000-07-12 | PGE 63.26B 7-12-00-L | Sherwood | 2000-07-13 | 2000-07-17 |  | 19 | 1242 |  | 3 oz
2000-07-12 | PGE 84.10A | na | na | na | na | na | na | na | na | na
2000-07-05 | PGE-TW2 | na | na | na | na | na | na | na | na | na
2000-07-05 | PGE TOP3 | na | na | na | na | na | na | na | na | na
2000-07-05 | PGE TOP4 7-5-00-L | Sherwood | 2000-07-06 | 2000-07-11 |  | 220 | 1242 | 220 | 1 oz | 220
2000-07-05 | PGE 0.55B 7-5-00-L | Sherwood | 2000-07-06 | 2000-07-11 |  | 17 | 1016 | 14 | 2 oz | 15.5
2000-07-05 | PGE 10.84A 7-5-00-L | Sherwood | 2000-07-06 | 2000-07-11 |  | 21 | 1016 | 23 | 1/4 oz | 22
2000-07-05 | PGE 10.47B | na | na | na | na | na | na | na | na | na
2000-07-05 | PGE 15.33A 7-5-00-L | Sherwood | 2000-07-06 | 2000-07-11 |  | 16 | 1016 | 15 | 10 oz | 15.5
2000-07-05 | PGE 27.15A | na | na | na | na | na | na | na | na | na
2000-07-05 | PGE 27.15B | na | na | na | na | na | na | na | na | na
2000-07-05 | PGE 63.26A 7-5-00-L | Sherwood | 2000-07-06 | 2000-07-11 |  | 20 | 1016 | 21 | 6 oz | 20.5
2000-07-05 | PGE 63.26B 7-5-00-L | Sherwood | 2000-07-06 | 2000-07-11 |  | 19 | 1016 | 20 | 5 oz | 19.5
2000-07-05 | PGE 84.10A 7-5-00-L | Sherwood | 2000-07-06 | 2000-07-11 |  | 21 | 1016 | 22 | 2 oz | 21.5
2000-06-27 | PGE-TW2 | na | na | na | na | na | na | na | na | na
2000-06-27 | PGE TOP3 6-21-00-L | na | na | na | na | na | na | na | na | na
2000-06-27 | PGE TOP4 | na | na | na | na | na | na | na | na | na
2000-06-27 | PGE 0.55B 06-27-00-L | Sherwood | 2000-06-28 | 2000-06-30 |  | 19 | 1016 | 18 | 1/2 oz | 18.5
2000-06-27 | PGE 10.84A | na | na | na | na | na | na | na | na | na
2000-06-27 | PGE 10.47B | na | na | na | na | na | na | na | na | na
2000-06-27 | PGE 15.33A 06-27-00-L | Sherwood | 2000-06-28 | 2000-06-30 |  | 23 | 1016 | 22 | 3 oz | 22.5
2000-06-27 | PGE 27.15A | na | na | na | na | na | na | na | na | na
2000-06-27 | PGE 27.15B | na | na | na | na | na | na | na | na | na
2000-06-27 | PGE 63.26A 6-27-00-L | Sherwood | 2000-06-28 | 2000-06-30 |  | 24 | 1016 | 23 | 4 oz | 23.5
2000-06-27 | PGE 63.26B 06-27-00-L | Sherwood | 2000-06-28 | 2000-06-30 |  | 26 | 1016 | 20 | 3 oz | 23
2000-06-27 | PGE 84.10A | na | na | na | na | na | na | na | na | na
2000-06-21 | PGE-TW2 | na | na | na | na | na | na | na | na | na
2000-06-21 | PGE TOP3 6-21-00-L | Sherwood | 2000-06-22 | 2000-06-26 |  | 16 | 1016 | 16 | 4 oz | 16
2000-06-21 | PGE TOP4 6-21-00-W | Sherwood | 2000-06-28 | 2000-06-30 | na | 35 mg Wipe Sample Semi Quantitative | 1016 | 18 mg Wipe Sample | na | 26.5 mg | PGE - Semi Quantitative Wipe Sample
2000-06-21 | PGE 0.55B 06-21-00-L | Sherwood | 2000-06-22 | 2000-06-26 |  | 18 | 1016 | 18 | 3/4 oz | 18
2000-06-21 | PGE 10.84A 6-21-00-L | Sherwood | 2000-06-22 | 2000-06-26 |  | 24 | 1016 | 23 | 3/4 oz | 23.5
2000-06-21 | PGE 10.47B | na | na | na | na | na | na | na | na | na
2000-06-21 | PGE 15.33A 06-21-00-L | Sherwood | 2000-06-22 | 2000-06-26 |  | 24 | 1016 | 23 | 6 oz | 23.5
2000-06-21 | PGE 27.15A | na | na | na | na | na | na | na | na | na
2000-06-21 | PGE 27.15B | na | na | na | na | na | na | na | na | na
2000-06-21 | PGE 63.26A 6-21-00-L | Sherwood | 2000-06-22 | 2000-06-26 |  | 27 | 1016 | 26 | 32 oz | 26.5
2000-06-21 | PGE 63.26B 06-21-00-L | Sherwood | 2000-06-22 | 2000-06-26 |  | 17 | 1016 | 17 | 16 oz | 17
2000-06-21 | PGE 84.10A | na | na | na | na | na | na | na | na | na
2000-06-14 | PGE-TW2 | na | na | na | na | na | na | na | na | na
2000-06-14 | PGE TOP3 | na | na | na | na | na | na | na | na | na
2000-06-14 | PGE TOP4 06-14-00-L | Sherwood | 2000-06-15 | 2000-06-20 |  | 567 | 1016 | na | 1/2 oz | na
2000-06-14 | PGE 0.55B 06-14-00-L | Sherwood | 2000-06-15 | 2000-06-20 |  | 15 | 1016 | 16 | 1 oz | 15.5
2000-06-14 | PGE 10.84A | na | na | na | na | na | na | na | na | na
2000-06-14 | PGE 10.47B | na | na | na | na | na | na | na | na | na
2000-06-14 | PGE 15.33A 06-14-00-L | Sherwood | 2000-06-15 | 2000-06-20 |  | 25 | 1016 | 28 | 4 oz | 26.5
2000-06-14 | PGE 27.15A | na | na | na | na | na | na | na | na | na
2000-06-14 | PGE 27.15B | na | na | na | na | na | na | na | na | na
2000-06-14 | PGE 63.26A | na | na | na | na | na | na | na | na | na
2000-06-14 | PGE 63.26B 06-14-00-L | Sherwood | 2000-06-15 | 2000-06-20 |  | 16 | 1016 | 16 | 1 oz | 16
2000-06-14 | PGE 84.10A | na | na | na | na | na | na | na | na | na
2000-05-31 | PGE-TW2 | na | na | na | na | na | na | na | na | na
2000-05-31 | PGE TOP3 | na | na | na | na | na | na | na | na | na
2000-05-30 | PGE TOP4 05-30-00-L | Sherwood | 2000-06-01 | 2000-06-05 |  | 505 | 1016 | na | 4 oz | na | TW Sample broken during shipping
2000-05-31 | PGE 0.55B 05-31-00-L | Sherwood | 2000-06-01 | 2000-06-05 |  | 17 | 1016 | na | 20 oz | na | TW Sample broken during shipping
2000-05-31 | PGE 10.84A 05-31-00-L | Sherwood | 2000-06-01 | 2000-06-05 |  | 23 | 1016 | 23 | 4 oz | 23
2000-05-31 | PGE 10.47B | na | na | na | na | na | na | na | na | na
2000-05-31 | PGE 15.33A | na | na | na | na | na | na | na | na | na
2000-05-31 | PGE 27.15A | na | na | na | na | na | na | na | na | na
2000-05-31 | PGE 27.15B | na | na | na | na | na | na | na | na | na
2000-05-31 | PGE 63.26A | na | na | na | na | na | na | na | na | na
2000-05-31 | PGE 63.26B 05-31-00-L | Sherwood | 2000-06-01 | 2000-06-05 |  | 11 | 1016 | 12 | 3 oz | 11.5
2000-05-31 | PGE 84.10A | na | na | na | na | na | na | na | na | na
2000-05-17 | PGE-TW2 | na | na | na | na | na | na | na | na | na
2000-05-17 | PGE TOP3 | na | na | na | na | na | na | na | na | na
2000-05-17 | PGE TOP4 | na | na | na | na | na | na | na | na | na
2000-05-17 | PGE 0.55B 05-17-00-L | Sherwood | 2000-05-18 | 2000-05-22 |  | 11 | 1016 | 10 | 2 gal | 10.5
2000-05-17 | PGE 10.84A 05-17-00-L | Sherwood | 2000-05-18 | 2000-05-22 |  | 16 | 1016 | 17 | 10 oz | 16.5
2000-05-17 | PGE 10.47B | na | na | na | na | na | na | na | na | na
2000-05-17 | PGE 15.33A 05-17-00-L | Sherwood | 2000-05-18 | 2000-05-22 |  | 17 | 1016 | 17 | 8 oz | 17
2000-05-17 | PGE 27.15A | na | na | na | na | na | na | na | na | na
2000-05-17 | PGE 27.15B | na | na | na | na | na | na | na | na | na
2000-05-17 | PGE 63.26A | na | na | na | na | na | na | na | na | na
2000-05-17 | PGE 63.26B 05-17-00-L | Sherwood | 2000-05-18 | 2000-05-22 |  | 7 | 1016 | 7 | 4 oz | 7
2000-05-17 | PGE 84.10A | na | na | na | na | na | na | na | na | na
2000-05-03 | PGE-TW2 05-03-00-L | na | na | na | na | na | na | na | na | na
2000-05-03 | PGE TOP3 05-03-00-L | na | na | na | na | na | na | na | na | na
2000-05-03 | PGE TOP4 05-03-00-L | na | na | na | na | na | na | na | na | na
2000-05-03 | PGE 0.55B 05-03-00-L | Sherwood | 2000-05-04 | 2000-05-08 |  | 17 | 1016 | 16 | 4 oz | 16.5
2000-05-03 | PGE 10.84A 05-03-00-L | Sherwood | 2000-05-04 | 2000-05-08 |  | 21 | 1016 | 20 | 3 oz | 20.5
2000-05-03 | PGE 10.47B 05-03-00-L | na | na | na | na | na | na | na | na | na
2000-05-03 | PGE 15.33A 05-03-00-L | Sherwood | 2000-05-04 | 2000-05-08 |  | 24 | 1016 | 25 | 3 oz | 24.5
2000-05-03 | PGE 27.15A 05-03-00-L | na | na | na | na | na | na | na | na | na
2000-05-03 | PGE 27.15B 05-03-00-L | na | na | na | na | na | na | na | na | na
2000-05-03 | PGE 63.26A 05-03-00-L | na | na | na | na | na | na | na | na | na
2000-05-03 | PGE 63.26B 05-03-00-L | Sherwood | 2000-05-04 | 2000-05-08 |  | 9 | 1016 | 10 | 2 oz | 9.5
2000-05-03 | PGE 84.10A 05-03-00-L | na | na | na | na | na | na | na | na | na
2000-04-19 | PGE-TW2 04-19-00-L | na | na | na | na | na | na | na | na | na
2000-04-19 | PGE TOP3 04-19-00-L | na | na | na | na | na | na | na | na | na
2000-04-19 | PGE TOP4 04-19-00-L | na | na | na | na | na | na | na | na | na
2000-04-19 | PGE 0.55B 04-19-00-L | Sherwood | 2000-04-20 | 2000-04-24 |  | 17 | 1242 | 16 | 8 oz | 16.5
2000-04-19 | PGE 10.84A 04-19-00-L | na | na | na | na | na | na | na | na | na
2000-04-19 | PGE 10.47B 04-19-00-L | na | na | na | na | na | na | na | na | na
2000-04-19 | PGE 15.33A 04-19-00-L | na | na | na | na | na | na | na | na | na
2000-04-19 | PGE 27.15A 04-19-00-L | na | na | na | na | na | na | na | na | na
2000-04-19 | PGE 27.15B 04-19-00-L | na | na | na | na | na | na | na | na | na
2000-04-19 | PGE 63.26A 04-19-00-L | na | na | na | na | na | na | na | na | na
2000-04-19 | PGE 63.26B 04-19-00-L | Sherwood | 2000-04-20 | 2000-04-24 |  | 10 | 1016 | 9 | 2 oz | 9.5
2000-04-19 | PGE 84.10A 04-19-00-L | na | na | na | na | na | na | na | na | na
2000-04-05 | PGE-TW2 04-5-00-L | na | na | na | na | na | na | na | na | na
2000-04-05 | PGE TOP3 04-5-00-L | na | na | na | na | na | na | na | na | na
2000-04-05 | PGE TOP4 04-5-00-L | na | na | na | na | na | na | na | na | na
2000-04-05 | PGE 0.55B 04-5-00-L | Sherwood | 2000-04-06 | 2000-04-10 |  | 20 | 1016 | 21 | 2 oz | 20.5
2000-04-05 | PGE 10.84A 04-5-00-L | na | na | na | na | na | na | na | na | na
2000-04-05 | PGE 10.47B 04-5-00-L | na | na | na | na | na | na | na | na | na
2000-04-05 | PGE 15.33A 04-5-00-L | na | na | na | na | na | na | na | na | na
2000-04-05 | PGE 27.15A 04-5-00-L | na | na | na | na | na | na | na | na | na
2000-04-05 | PGE 27.15B 04-5-00-L | na | na | na | na | na | na | na | na | na
2000-04-05 | PGE 63.26A 04-5-00-L | na | na | na | na | na | na | na | na | na
2000-04-05 | PGE 63.26B 04-5-00-L | Sherwood | 2000-04-06 | 2000-04-10 |  | 8 | 1016 | 8 | 4 oz | 8
2000-04-05 | PGE 84.10A 04-5-00-L | na | na | na | na | na | na | na | na | na
2000-03-22 | PGE-TW2 03-22-00-L | na | na | na | na | na | na | na | na | na
2000-03-22 | PGE TOP3 03-22-00-L | na | na | na | na | na | na | na | na | na
2000-03-22 | PGE TOP4 03-22-00-L | na | na | na | na | na | na | na | na | na
2000-03-22 | PGE 0.55B 03-22-00-L | Sherwood | 2000-03-23 | 2000-03-28 |  | 10 | 1248 | 12 | 4 oz | 11
2000-03-22 | PGE 10.84A 03-22-00-L | Sherwood | 2000-03-23 | 2000-03-28 |  | 13 | 1016 | 16 | 2 oa | 14.5
2000-03-22 | PGE 10.47B 03-22-00-L | na | na | na | na | na | na | na | na | na
2000-03-22 | PGE 15.33A 03-22-00-L | Sherwood | 2000-03-23 | 2000-03-28 |  | 35 | 1016 | 55 | 2 oz | 45
2000-03-22 | PGE 27.15A 03-22-00-L | na | na | na | na | na | na | na | na | na
2000-03-22 | PGE 27.15B 03-22-00-L | na | na | na | na | na | na | na | na | na
2000-03-22 | PGE 63.26A 03-22-00-L | na | na | na | na | na | na | na | na | na
2000-03-22 | PGE 63.26B 03-22-00-L | Sherwood | 2000-03-23 | 2000-03-28 |  | 27 | 1016 | 10 | 3 oz | 18.5
2000-03-22 | PGE 84.10A 03-22-00-L | Sherwood | 2000-03-23 | 2000-03-28 |  | 21 | 1016 | 27 | 2 oz | 24
2000-03-01 | PGE-TW2 03-01-00-L | na | na | na | na | na | na | na | na | na
2000-03-01 | PGE TOP3 03-01-00-L | na | na | na | na | na | na | na | na | na
2000-03-01 | PGE TOP4 03-01-00-L | na | na | na | na | na | na | na | na | na
2000-03-01 | PGE 0.55B 03-01-00-L | Sherwood | 2000-03-02 | 2000-03-06 |  | 23 | 1016 | 24 | 1 gal | 23.5
2000-03-01 | PGE 10.84A 03-01-00-L | Sherwood | 2000-03-02 | 2000-03-06 |  | 21 | 1016 | 20 | 1 oz | 20.5
2000-03-01 | PGE 10.47B 03-01-00-L | na | na | na | na | na | na | na | na | na
2000-03-01 | PGE 15.33A 03-01-00-L | Sherwood | 2000-03-02 | 2000-03-06 |  | 26 | 1016 | 24 | 4 oz | 25
2000-02-09 | PGE-TW2 02-09-00-L | na | na | na | na | na | na | na | na | na
2000-02-09 | PGE TOP3 02-09-00-L | na | na | na | na | na | na | na | na | na
2000-02-09 | PGE TOP4 02-09-00-L | na | na | na | na | na | na | na | na | na
2000-02-09 | PGE 0.55B 02-09-00-L | Sherwood | 2000-02-11 | 2000-02-18 |  | 29 | 1016 | 24 |  | 26.5
2000-02-09 | PGE 10.84A 02-09-00-L | na | na | na | na | na | na | na | na | na
2000-02-09 | PGE 10.47B 02-09-00-L | na | na | na | na | na | na | na | na | na
2000-02-09 | PGE 15.33A 02-09-00-L | Sherwood | 2000-02-11 | 2000-02-18 |  | 26 | 1016 | 16 |  | 21
2000-02-03 | PGE MP 63B 2-3-00-L | Sherwood | 2000-02-04 | 2000-02-08 |  | 3 | 1016 | na | na | na
2000-01-19 | PGE MP 103B Mist 1-19-00-L | Sherwood | 2000-01-20 | 2000-01-26 |  | ND | na | na | na | na
2000-01-19 | PGE MP 103B MLV 1-19-00-W | Sherwood | 2000-01-20 | 2000-01-26 |  | ND | na | na | na | na | Wipe Sample
2000-01-19 | PGE MP 103A PG Mist 1-19-00-L | Sherwood | 2000-01-20 | 2000-01-26 |  | <1 | na | na | na | na
2000-01-19 | PGE MP 103A V-3 1-19-00-W | Sherwood | 2000-01-20 | 2000-01-26 |  | <1 ug/100 sqcm | na | na | na | na | Wipe Sample
2000-01-19 | PGE Mp 40.49B PG Mist 1-19-00-L | Sherwood | 2000-01-20 | 2000-01-26 |  | ND | na | na | na | na
2000-01-19 | PGE MP 40.49B V-6 1-19-00-W | Sherwood | 2000-01-20 | 2000-01-26 |  | 1.2 ug/100 sqcm | 1016 | na | na | na | Wipe Sample
2000-01-19 | PGE MP 40.87A PG Mist 1-19-00-L | Sherwood | 2000-01-20 | 2000-01-26 |  | ND | na | na | na | na
2000-01-19 | PGE MP 40.87A V-3 1-19-00-W | Sherwood | 2000-01-20 | 2000-01-26 |  | <1 ug/100 sqcm | na | na | na | na | Wipe Sampe
2000-01-19 | PGE-TW2 01-19-00-L | na | na | na |  | na | na | na | na | na
2000-01-19 | PGE TOP3 01-19-00-L | na | na | na |  | na | na | na | na | na
2000-01-19 | PGE TOP4 01-19-00-L | na | na | na |  | na | na | na | na | na
2000-01-19 | PGE 0.55B 01-19-00-L | Sherwood | 2000-01-19 | 2000-01-21 |  | 17 | 1016 | 32 | 7 oz | 24.5
2000-01-19 | PGE 10.84A 01-19-00-L | Sherwood | 2000-01-19 | 2000-01-21 |  | 8 | 1016 | 18 | 2 oz | 13
2000-01-19 | PGE 10.47B 01-19-00-L | Sherwood | 2000-01-19 | 2000-01-21 |  | 1 | 1016 | 2 | 1 oz | 1.5
2000-01-19 | PGE 15.33A 01-19-00-L | Sherwood | 2000-01-19 | 2000-01-21 |  | 24 | 1016 | 28 | 20 oz | 26
2000-01-07 | PGE MP71.98A Reg 1-7-00-W | Sherwood | 2000-01-07 | 2000-01-11 |  | <2 ug/100 sqcm | See Comments | na | na | na | Wipe Sample detection limit raised due to matrix effects. Aroclor 1260 present at <1 ug/100 sqcm
2000-01-07 | PGE MP65A Tap 1-7-00-W | Sherwood | 2000-01-07 | 2000-01-11 |  | ND | na | na | na | na | Wipe Sample
2000-01-07 | PGE MP63.36A Tap 1-7-00-W | Sherwood | 2000-01-07 | 2000-01-11 |  | 3 ug/100 sqsm | 1260 | na | na | na | Wipe Sample
2000-01-07 | PGE MP62.98A Tap 1-7-00-W | Sherwood | 2000-01-07 | 2000-01-11 |  | ND | na | na | na | na | Wipe Sample
2000-01-07 | PGE MP40.49B PGMist 1-7-00-L | Sherwood | 2000-01-07 | 2000-01-11 |  | <1 | na | na | na | na
2000-01-07 | PGE MP40.49B V-6 1-7-00-W | Sherwood | 2000-01-07 | 2000-01-11 |  | ND<2 ug/100 sqcm | See Comments | na | na | na | Wipe Sample detection limit raised due to matrix interference
2000-01-07 | PGE MP40.87A PGMist 1-7-00-L | Sherwood | 2000-01-07 | 2000-01-11 |  | ND | na | na | na | na
2000-01-07 | PGE MP40.87A MLV 1-7-00-W | Sherwood | 2000-01-07 | 2000-01-11 |  | ND<3 ug/100 sqcm | See Comments | na | na | na | Wipe Sample detection limit raised due to matrix interference
2000-01-05 | PGE 103A PG Mist 1-5-00-L | Sherwood | 2000-01-07 | 2000-01-11 |  | ND | na | na |  | na
2000-01-06 | PGE 103B PG Mist 1-6-00-L | Sherwood | 2000-01-07 | 2000-01-11 |  | ND | na | na |  | na
2000-01-06 | PGE MP62 All-Amer-W | Sherwood | 2000-01-07 | 2000-01-11 |  | ND<7 ug/100sqcm | See Comments | na |  | na | Wipe Sample detection limit raised due to matrix interference. Peak pattern not consistent with known Aroclors.
2000-01-06 | PGE MP62 All-Amer-L | Sherwood | 2000-01-07 | 2000-01-11 |  | 1 | 1016 | na |  | na
2000-01-06 | Amboy Secondary Reg Station | Sherwood | 2000-01-07 | 2000-01-11 |  | ND | na | na |  | na | Wipe Samples
2000-01-06 | PGE MP103A Heater | Sherwood | 2000-01-07 | 2000-01-11 |  | ND<20 ug/100sqcm | See Comments | na |  | na | Wipe Samples detection limit raised due to matrix interference. Peak pattern not consistent with known Aroclors
2000-01-06 | PGE MP103A Heater Lid | Sherwood | 2000-01-07 | 2000-01-11 |  | ND<10 ug/100 sqcm | See Comments | na |  | na | Wipe Samples detection limit raised due to matrix interference. Peak pattern not consistent with known Aroclors
2000-01-06 | PGE MP74A Amboy Primary | Sherwood | 2000-01-07 | 2000-01-11 |  | ND<2 ug/100 sqcm | See Comments | na |  | na | Wipe Samples detection limit raised due to matrix interference. Peak pattern not consistent with known Aroclors
2000-01-05 | PGE-TW2 01-05-00-L | na | na | na | na | na | na | na | na | na
2000-01-05 | PGE TOP3 01-05-00-L | na | na | na | na | na | na | na | na | na
2000-01-05 | PGE TOP4 01-05-00-L | na | na | na | na | na | na | na | na | na
2000-01-05 | PGE 0.55B 12-29-99-L | Sherwood | 2000-01-07 | 2000-01-11 |  | 17 | 1016 | 21 |  | 19
2000-01-05 | PGE 10.84A 12-29-99-L | Sherwood | 2000-01-07 | 2000-01-11 |  | 9 | 1016 | 7 |  | 8
2000-01-05 | PGE 10.47B 01-05-00-L | na | na | na |  | na | na | na | na | na
2000-01-05 | PGE 15.33A 12-29-99-L | Sherwood | 2000-01-07 | 2000-01-11 |  | 33 | 1016 | 32 |  | 32.5
1999-12-31 | PGE MP 103A Valve | Sherwood | 2000-01-03 | 2000-01-05 |  | ND | na | na | na | na | Wipe Samples
1999-12-31 | PGE MP 103A Insertion Meter | Sherwood | 2000-01-03 | 2000-01-05 |  | ND | na | na | na | na | Wipe Samples
1999-12-31 | PGE MP103B Valve | Sherwood | 2000-01-03 | 2000-01-05 |  | ND<2 ug/100 sqcm | na | na | na | na | Wipe Samples detection limit raised due to matrix interference
1999-12-31 | PGE MP 103B Insertion Meter | Sherwood | 2000-01-03 | 2000-01-05 |  | ND<2 ug/100 sqcm | na | na | na | na | Wipe Samples detection limit raised due to matrix interference
1999-12-30 | PGE MP 40B Insertion Meter | Sherwood | 1999-12-31 | 2000-01-04 |  | ND <5 ug/100sqcm | na | na | na | na | Wipe Samples detection limit raised due to matrix interference
1999-12-30 | PGE MP 40B Valve | Sherwood | 1999-12-31 | 2000-01-04 |  | ND <5 ug/100sqcm | na | na | na | na | Wipe Samples detection limit raised due to matrix interference
1999-12-30 | PGE MP 40A Insertion Meter | Sherwood | 1999-12-31 | 2000-01-04 |  | ND <5 ug/100sqcm | na | na | na | na | Wipe Samples detection limit raised due to matrix interference
1999-12-30 | PGE MP 40A Valve | Sherwood | 1999-12-31 | 2000-01-04 |  | ND <5 ug/100sqcm | na | na | na | na | Wipe Samples detection limit raised due to matrix interference
1999-12-29 | Southwest Gas Meter Park Moabi Mtr# 116902 | Sherwood | 1999-12-31 | 2000-01-04 |  | ND | na | nD | na | ND | Wipe Samples
1999-12-29 | Southwest Gas Meter Needles Mtr # R384072 | Sherwood | 1999-12-31 | 2000-01-04 |  | ND | na | ND | na | ND | Wipe Samples
1999-12-29 | PGE-TW2 12-29-99-L | na | na | na | na | na | na | na | na | na
1999-12-29 | PGE TOP3 12-29-99-L | na | na | na | na | na | na | na | na | na
1999-12-29 | PGE TOP4 12-29-99-L | na | na | na | na | na | na | na | na | na
1999-12-29 | PGE 0.55B 12-29-99-L | Sherwood | 1999-12-31 | 2000-01-04 |  | 29 | 1016 | 31 | 8 oz | 30
1999-12-29 | PGE 10.84A 12-29-99-L | Sherwood | 1999-12-31 | 2000-01-04 |  | 16 | 1016 | 14 | 4 oz | 15
1999-12-29 | PGE 10.47B 12-29-99-L | Sherwood | 1999-12-31 | 2000-01-04 |  | 2 | 1016 | 2 | 1 oz | 2
1999-12-29 | PGE 15.33A 12-29-99-L | Sherwood | 1999-12-31 | 2000-01-04 |  | 30 | 1016 | 27 | 10 oz | 28.5
1999-12-14 | PGE-TW2 12-14-99-L | na | na | na |  | na | na | na | na | na | No liqiud
1999-12-14 | PGE TOP3 12-14-99-L | na | na | na |  | na | na | na | na | na | No liqiud
1999-12-14 | PGE TOP4 12-14-99-L | na | na | na |  | na | na | na | na | na | No liqiud
1999-12-14 | PGE 0.55B 12-14-99-L | Sherwood | 1999-12-14 | 1999-12-16 |  | 21 | 1016 | 23 | 3 oz | 22
1999-12-14 | PGE 10.84A 12-14-99-L | Sherwood | 1999-12-14 | 1999-12-16 |  | 9 | 1016 | 15 | 2 oz | 12
1999-12-14 | PGE 10.47B 12-14-99-L | na | na | na |  | na | na | na | na | na | No liqiud
1999-12-14 | PGE 15.33A 12-14-99-L | Sherwood | 1999-12-14 | 1999-12-16 |  | 39 | 1016 | 39 |  | 39
1999-12-08 | PGE-TW2 12-08-99-L | na | na | na |  | na | na | na | na | na | No liqiud
1999-12-08 | PGE TOP3 12-08-99-L | na | na | na |  | na | na | na | na | na | No liqiud
1999-12-08 | PGE TOP4 12-08-99-L | na | na | na |  | na | na | na | na | na | No liqiud
1999-12-08 | PGE 0.55B 12-08-99-L | Sherwood | 1999-12-09 | 1999-12-13 |  | 30 | 1016 | 33 |  | 31.5
1999-12-08 | PGE 10.84A 12-08-99-L | Sherwood | 1999-12-09 | 1999-12-13 |  | 13 | 1016 | 13 |  | 13
1999-12-08 | PGE 10.47B 12-08-99-L | na | na | na |  | na | na | na | na | na | No liqiud
1999-12-08 | PGE 15.33A 12-08-99-L | Sherwood | 1999-12-09 | 1999-12-13 |  | 35 | 1016 | 36 |  | 35.5
1999-12-03 | PGE MP 103A Valve | Sherwood | 1999-12-06 | 1999-12-08 |  | <1 ug/100sqcm | na | na | na | na | Wipe Samples
1999-12-03 | PGE MP 103A Insertion Meter | Sherwood | 1999-12-06 | 1999-12-08 |  | <1 ug/100sqcm | na | na | na | na | Wipe Samples
1999-12-03 | PGE MP 103 A & B Blank | Sherwood | 1999-12-06 | 1999-12-08 |  | ND | na | na | na | na | Wipe Samples
1999-12-03 | PGE MP 103B Insertion Meter | Sherwood | 1999-12-06 | 1999-12-08 |  | <1 ug/100sqcm | na | na | na | na | Wipe Samples
1999-12-03 | PGE MP 103B Valve | Sherwood | 1999-12-06 | 1999-12-08 |  | 1.3 ug/100sqcm | 1016 | na | na | na | Wipe Samples
1999-12-03 | PGE MP 40A Valve | Sherwood | 1999-12-06 | 1999-12-08 |  | 1.8 ug/100sqcm | 1016 | na | na | na | Wipe Samples
1999-12-03 | PGE MP40 A & B Blank | Sherwood | 1999-12-06 | 1999-12-08 |  | ND | na | na | na | na | Wipe Samples
1999-12-03 | PGE MP 40A Insertion Meter | Sherwood | 1999-12-06 | 1999-12-08 |  | 1.0 ug/100sqcm | 1016 | na | na | na | Wipe Samples
1999-12-03 | PGE MP 40B Valve | Sherwood | 1999-12-06 | 1999-12-08 |  | 1.6 ug/100sqcm | 1016 | na | na | na | Wipe Samples
1999-12-03 | PGE MP 40B Insertion Meter | Sherwood | 1999-12-06 | 1999-12-08 |  | 1.7 ug/100sqcm | 1016 | na | na | na | Wipe Samples
1999-12-01 | PGE MP 169.95B 12-1-99-L | Sherwood | 1999-12-06 | 1999-12-08 |  | <1 | na | na | na | na | Hinkley District
1999-12-01 | PGE TOP3 12-01-99-L | na | na | na |  | na | na | na | na | na | No liqiud
1999-12-01 | PGE TOP4 12-01-99-L | na | na | na |  | na | na | na | na | na | No liqiud
1999-12-01 | PGE 0.55B 12-01-99-L | Sherwood | 1999-12-01 | 1999-12-06 |  | 47 | 1016 | 38 | 16 oz | 42.5
1999-12-01 | PGE 10.84A 12-01-99-L | Sherwood | 1999-12-01 | 1999-12-06 |  | 11 | 1016 | 11 | 2 oz | 11
1999-12-01 | PGE 10.47B 12-01-99-L | Sherwood | 1999-12-01 | 1999-12-06 |  | 3 | 1016 | 3 | 1 oz | 3
1999-12-01 | PGE 15.33A 12-01-99-L | Sherwood | 1999-12-01 | 1999-12-06 |  | 25 | 1016 | 26 | 16 oz | 25.5
1999-11-24 | PGE-TW2 11-24-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-11-24 | PGE TOP3 11-24-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-11-24 | PGE TOP4 11-24-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-11-24 | PGE 0.55B 11-24-99-L | Sherwood | 1999-11-24 | 1999-11-30 |  | 44 | 1016 | 41 | 4 oz | 42.5
1999-11-24 | PGE 10.84A 11-24-99-L | Sherwood | 1999-11-24 | 1999-11-30 |  | 13 | 1016 | 11 | 6 oz | 12
1999-11-24 | PGE 10.47B 11-24-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-11-24 | PGE 15.33A 11-24-99-L | Sherwood | 1999-11-24 | 1999-11-30 |  | 10 | 1016 | 20 | 16 oz | 15
1999-11-18 | PGE-TW 2 11-18-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-11-18 | PGE TOP 3 11-18-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-11-18 | PGE TOP4 11-18-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-11-18 | PGE 0.55B 11-18-99-L | Sherwood | 1999-11-19 | 1999-11-23 |  | 26 | 1016 | 29 | 4 oz | 27.5
1999-11-18 | PGE 10.84A 11-18-99-L | Sherwood | 1999-11-19 | 1999-11-23 |  | 22 | 1016 | 22 | 2 oz | 22
1999-11-18 | PGE 10.47B 11-18-99-L | na | na | na |  | na | na | na | na | na | No liqiud
1999-11-18 | PGE 15.33A 11-18-99-L | Sherwood | 1999-11-19 | 1999-11-23 |  | 18 | 1016 | 20 | 1 oz | 19
1999-11-03 | PGE-TW2 11-03-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-11-03 | PGE TOP3 11-03-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-11-03 | PGE TOP4 11-03-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-11-03 | PGE 0.55B 11-2-99-L | Sherwood | 1999-11-03 | 1999-11-05 |  | 14 | 1016 | na | na | 14
1999-11-03 | PGE 10.84A 11-03-99-L | Sherwood | 1999-11-03 | 1999-11-05 |  | 16 | 1016 | 17 | 2oz | 16.5
1999-11-03 | PGE 10.47B 11-03-99-L | Sherwood | 1999-11-03 | 1999-11-05 |  | <1 | na | 1 | 2oz | 1
1999-11-03 | PGE 15.33A 11-03-99-L | Sherwood | 1999-11-03 | 1999-11-05 |  | 18 | 1016 | 18 | 10oz | 18
1999-10-27 | PGE TW 2 10-27-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-10-27 | PGE TOP3 10-27-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-10-27 | PGE TOP4 10-27-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-10-27 | PGE 10.84A 10-27-99-L | Sherwood | 1999-10-28 | 1999-11-02 |  | 19 | 1016 | 18 | 4 oz | 18.5
1999-10-27 | PGE 10.47B 10-27-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-10-27 | PGE 15.33A 10-27-99-L | Sherwood | 1999-10-28 | 1999-11-02 |  | 27 | 1016 | 22 | 30 oz | 24.5
1999-10-20 | PGE TW2 10-20-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-10-20 | PGE TOP3 10-20-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-10-20 | PGE TOP4 10-20-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-10-20 | PGE 10.84A 10-20-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-10-20 | PGE 10.47B 10-20-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-10-20 | PGE 15.33A 10-20-99-L | Sherwood | 1999-10-21 | 1999-10-25 |  | 28 | 1016 | 29 | 10oz | 28.5
1999-10-14 | PGE TW2 10-14-99-L | na | na | na | na | na | na | na | na | 0 | No liqiud
1999-10-14 | PGE TOP3 10-14-99-L | na | na | na | na | na | an | na | na | 0 | No liqiud
1999-10-14 | PGE TOP4 10-14-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-10-14 | PGE 10.84A 10-14-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-10-14 | PGE 10.47B 10-14-99-L | Sherwood | 1999-10-14 | 1999-10-18 |  | 2 | 1016 | 1 | 1/2oz | 1.5
1999-10-14 | PGE 15.33A 10-14-99-L | Sherwood | 1999-10-14 | 1999-10-18 |  | 10 | 1016 | 15 | 30oz | 12.5
1999-10-06 | PGE-TW2 10-6-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-10-06 | PGE TOP3 10-6-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-10-06 | PGE TOP4 10-6-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-10-06 | PGE 10.84A 10-6-99-L | Sherwood | 1999-10-06 | 1999-10-12 |  | 9 | 1016 | 8 | 2oz | 8.5
1999-10-06 | PGE 10.47B 10-6-99-L | na | na | na |  | na | na | na | na | na | No liqiud
1999-10-06 | PGE 15.33A 10-6-99-L | Sherwood | 1999-10-06 | 1999-10-12 |  | 8 | 1016 | 9 | 1oz | 8.5
1999-09-30 | PGE-TW2 9-30-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-09-30 | PGE TOP3 9-30-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-09-30 | PGE TOP4 9-30-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-09-30 | PGE 10.84A 9-30-99-L | Sherwood | 1999-09-30 | 1999-10-05 |  | 4 | 1016 | 4 | 1oz | 4
1999-09-30 | PGE 10.47B 9-30-99-L | Sherwood | 1999-09-30 | 1999-10-05 |  | <1 | na | <1 | 2oz | <1
1999-09-30 | PGE 15.33A 9-30-99-L | Sherwood | 1999-09-30 | 1999-10-05 |  | 7 | 1016 | 8 | 10oz | 7.5
1999-09-23 | PGE TW2 9-23-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-09-23 | PGE TOP3 9-23-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-09-23 | PGE TOP4 9-23-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-09-23 | PGE 10.84A 9-23-99-L | Sherwood | 1999-09-24 | 1999-09-28 |  | 5 | 1016 | 4 | 2 oz | 4.5
1999-09-23 | PGE 10.47B 9-23-99-L | Sherwood | 1999-09-24 | 1999-09-28 |  | 1 | 1016 | 2 | 1 oz | 1.5
1999-09-23 | PGE 15.33A 9-23-99-L | Sherwood | 1999-09-24 | 1999-09-28 |  | 5 | 1016 | 5 | 8 oz | 5
1999-09-23 | PGE 8.58A 9-23-99-L | Sherwood | 1999-09-24 | 1999-09-28 |  | 6 | 1016 | na | 1/2 Gal | 6
1999-09-23 | PGE 5.08A 9-23-99-L | Sherwood | 1999-09-24 | 1999-09-28 |  | 6 | 1016 | na | 1 Gal | 6
1999-09-23 | PGE 3.16A 9-23-99-L | Sherwood | 1999-09-24 | 1999-09-28 |  | 6 | 1016 | na | 2 Gal | 6
1999-09-23 | PGE 0.13A 9-23-99-L | Sherwood | 1999-09-24 | 1999-09-28 |  | ND | na | na | 20 Gal | 0 | El Paso Intake only
1999-09-16 | PGE-TW 2 9-16-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-09-16 | PGE Top3 9-16-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-09-16 | PGE TOP4 9-16-99-L | na | na | na | na | na | na | na | na | na | No liqiud
1999-09-16 | PGE 10.84A 9-16-99-L | Sherwood | 1999-09-16 | 1999-09-20 |  | 4 | 1016 | 4 | 4 oz | 4
1999-09-16 | PGE 10.47B 9-16-99-L | Sherwood | 1999-09-16 | 1999-09-20 |  | <1 | na | <1 | 1 oz | <1
1999-09-16 | PGE 15.33A 9-16-99-L | Sherwood | 1999-09-16 | 1999-09-20 |  | 4 | 1016 | 4 | 6 oz | 4
1999-09-14 | PGE TOP4 9-14-99-L | Sherwood | 1999-09-16 | 1999-09-20 |  | 35 | 1016 |  | 4 oz | 35 | PGE Only
1999-09-12 | PGE TOP6 9-12-99-L | Sherwood | 1999-09-16 | 1999-09-20 |  | 71 | 1016 |  | 4 oz | 71 | PGE Only