## ENRON 7400
Rolls-Royce Energy Systems, Inc.
Expected Performance and emissions
100% Base Load
| 1 | 2 | 3 | 4 | 5
Ambient Temperature (°C) | 15 | 20 | 25 | 30 | 35
Ambient Temperature (°F) | 59 | 68 | 77 | 86 | 95
Pressure (PSI) | 11.2 | 11.2 | 11.2 | 11.2 | 11.2
Elevation (ft ASL) | 7400 | 7400 | 7400 | 7400 | 7400
Relative Humidity (%) | 60 | 60 | 60 | 60 | 60
Mode | MD | MD | MD | MD | MD
Power Turbine | RT62 | RT62 | RT62 | RT62 | RT62
Limit | Base Co | Base Co | Base Co | Base Co | Base Co
Control Parameter | Rating | Rating | Rating | Rating | Rating
PT Speed (RPM) | Actual | Actual | Actual | Actual | Actual
PT Capacity Factor | 1 | 1 | 1 | 1 | 1
Bleed Take off | IP7 | IP7 | IP7 | IP7 | IP7
Nozzle Area (Sq In) | - | - | - | - | -
Combustor | DLE | DLE | DLE | DLE | DLE
Fuel | Nat Gas | Nat Gas | Nat Gas | Nat Gas | Nat Gas
Lower Cal Value (CHU/lb) | 11730 | 11730 | 11730 | 11730 | 11730
Lower Heating Value (Btu/lb) | 21114 | 21114 | 21114 | 21114 | 21114
Water Fuel Ratio | - | - | - | - | -
Water Temp (°C) | - | - | - | - | -
Losses | Mod | Mod | Mod | Mod | Mod
Inlet Loss (in H2O) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Exhaust Loss (in H2O) | 4 | 4 | 4 | 4 | 4
Generator Efficiency (%) | - | - | - | - | -
Gearbox Efficiency (%) | - | - | - | - | -
Brochure GG Power (EGHP) | - | - | - | - | -
Shaft Power (HP) | 28386 | 27155 | 25926 | 24720 | 23525
Heat Rate (BTU/HP.Hr) | 6906 | 6985 | 7078 | 7181 | 7298
Guarantee Power (HP) | 28386 | 27155 | 25926 | 24720 | 23525
Guarantee Heat Rate (BTU/HP.Hr) | 7113 | 7195 | 7290 | 7396 | 7517
BOV Status | Closed | Closed | Closed | Closed | Closed
IP Speed (RPM) | 6615 | 6626 | 6631 | 6637 | 6644
HP Speed (RPM) | 9309 | 9322 | 9336 | 9353 | 9373
PT Speed (RPM) | 4800 | 4800 | 4800 | 4800 | 4800
GG Inlet Flow (lb/s) | 150 | 145.6 | 141.2 | 136.8 | 132.3
Water Flow (lb/Hr) | - | - | - | - | -
Fuel Flow (lb/Hr) | 9284 | 8984 | 8691 | 8407 | 8131
GG Exit Flow (lb/s) | 151 | 146.6 | 142.2 | 137.8 | 133.2
GG Exit Temp (K) | 1040 | 1040 | 1040 | 1040 | 1040
GG Exit Press (PSI) | 42.9 | 41.7 | 40.5 | 39.3 | 38.1
True PTET (Ref) (°C) | 779.2 | 779.2 | 779.2 | 779.1 | 779.1
PT Exit Flow (lb/s) | 152.4 | 147.9 | 143.5 | 139 | 134.4
PT Exit Temp (K) | 775.9 | 780.6 | 785.7 | 790.9 | 796.6
PT Exit Press (PSI) | 11.3 | 11.3 | 11.3 | 11.3 | 11.3
Message Code 1 | 301 | 301 | 301 | 301 | 301
Message Code 2 | 0 | 0 | 0 | 0 | 0
NOx (vppm), 15% O2 | 25 | 25 | 25 | 25 | 25
NOx (tons/yr) | 95.2881 | 92.4745 | 89.7234 | 86.9098 | 84.0336
NOx (vppm), 15% O2 | 45 | 45 | 45 | 45 | 45
NOx (tons/yr) | 171.5186 | 166.4541 | 161.5021 | 156.4375 | 151.2605
CO (vppm) | 5 | 5 | 5 | 5 | 5
CO (tons/yr) | 11.5976 | 11.2552 | 10.9203 | 10.5779 | 10.2278
CO (vppm) | 25 | 25 | 25 | 25 | 25
CO (tons/yr) | 57.9882 | 56.276 | 54.6018 | 52.8895 | 51.1392
50% Base Load
Shaft Power (HP) | 14193 | 13577.5 | 12963 | 12200 | 11762.5
PT Exit Flow (lb/s) | 116.5 | 113.1 | 109.7 | 105.9 | 103
NOx (vppm), 15% O2 | 15 | 15 | 15 | 15 | 15
NOx (tons/yr) | 43.705 | 42.4295 | 41.154 | 39.7284 | 38.6405
NOx (vppm), 15% O2 | 45 | 45 | 45 | 45 | 45
NOx (tons/yr) | 131.1149 | 127.2884 | 123.4619 | 119.1852 | 115.9214
CO (vppm) | 215 | 215 | 215 | 215 | 215
CO (tons/yr) | 381.223 | 370.0971 | 358.9713 | 346.5366 | 337.0469
CO (vppm) | 250 | 250 | 250 | 250 | 250
CO (tons/yr) | 443.2825 | 430.3455 | 417.4085 | 402.9495 | 391.915

## ENRON6800
| 1 | 2 | 3 | 4 | 5
Ambient Temperature (°C) | 15 | 20 | 25 | 30 | 35
Ambient Temperature (°F) | 59 | 68 | 77 | 86 | 95
Pressure (PSI) | 11.4 | 11.4 | 11.4 | 11.4 | 11.4
Elevation (ft ASL) | 6800 | 6800 | 6800 | 6800 | 6800
Relative Humidity (%) | 60 | 60 | 60 | 60 | 60
Mode | MD | MD | MD | MD | MD
Power Turbine | RT62 | RT62 | RT62 | RT62 | RT62
Limit | Base Co | Base Co | Base Co | Base Co | Base Co
Control Parameter | Rating | Rating | Rating | Rating | Rating
PT Speed (RPM) | Actual | Actual | Actual | Actual | Actual
PT Capacity Factor | 1 | 1 | 1 | 1 | 1
Bleed Take off | IP7 | IP7 | IP7 | IP7 | IP7
Nozzle Area (Sq In) | - | - | - | - | -
Combustor | DLE | DLE | DLE | DLE | DLE
Fuel | Nat Gas | Nat Gas | Nat Gas | Nat Gas | Nat Gas
Lower Cal Value (CHU/lb) | 11730 | 11730 | 11730 | 11730 | 11730
Lower Heating Value (Btu/lb) | 21114 | 21114 | 21114 | 21114 | 21114
Water Fuel Ratio | - | - | - | - | -
Water Temp (°C) | - | - | - | - | -
Losses | Mod | Mod | Mod | Mod | Mod
Inlet Loss (in H2O) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Exhaust Loss (in H2O) | 4 | 4 | 4 | 4 | 4
Generator Efficiency (%) | - | - | - | - | -
Gearbox Efficiency (%) | - | - | - | - | -
Brochure GG Power (EGHP) | - | - | - | - | -
Shaft Power (HP) | 29034 | 27775 | 26509 | 25286 | 24095
Heat Rate (BTU/HP.Hr) | 6906 | 6986 | 7078 | 7180 | 7294
Guarantee Power (HP) | 29034 | 27775 | 26509 | 25286 | 24095
Guarantee Heat Rate (BTU/HP.Hr) | 7113 | 7195 | 7290 | 7396 | 7513
BOV Status | Closed | Closed | Closed | Closed | Closed
IP Speed (RPM) | 6614 | 6626 | 6629 | 6636 | 6645
HP Speed (RPM) | 9308 | 9321 | 9334 | 9352 | 9374
PT Speed (RPM) | 4800 | 4800 | 4800 | 4800 | 4800
GG Inlet Flow (lb/s) | 153.4 | 149 | 144.5 | 140 | 135.5
Water Flow (lb/Hr) | - | - | - | - | -
Fuel Flow (lb/Hr) | 9496 | 9190 | 8886 | 8599 | 8324
GG Exit Flow (lb/s) | 154.5 | 150.1 | 145.5 | 141 | 136.5
GG Exit Temp (K) | 1040 | 1040 | 1040 | 1040 | 1040
GG Exit Press (PSI) | 43.9 | 42.6 | 41.4 | 40.2 | 39
True PTET (Ref) (°C) | 779.1 | 779.1 | 779 | 779.1 | 779.1
PT Exit Flow (lb/s) | 155.9 | 151.4 | 146.8 | 142.2 | 137.7
PT Exit Temp (K) | 775.9 | 780.6 | 785.6 | 790.9 | 796.4
PT Exit Press (PSI) | 11.5 | 11.5 | 11.5 | 11.5 | 11.5
Message Code 1 | 301 | 301 | 301 | 301 | 301
Message Code 2 | 0 | 0 | 0 | 0 | 0
NOx (vppm) | 25 | 25 | 25 | 25 | 25
NOx (tons/yr) | 97.4765 | 94.6629 | 91.7867 | 88.9106 | 86.0969
CO (vppm) | 5 | 5 | 5 | 5 | 5
CO (tons/yr) | 11.864 | 11.5215 | 11.1715 | 10.8214 | 10.479

## ENRON6000
| 1 | 2 | 3 | 4 | 5
Ambient Temperature (°C) | 15 | 20 | 25 | 30 | 35
Ambient Temperature (°F) | 59 | 68 | 77 | 86 | 95
Pressure (PSI) | 11.8 | 11.8 | 11.8 | 11.8 | 11.8
Elevation (ft ASL) | 6000 | 6000 | 6000 | 6000 | 6000
Relative Humidity (%) | 60 | 60 | 60 | 60 | 60
Mode | MD | MD | MD | MD | MD
Power Turbine | RT62 | RT62 | RT62 | RT62 | RT62
Limit | Base Co | Base Co | Base Co | Base Co | Base Co
Control Parameter | Rating | Rating | Rating | Rating | Rating
PT Speed (RPM) | Actual | Actual | Actual | Actual | Actual
PT Capacity Factor | 1 | 1 | 1 | 1 | 1
Bleed Take off | IP7 | IP7 | IP7 | IP7 | IP7
Nozzle Area (Sq In) | - | - | - | - | -
Combustor | DLE | DLE | DLE | DLE | DLE
Fuel | Nat Gas | Nat Gas | Nat Gas | Nat Gas | Nat Gas
Lower Cal Value (CHU/lb) | 11730 | 11730 | 11730 | 11730 | 11730
Lower Heating Value (Btu/lb) | 21114 | 21114 | 21114 | 21114 | 21114
Water Fuel Ratio | - | - | - | - | -
Water Temp (°C) | - | - | - | - | -
Losses | Mod | Mod | Mod | Mod | Mod
Inlet Loss (in H2O) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Exhaust Loss (in H2O) | 4 | 4 | 4 | 4 | 4
Generator Efficiency (%) | - | - | - | - | -
Gearbox Efficiency (%) | - | - | - | - | -
Brochure GG Power (EGHP) | - | - | - | - | -
Shaft Power (HP) | 29930 | 28614 | 27326 | 26049 | 24811
Heat Rate (BTU/HP.Hr) | 6905 | 6986 | 7077 | 7180 | 7293
Guarantee Power (HP) | 29930 | 28614 | 27326 | 26049 | 24811
Guarantee Heat Rate (BTU/HP.Hr) | 7112 | 7195 | 7289 | 7395 | 7512
BOV Status | Closed | Closed | Closed | Closed | Closed
IP Speed (RPM) | 6614 | 6624 | 6629 | 6634 | 6642
HP Speed (RPM) | 9308 | 9319 | 9334 | 9350 | 9371
PT Speed (RPM) | 4800 | 4800 | 4800 | 4800 | 4800
GG Inlet Flow (lb/s) | 158.2 | 153.5 | 148.9 | 144.3 | 139.7
Water Flow (lb/Hr) | - | - | - | - | -
Fuel Flow (lb/Hr) | 9788 | 9467 | 9159 | 8858 | 8571
GG Exit Flow (lb/s) | 159.3 | 154.6 | 150 | 145.3 | 140.6
GG Exit Temp (K) | 1040 | 1040 | 1040 | 1040 | 1040
GG Exit Press (PSI) | 45.2 | 43.9 | 42.7 | 41.4 | 40.2
True PTET (Ref) (°C) | 779.1 | 779.1 | 779.1 | 779.1 | 779.1
PT Exit Flow (lb/s) | 160.7 | 156 | 151.3 | 146.6 | 141.9
PT Exit Temp (K) | 775.9 | 780.6 | 785.6 | 790.9 | 796.4
PT Exit Press (PSI) | 11.9 | 11.9 | 11.9 | 11.9 | 11.9
Message Code 1 | 301 | 301 | 301 | 301 | 301
Message Code 2 | 0 | 0 | 0 | 0 | 0
NOx (vppm) | 25 | 25 | 25 | 25 | 25
NOx (tons/yr) | 100.4777 | 97.539 | 94.6003 | 91.6616 | 88.723
CO (vppm) | 5 | 5 | 5 | 5 | 5
CO (tons/yr) | 12.2293 | 11.8716 | 11.5139 | 11.1563 | 10.7986

## ENRON5700
Rolls-Royce plc - Performance Program Coberra 6000 / RB211
Point Number | 1 | 2 | 3 | 4 | 5
Ambient Temperature (°C) | 15 | 20 | 25 | 30 | 35
Ambient Temperature (°F) | 59 | 68 | 77 | 86 | 95
Pressure (PSI) | 11.9 | 11.9 | 11.9 | 11.9 | 11.9
Elevation (ft ASL) | 5700 | 5700 | 5700 | 5700 | 5700
Relative Humidity (%) | 60 | 60 | 60 | 60 | 60
Mode | MD | MD | MD | MD | MD
Power Turbine | RT62 | RT62 | RT62 | RT62 | RT62
Limit | Base Co | Base Co | Base Co | Base Co | Base Co
Control Parameter | Rating | Rating | Rating | Rating | Rating
PT Speed (RPM) | Actual | Actual | Actual | Actual | Actual
PT Capacity Factor | 1 | 1 | 1 | 1 | 1
Bleed Take off | IP7 | IP7 | IP7 | IP7 | IP7
Nozzle Area (Sq In) | - | - | - | - | -
Combustor | DLE | DLE | DLE | DLE | DLE
Fuel | Nat Gas | Nat Gas | Nat Gas | Nat Gas | Nat Gas
Lower Cal Value (CHU/lb) | 11730 | 11730 | 11730 | 11730 | 11730
Lower Heating Value (Btu/lb) | 21114 | 21114 | 21114 | 21114 | 21114
Water Fuel Ratio | - | - | - | - | -
Water Temp (°C) | - | - | - | - | -
Losses | Mod | Mod | Mod | Mod | Mod
Inlet Loss (in H2O) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Exhaust Loss (in H2O) | 4 | 4 | 4 | 4 | 4
Generator Efficiency (%) | - | - | - | - | -
Gearbox Efficiency (%) | - | - | - | - | -
Brochure GG Power (EGHP) | - | - | - | - | -
Shaft Power (HP) | 30271 | 28942 | 27635 | 26343 | 25073
Heat Rate (BTU/HP.Hr) | 6904 | 6986 | 7077 | 7179 | 7294
Guarantee Power (HP) | 30271 | 28942 | 27635 | 26343 | 25073
Guarantee Heat Rate (BTU/HP.Hr) | 7112 | 7195 | 7289 | 7395 | 7513
BOV Status | Closed | Closed | Closed | Closed | Closed
IP Speed (RPM) | 6614 | 6624 | 6629 | 6634 | 6641
HP Speed (RPM) | 9308 | 9319 | 9334 | 9350 | 9370
PT Speed (RPM) | 4800 | 4800 | 4800 | 4800 | 4800
GG Inlet Flow (lb/s) | 160 | 155.3 | 150.6 | 145.9 | 141.2
Water Flow (lb/Hr) | - | - | - | - | -
Fuel Flow (lb/Hr) | 9899 | 9575 | 9262 | 8957 | 8662
GG Exit Flow (lb/s) | 161.1 | 156.4 | 151.7 | 147 | 142.2
GG Exit Temp (K) | 1040 | 1040 | 1040 | 1040 | 1040
GG Exit Press (PSI) | 45.7 | 44.4 | 43.2 | 41.9 | 40.6
True PTET (Ref) (°C) | 779.1 | 779.1 | 779.1 | 779.1 | 779
PT Exit Flow (lb/s) | 162.5 | 157.8 | 153 | 148.3 | 143.4
PT Exit Temp (K) | 775.9 | 780.6 | 785.6 | 790.9 | 796.3
PT Exit Press (PSI) | 12 | 12 | 12 | 12 | 12
Message Code 1 | 301 | 301 | 301 | 301 | 301
Message Code 2 | 0 | 0 | 0 | 0 | 0
NOx (vppm) | 25 | 25 | 25 | 25 | 25
NOx (tons/yr) | 101.6031 | 98.6645 | 95.6633 | 92.7246 | 89.6608
CO (vppm) | 5 | 5 | 5 | 5 | 5
CO (tons/yr) | 12.3663 | 12.0086 | 11.6433 | 11.2856 | 10.9127