## data
|  | unit - new & clean data |  |  |  |  | special adjustments |  | plant data new & clean
|  | kW | Btu/kWhr LHV |  | delta kW% | delta HR% | kW | Btu/kWhr | kW | Btu/kWhr LHV
E Sprint with chilling |  | 48000 | 8570 |  |  |  | 0 |  | 177540 | 10492
E Sprint without chilling |  | 40500 | 8957 |  | -15.62% | 4.516% | 0 |  | 149799.375 | 10965.7928 | ignore this line just to calc the next line!!!!
[7 empty] | 6000 |  | 155799.375 | 10543.4884 | this is the CTG adjusted with the chilling kW added back in.
Sprint without chilling | HP Sprint only | 34500 | 9189 |  | -14.81% | 2.59% | 0 |  | 127606.875 | 10816.5809
no Sprint no chilling |  | 28500 | 9400 |  | -17.39% | 2.296% | 0 |  | 105414.375 | 11064.9538
44385
37449.8438
38949.8438
31901.7188
26353.5938
| Altitude | CIT | Wet Bulb | RH | output | heat rate
| ft asl | F | F | % | kW | Btu/kWhr LHV
S&S Guar | - | 50 |  | 95% | 48580 | 8570
ElectriCities | 150 | 50 |  | 95% | 48316 | 8570
| 40 | 96 |  | 48% | 40559 | 8957
| - | 50 |  | 95% | 48580 | 8570
| - | 50 |  | 95% | 48580 | 8570
| - | 50 |  | 95% | 48580 | 8570
| - | 50 |  | 95% | 48580 | 8570
| - | 50 |  | 95% | 48580 | 8570

## Chart1
4 UNITS W/ FULL SPRINT, 4 UNITS W/ CHILLING (4 TOTAL)
4 UNITS W/ FULL SPRINT, 3 UNITS W/ CHILLING (4 TOTAL)
4 UNITS W/ FULL SPRINT 2 UNITS W/ CHILLING (4 TOTAL)
4 UNITS W/ FULL SPRINT 1 UNIT W/ CHILLING (4 TOTAL)
4 UNITS W/ FULL SPRINT NO CHILLING (4 TOTAL)
3 UNITS W/ FULL SPRINT, 1 UNIT W/ HP SPRINT ONLY, NO CHILLING (4 TOTAL)
3 UNITS W/ FULL SPRINT, 1 UNIT W/ NO SPRINT, NO CHILLING (4 TOTAL)
2 UNITS W/ FULL SPRINT, 2 UNITS W/ HP SPRINT ONLY, NO CHILLING (4 TOTAL)
2 UNITS W/ FULL SPRINT, 2 UNITS W/ HP SPRINT ONLY, NO CHILLING (4 TOTAL)
1 UNIT W/ FULL SPRINT, 3 UNITS W/ HP SPRINT ONLY, NO CHILLING (4 TOTAL)
4 UNITS W/ HP SPRINT ONLY, NO CHILLING (4 TOTAL)
3 UNITS W/ FULL SPRINT, 3 UNITS W/ CHILLING (3 TOTAL)
3 UNITS W/ FULL SPRINT, 2 UNITS W/ CHILLING (3 TOTAL)
3 UNITS W/ FULL SPRINT, 1 UNIT W/ CHILLING (3 TOTAL)
3 UNITS W/ FULL SPRINT, NO CHILLING (3 TOTAL)
2 UNITS W/ FULL SPRINT, 1 UNIT W/ HP SPRINT ONLY, NO CHILLING ( 3 TOTAL)
2 UNITS W/ FULL SPRINT, 1 UNIT W/ NO SPRINT, NO CHILLING (3 TOTAL)
1 UNIT W/ FULL SPRINT, 1 UNIT W/ HP SPRINT, 1 UNIT W/ NO SPRINT, NO CHILLING (3 TOTAL)
2 UNITS W/ FULL SPRINT 2 UNITS W/ CHILLING (2 TOTAL)
2 UNITS W/ FULL SPRINT, 1 UNIT W/ CHILLING (2 TOTAL)
2 UNITS W/ FULL SPRINT, NO CHILLING (2 TOTAL)
1 UNIT W/ FULL SPRINT, 1 UNIT W/ HP SPRINT, NO CHILLING (2 TOTAL)
2 UNITS W/ HP SPRINT ONLY, NO CHILLING (2 TOTAL)
1 UNITS W/ FULL SPRINT, 1 UNIT W/ NO SPRINT, NO CHILLING (2 TOTAL)
1 UNITS W/ HP SPRINT ONLY, 1 UNIT W/ NO SPRINT, NO CHILLING (2 TOTAL)
2 UNITS W/ NO SPRINT AND NO CHILLING (2 TOTAL)
1 UNIT W/ FULL SPRINT AND CHILLING (1 TOTAL)
1 UNIT W/ FULL SPRINT AND NO CHILLING (1 TOTAL)
1 UNIT W/ HP SPRINT ONLY AND NO CHILLING (1 TOTAL)

## curve
|  | 44385 | 10492
|  | 38949.8438 | 10543.4884
|  | 31901.7188 | 10816.5809
|  | 26353.5938 | 11064.9538
Chilling capacity control
plant output | kW | 177540 | 172104.8438 | 166669.6875 | 161234.5312 | 155799.375 | 148751.25 | 143203.125 | 141703.125 | 130606.875 | 134655 | 127606.875 | 133155 | 127719.8438 | 122284.6875 | 116849.5312 | 109801.4062 | 104253.2812 | 97205.1562 | 88770 | 83334.8438 | 77899.6875 | 70851.5625 | 63803.4375 | 65303.4375 | 58255.3125 | 52707.1875 | 49385 | 44385 | 38949.8438 | 31901.7188
| % | 100% | 96.94% | 93.88% | 90.82% | 87.75% | 83.78% | 80.66% | 79.81% | 73.56% | 75.84% | 71.88% | 75% | 71.94% | 68.88% | 65.82% | 61.85% | 58.72% | 54.75% | 50% | 46.94% | 43.88% | 39.91% | 35.94% | 36.78% | 32.81% | 29.69% | 27.82% | 25% | 21.94% | 17.97%
unit 1 | kW | 44385 | 38949.8438 | 38949.8438 | 38949.8438 | 38949.8438 | 31901.7188 | 26353.5938 | 31901.7188 | 26353.5938 | 31901.7188 | 31901.7188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
unit 2 | kW | 44385 | 44385 | 38949.8438 | 38949.8438 | 38949.8438 | 38949.8438 | 38949.8438 | 31901.7188 | 26353.5938 | 31901.7188 | 31901.7188 | 44385 | 38949.8438 | 38949.8438 | 38949.8438 | 31901.7188 | 26353.5938 | 26353.5938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
unit 3 | kW | 44385 | 44385 | 44385 | 38949.8438 | 38949.8438 | 38949.8438 | 38949.8438 | 38949.8438 | 38949.8438 | 31901.7188 | 31901.7188 | 44385 | 44385 | 38949.8438 | 38949.8438 | 38949.8438 | 38949.8438 | 31901.7188 | 44385 | 38949.8438 | 38949.8438 | 31901.7188 | 31901.7188 | 26353.5938 | 26353.5938 | 26353.5938 | 44385 | 44385 | 38949.8438 | 31901.7188
unit 4 | kW | 44385 | 44385 | 44385 | 44385 | 38949.8438 | 38949.8438 | 38949.8438 | 38949.8438 | 38949.8438 | 38949.8438 | 31901.7188 | 44385 | 44385 | 44385 | 38949.8438 | 38949.8438 | 38949.8438 | 38949.8438 | 44385 | 44385 | 38949.8438 | 38949.8438 | 31901.7188 | 38949.8438 | 31901.7188 | 26353.5938 | 5000 | 0 | 0 | 0
plant net heat rate | Btu/kWhr HHV net | 10492 | 10503.6526 | 10516.0651 | 10529.3146 | 10543.4884 | 10602.0568 | 10639.4534 | 10666.4514 | 10753.9289 | 10737.5871 | 10816.5809 | 10492 | 10507.7021 | 10524.7999 | 10543.4884 | 10622.8327 | 10675.3067 | 10774.4906 | 10492 | 10516.0651 | 10543.4884 | 10666.4514 | 10816.5809 | 10753.9289 | 10928.94 | 11064.9538 | 12467.0937 | 10492 | 10543.4884 | 10816.5809
| % | 100% | 100.1% | 100.2% | 100.4% | 100.5% | 101% | 101.4% | 101.7% | 102.5% | 102.3% | 103.1% | 100% | 100.1% | 100.3% | 100.5% | 101.2% | 101.7% | 102.7% | 100% | 100.2% | 100.5% | 101.7% | 103.1% | 102.5% | 104.2% | 105.5% | 118.8% | 100% | 100.5% | 103.1%
unit 1 | Btu/kWhr HHV net | 10492 | 10543.4884 | 10543.4884 | 10543.4884 | 10543.4884 | 10816.5809 | 11064.9538 | 10816.5809 | 11064.9538 | 10816.5809 | 10816.5809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
unit 2 | Btu/kWhr HHV net | 10492 | 10492 | 10543.4884 | 10543.4884 | 10543.4884 | 10543.4884 | 10543.4884 | 10816.5809 | 11064.9538 | 10816.5809 | 10816.5809 | 10492 | 10543.4884 | 10543.4884 | 10543.4884 | 10816.5809 | 11064.9538 | 11064.9538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
unit 3 | Btu/kWhr HHV net | 10492 | 10492 | 10492 | 10543.4884 | 10543.4884 | 10543.4884 | 10543.4884 | 10543.4884 | 10543.4884 | 10816.5809 | 10816.5809 | 10492 | 10492 | 10543.4884 | 10543.4884 | 10543.4884 | 10543.4884 | 10816.5809 | 10492 | 10543.4884 | 10543.4884 | 10816.5809 | 10816.5809 | 11064.9538 | 11064.9538 | 11064.9538 | 10492 | 10492 | 10543.4884 | 10816.5809
unit 4 | Btu/kWhr HHV net | 10492 | 10492 | 10492 | 10492 | 10543.4884 | 10543.4884 | 10543.4884 | 10543.4884 | 10543.4884 | 10543.4884 | 10816.5809 | 10492 | 10492 | 10492 | 10543.4884 | 10543.4884 | 10543.4884 | 10543.4884 | 10492 | 10492 | 10543.4884 | 10543.4884 | 10816.5809 | 10543.4884 | 10816.5809 | 11064.9538 | 30000 | 0 | 0 | 0
factor
| base heat rate |  |  | 10492 | 1
| margin adjustment |  |  | 3.5% | 0.965
| combined |  |  |  | 0.965
| 182540 | 177540 |  | 10124.78
|  | 172104.8438 | 96.94% | 10136.0247
|  | 166669.6875 | 93.88% | 10148.0029
|  | 161234.5312 | 90.82% | 10160.7885
|  | 155799.375 | 87.75% | 10174.4663
|  | 148751.25 | 83.78% | 10230.9848
|  | 143203.125 | 80.66% | 10267.0725
|  | 133155 | 75% | 10124.78
|  | 127719.8438 | 71.94% | 10139.9325
|  | 122284.6875 | 68.88% | 10156.4319
|  | 116849.5312 | 65.82% | 10174.4663
|  | 109801.4062 | 61.85% | 10251.0336
|  | 104253.2812 | 58.72% | 10301.6709
|  | 97205.1562 | 54.75% | 10397.3834
|  | 88770 | 50% | 10124.78
|  | 83334.8438 | 46.94% | 10148.0029
|  | 77899.6875 | 43.88% | 10174.4663
|  | 70851.5625 | 39.91% | 10293.1256
|  | 65303.4375 | 36.78% | 10377.5414
|  | 58255.3125 | 32.81% | 10546.4271
|  | 52707.1875 | 29.69% | 10677.6804
|  | 44385 | 25% | 10124.78
|  | 38949.8438 | 21.94% | 10174.4663
|  | 31901.7188 | 17.97% | 10438.0005