## Table of Contents (hidden)
Rochester Public Utilities LM6000 PC Power Project
Operations & Maintenance Cost Estimate
Table of Contents
Table of Contents |  | 1
Scope
| Project Scope Description | 2
| List of Assumptions | 3
| Map | 4
Summary - Operations & Maintenance Cost Estimate |  | 5
O&M Pre-Mobilization / Mobilization Cost Estimate |  | 6
| Staff Mobilization Schedule | 7
| O&M Mobilization Staffing Plan | 8
| Training Program | 9
| Turnkey/O&M/Owner Scope Split | 10
| Owners' Engineer Cost Estimate | 12
| O&M Pre-Mobilization / Mobilization Estimate Backup/Detail | 13
Commercial Operations O&M Estimate |  | 18
| Staffing Plan | 19
| O&M Estimate Backup/Detail | 20
Major Maintenance Cost Estimate
| Capital & Operational Spares | 25
| GT Scheduled Major Maint. Program (year by year) | 26

## Scope
Rochester Public Utilities LM6000 PC Power Project
Project Scope Description
Scope of Work: | Full Operations and Maintenance services during the Pre-Operating and
Operating Period for one stand alone, gas-fired LM6000 simple cycle peaking facility
to be located at an existing, staffed cogeneration facility
Location: | Rochester, Minnesota
Ownership: | Enron to build, Rochester Public Utilities to own and operate
Enron to have option on power through 2005
Capacity: | 47 | MW (GTs @ ISO)
Equipment: | 1 | ea. LM6000 PC Sprint gas turbines in simple cycle with water injection
| Water treatment plant: |  |  | Leased
Water source: Municipal source
Water injection for NOX control at a rate of 60 gpm/GT
Water injection for Spray Intercooling (SPRINT) at a rate of 7.5 gpm/GT
induced draft Cooling Tower with circ. water pumps with bromine treatment
Chillers with condenser and chilled water pumps
| 0 | SCR units
| Gas Compression required: |  |  | Yes
Distributed Control System
No gas and electric distribution systems
Fuel: | Primary Fuel to be Pipeline Quality Natural Gas
No backup fuel
Operations Mode: | Annual run hours: |  |  | 1200
| Annual # of starts: |  |  | 100
| Annual plant load factor: |  |  | 13.7%
dispatch on Monday-Friday 6am to 10pm, June-September
Facilities: | Administrative office space, storage
Warehouse with some climate control space
Maintenance shop with bay
Central control room and small lab area
Sanitary facilities, to include lockers & showers
PPA: | Term in years: |  | 20
Tentative schedule: | COD is June 2001
Commercial Office: | In owner's scope.
Owners Engineer: | In owner's scope.

## Revisions (hidden)
Rochester Public Utilities LM6000 PC Power Project
Revisions Listing
From | To | Changes/Comments
Rev 0 | Rev 1 | 1. Assume that water plant will be installed instead of leasing of trailer mounted demineralizers. Presents a net reduction in annual O&M expense, but an increase in the initial capital costs of project.
2. Increase in the usage of ammonia for NOx control in the SCR from 25 lbs/hr/GT to 46 lbs/hr/GT, based on specifications for the use of the Engelhard CO + SCR system.
3. Reduction in delivered, unit cost of 28% aqueous ammonia solution from $0.25/lb to $0.15/lb, based on verbal quote from Ashland Chemical, 2/00.
4. Increase in the benefits cost for labor due to change in OEC benefits package for O&M staff.

## Assumptions
Rochester Public Utilities LM6000 PC Power Project
List of Assumptions
1) | Base year for all costs and prices herein: current 2000 US $ (no escalation or inflation included).
2) | Primary fuel: Pipeline Quality Natural Gas delivered at 400 psig.
3) | Backup fuel: # 2 Diesel with no planned usage
4) | Plant operating scenario based on operating Jun-Sept., Mon-Fri., 16 hours/day at a baseload setting. Plant to not be considered available during the weekends (year round) and evenings during the off-peak season. Some maintenance outage will be required in off seasons.
5) | Type of combustion system: standard with water injection for NOx control to 25 ppmv.
6) | Assume all major schedule maintenance to be performed during off-peak season.
7) . | Gas turbine scheduled maintenance costs and initial spare parts based on S&S (George Graham) email dated 12/10/99.
8) | Chemical treatment cost based of use of leased demineralizers on trailers at a cost of $10/Mgal. Assumes a source water quality of 500 ppm TDS water. Owner to provide sample analysis.
9) | Chemical costs, GT major maintenance reserve and 75% of annual maintenance are assumed variable with dispatch; all other costs are fixed.
10) | Variable costs are based on the above assumed plant operating scenario.
11) | Standard Scope Split between Turnkey/Startup Contractor and Owner/Operator per enclosed.
12) | Turnkey Contractor: EECC/NEPCO
13) | Sustaining project capital expenses cover only replacement of initial procurement items at end of useful life.
14) . | Operations staffing plan based on the operating scenario stated above and the assumption that temporary staff (3 total) will be laid on for the peak season to supplement the permanent staffing of 4 for a staff total of 7 O&M persons during the peak season. RPU has no existing O&M staff in the area.
15) | Some administrative and support functions to operate the project are provided by the Operator from the home office or other project sites.
16) | Owner assumed to provide the following functions (Asset Management):
Revenue and Property Book Accounting including customer and fuel supplier billing
Tax Accounting including preparing Local and US tax returns
Annual financial audits by outside auditors.
Maintaining Bank accounts and treasury functions
Commercial contracts and interface with Power Purchasers and Fuel Suppliers
Fuel purchasing & supply, logistics and scheduling
Government and Public Relations
Legal and contractual requirements
Project Human resources (compensation and benefits plans)
Interface with Lenders and Partners regarding funding and information requests
Budgeting, Operating and Capital planning
Dealing with Customs authorities with regard to imported goods and services.
17) | This O&M Estimate does not include the cost of the following items:
Fuel
Water rights and water usage costs
Purchased (backfeed) power and other purchased utilities
Insurance
Buildings: Administration, Warehouse and Shop facilities
Operating or Environmental Permits
Communications facilities (internal & external)
Customs duties, Taxes or VAT
escalation, inflation or exchange rate risk
Emissions, discharge or waste hauling Fees
Security (At Owner's discretion)
18) Major scheduled maintenance intervals per OEM (S&S): Hot Gas Path - 24,000 hrs; Major - 50,000 hours.
19) EPC Contract to provide an allowance for GT familiarization and operations training to O&M staff.
20) | Does not include annual Lease Engine Membership dues.
21) | not used
22) | Assume cooling tower flow rate of 8,500 gpm/GT, approach of 5, range of 10, 3 cycles of concentration.
23) | Assumes that the owner will not accrue for Major scheduled GT maintenance during the term.
24) | not used
25) | not used
26) | Owner's Engineer within the Owner's scope, but estimate is provided.

## Map (hidden)
Rochester Public Utilities LM6000 PC Power Project
Map
Lakefield

## Summary
Rochester Public Utilities LM6000 PC Power Project
Summary - Operations & Maintenance Cost Estimate
[6 empty] | 47 | MW
Expenses before Commercial Operation:
US $
O&M Pre-Mobilization / Mobilization Expenses
| Pre-Mobilization Expenses |  | 0
| Mobilization Payroll and Burden |  | 182382.3764
| Mobilization Operating Expenses |  | 375000
| Mobilization Procurement Expenses |  | 260000
| Total O&M Pre-Mobilization / Mobilization Expenses |  | 817382.3764 | 17.3911 | per kW
| Housing Colony Mobilization Expenses |  | 0
| Commercial Office Mobilization Expenses |  | 0
| Owners' Engineer Expenses |  | 0
| Initial Operating Spares |  | 1000000 | 21.2766 | per kW
| O&M Mobilization Period Fee |  | 80000 | 1.7021 | per kW
| Total |  | 1897382.3764 | 40.3698 | per kW
| Owner's Engineer Estimate |  | 500000
Expenses during Commercial Operation:
Annual US $
O&M Expenses |  |  |  | Fixed ($/kw-yr) | Variable ($/mWh)
| Payroll and Burden |  | 483930.9419 | 10.2964
| Administration & Operations Expenses |  | 180000 | 3.8298 |  | chemical estimate
| Chemicals |  | 60600 |  | 1.0745 | 48600 | # gt x 67.5 gpm x 60 min x annual # hrs x $10/Mgal |  | (trailer lease)
| Maintenance Expenses (excl. GT Scheduled Maint. Program) |  | 174988 | 0.93079 | 2.327 | 0 | 46 lbs/hr/SCR x # SCR units x annual # hrs x $0.20/lb |  | (ammonia)
| Sustaining Capital Expenses |  | 26000 | 0.55319 |  | 2000 | # gts x $2000/yr/gt | (gt soap)
[6 empty] | 10000 | Cooling tower treatment for # annual hrs of service ($10,000/GT/1,400 hrs)
| Total O&M Expenses (ex GT Scheduled Maint.) |  | 925518.9419 |  |  | 159080 | Annual Maint estimate ($000)
SCR Catalyst Replacement Annual Accrual |  |  | 0 |  | 0
GT Scheduled Major Maintenance Program |  | Term total | 0
|  | $/fired hr/GT | 0 |  | 0
|  |  |  | FOM | VOM
Total Plant O&M Expenses (excluding fee) |  |  |  | 15.6102 | 3.4014
Housing Colony Operating Expenses |  |  | 0 | 0 | 0
Commercial Office Expenses |  |  | 0 | 0 | 0
Average Annual Operating Expenses (excluding Fee and G&A)
|  |  |  | ($/kw-yr) | $/mWhr
O&M Annual Fee |  |  | 100000 | 2.1277

## Mob_Estimate (hidden)
Rochester Public Utilities LM6000 PC Power Project
O&M Pre-Mobilization / Mobilization Cost Estimate
US $
O&M Pre-Mobilization Expenses |  | 0
Mobilization Payroll & Burden |  | 145405.9354
Mobilization Operating Expenses
| Employee Expenses | 0
| Recruiting Expenses | 22750
| Relocation Expenses | 40000
| Outside Services | 25000
| Other Supplies & Expenses | 23750
| Communications | 10400
| Temporary Offices/Facilities | 18800
| Training | 131827.5
| Manuals & Procedures | 72100
| Permits | 0
| Insurance | 0
| Operations Support Personnel | 16500
| Total Mobilization Operating Expenses | 361127.5
Mobilization Procurement Expenses
| Office Furnishings & Equipment | 94967.25
| Safety & Environmental Equipment | 32130
| Vehicles & Mobile Equipment (excluding switch engine) | 12495
| Warehouse Furnishings & Equipment | 21000
| Laboratory Equipment | 8400
| Shop Tools & Equipment | 82367.25
| Chemicals, Lubricants, Hydraulic Fluids | 4161.3
| Total Mobilization Procurement Expenses | 255520.8
Total O&M Pre-Mobilization / Mobilization Expenses |  | 762054.2354
Housing Colony Mobilization |  | 0
Commercial Office Mobilization |  | 0
Owners' Engineer |  | 0
Initial Operating Spares |  | 1006075.847
OM&A Mobilization Fee (incl. Commercial Office) |  | 80000
Operator Overhead Charge (G&A) |  | 10000

## Mob_Schedule (hidden)
Rochester Public Utilities LM6000 PC Power Project
Staff Mobilization Schedule
MOB. MONTHS | 18 | 17 | 16 | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | COD
SCHEDULE | [9 empty] | Recruiting/Procedures/CMMS Input/Store Room Setup |  |  |  | Training |  | Commissioning/Startup
PLANT MANAGER
TECHNICIAN III
FACILITY NEEDS
ADMINISTRATION FACILITIES
OFFICE EQUIPMENT
WAREHOUSE/SHOP
VEHICLES
TRAINING FACILITIES
TOOLS AND O&M EQUIPMENT

## MobStaff (hidden)
Rochester Public Utilities LM6000 PC Power Project
O&M Mobilization Staffing Plan
Mobilization Before CommercialOperation
|  | Staff | Number | Salary & | Total Salary
| No. | Area | of | Benefits | & Benefits
| Personnel | A,O or M | Months | US$/Month | US $
PLANT MANAGER | 1 | A | 9 | 9809.1466 | 88282.3194
MAINTENANCE MANAGER | 0 | O | 6 | 9809.1466 | 0
PURCHASING / WAREHOUSE | 0 | M | 5 | 6531.7186 | 0
CLERK | 0 | O,M | 7 | 3427.5261 | 0
PLANT SUPERVISOR | 0 | M | 6 | 6953.1022 | 0
TECHNICIAN III | 2 | O,M | 5 | 5712.3616 | 57123.616
TECHNICIAN II | 0 | O,M | 5 | 4340.5239 | 0
TOTALS | 3 |  |  |  | 145405.9354
Overtime (15%) for last 2 months of Mobilization added to Techs by way of increasing months by .33
ASSUMPTIONS FOR PRE-OPERATIONS STAFF MOBILIZATION
POSITIONS | ANNUAL* | Annual
| SALARY | Hours
| IN US $ | 2080
PLANT MANAGER | 117709.7592
MAINTENANCE MANAGER | 117709.7592
PURCHASING / WAREHOUSE | 78380.6232
CLERK | 41130.313
PLANT SUPERVISOR | 83437.2264
TECHNICIAN III | 68548.3392
TECHNICIAN II | 52086.2866
Straight Time Domestic Rates
Employee Cost Breakdown
| Base | Payroll | Workers |  | Group | General |  |  | Base
Position or | Hourly | Tax | Comp. | O/H | Ins. | Liability | Pension | Burdened | Annual
Employee Name | Rate | Burdens | Ins. | Alloc. | Prem. | Ins. |  | Total | Salary
|  | 14.34% | 7.78% | 12% | 440.66 | 1% | 5%
Administration
PLANT MANAGER | 38.4615 | 5.5154 | 2.9923 | 4.6154 | 2.5423 | 0.54127 | 1.9231 | 56.5912 | 80000
MAINTENANCE MANAGER | 38.4615 | 5.5154 | 2.9923 | 4.6154 | 2.5423 | 0.54127 | 1.9231 | 56.5912 | 80000
PURCHASING / WAREHOUSE | 25 | 3.585 | 1.945 | 3 | 2.5423 | 0.36072 | 1.25 | 37.683 | 52000
CLERK | 12.25 | 1.7567 | 0.95305 | 1.47 | 2.5423 | 0.18972 | 0.6125 | 19.7742 | 25480
Operations & Maint.
PLANT SUPERVISOR | 26.7308 | 3.8332 | 2.0797 | 3.2077 | 2.5423 | 0.38394 | 1.3365 | 40.1141 | 55600
TECHNICIAN III | 21.6346 | 3.1024 | 1.6832 | 2.5962 | 2.5423 | 0.31559 | 1.0817 | 32.9559 | 45000
TECHNICIAN II | 16 | 2.2944 | 1.2448 | 1.92 | 2.5423 | 0.24001 | 0.8 | 25.0415 | 33280
Over Time Domestic Rates
Employee Cost Breakdown
| Base | Payroll | Workers |  | Group | General
Position or | Hourly | Tax | Comp. | O/H | Ins. | Liability | Pension | Burdened
Employee Name | Rate | Burdens | Ins. | Alloc. | Prem. | Ins. |  | Total
|  | 14.34% | 7.78% | 12% | 0 | 1% | 0%
Administration
PLANT MANAGER | 57.6923 | 8.2731 | 4.4885 | 6.9231 | 0 | 0.77377 | 0 | 78.1507
MAINTENANCE MANAGER | 57.6923 | 8.2731 | 4.4885 | 6.9231 | 0 | 0.77377 | 0 | 78.1507
PURCHASING / WAREHOUSE | 37.5 | 5.3775 | 2.9175 | 4.5 | 0 | 0.50295 | 0 | 50.798
CLERK | 18.375 | 2.635 | 1.4296 | 2.205 | 0 | 0.24645 | 0 | 24.891
Operations & Maint.
PLANT SUPERVISOR | 40.0962 | 5.7498 | 3.1195 | 4.8115 | 0 | 0.53777 | 0 | 54.3147
TECHNICIAN III | 32.4519 | 4.6536 | 2.5248 | 3.8942 | 0 | 0.43525 | 0 | 43.9598
TECHNICIAN II | 24 | 3.4416 | 1.8672 | 2.88 | 0 | 0.32189 | 0 | 32.5107
Note on B47: Tina Toburen: Flagged for verification

## Training (hidden)
Rochester Public Utilities LM6000 PC Power Project
Training Program
Employee Class Training | Days | Attending
Basic Plant Training
New Employee Orientation | 1 | All | Supplied by: | O&M Contractor
Plant Safety/Environmental/Firefighting | 5 | All | Supplied by: | O&M Contractor
O&M Practices/Admin Procedures | 1 | All | Supplied by: | O&M Contractor
Simple Cycle Training Program
Power Plant Fundamentals | 0.5 | All | Supplied by: | TriTech
BOP Familiarization * | 0.5 | All | Supplied by: | TriTech
Combustion Turbine Familiarization | 2 | All | Supplied by: | TriTech
Combustion Turbine Operation | 10 | All | Supplied by: | General Electric
BOP Operation * | 0 | All | Supplied by: | TriTech
Combustion Turbine Preventive Maintenance | 0 | All | Supplied by: | TriTech
BOP Preventive Maintenance * | 0 | All | Supplied by: | TriTech
Gas Turbine Mark V | 0 | All | Supplied by: | General Electric
DCS & Mark IV Operations and Maintenance Training (2 people for 4 weeks)
Software & Hardware Maintenance | 0 | Opts/Eng/I&C | Supplied by: | To be determined
Troubleshooting | 0 | Opts/Eng/I&C | Supplied by: | To be determined
Total Class Training Duration | 20 | Days
Estimated Training Expenses |  |  |  | 135500
Meals, Etc. | $50/day x 20 days x 7 employees |  |  | 7000
Travel Expenses (to Minnesota) | $125/day x 12 days x 7 employees |  |  | 10500
| $450 airfare x 7 employees |  |  | 3150
Classroom Facility rental: |  |  |  | 0
Training Coordinator | $75/hr x 10 hrs/wk x 5 weeks + OJT Admin @ 40 hours |  |  | 6750
Phase I - Employee Orientation | $500/day x 5 days |  |  | 2500
Phase II - Technical Training
Fundamentals & BOP Systems | TriTech Quotation |  |  | 30000
Combustion Turbine | General Electric Option at Caledonia |  |  | 61150
Instructor | Included |  |  | 0
DCS Training | General Electric Option |  |  | 0
Control Room Simulator Training | Not included |  |  | 0
Phase III - Leadership Training | By Enron Corp in Houston |  |  | 0
Phase IV - Safety & Environmental | $1500 x 1 trip + 40 hours x $75 |  |  | 4500
Phase V - OJT Program | Supplied by GE during TD of I |  |  | 0
Supplies & Other Expenses | 5% of Subtotal |  |  | 6277.5
Grand Total Training Cost |  |  |  | 131827.5

## Training2 (hidden)
Rochester Public Utilities LM6000 PC Power Project
Training Program
Weeks
Basic Plant Training
| New Employee Orientation (1 day) |  |  | 0.2 |  | Supplied by: | OEC
| Plant Safety/Environmental/Firefighting (1 day) |  |  | 0.2 |  | Supplied by: | OEC
| Power Plant Fundamentals (20 days) |  |  | 4 |  | Supplied by: | OEC
Major Systems Training
| Introduction to Plant Systems (1 day) |  |  | 0.2 |  | Supplied by: | OEC
| Introduction to Power Gen. Equipment (1day) |  |  | 0.2 |  | Supplied by: | OEC
| HRSG & Cooling Water Chemistry (1day) |  |  | 0 |  | Supplied by: | N/A
| Steam Distribution System (1day) |  |  | 0 |  | Supplied by: | N/A
Power Block
| CT-Generator Operation (5 days) |  |  | 1 |  | Supplied by: | OEC
| ST-Generator Operation (3 days) |  |  | 0 |  | Supplied by: | N/A
| HRSG Operation (2 days) |  |  | 0 |  | Supplied by: | N/A
Utility Systems Operator Training
| Water Treatment & Cooling System Operation |  |  |  |  | Supplied by: | N/A
| Fuel Handling Systems |  |  |  |  | Supplied by: | N/A
| Plant Utility Systems (BOP: hydrogen, misc. systems) |  |  |  |  | Supplied by: | OEC
0.2
Control Room Training
| Basic Controls and DCS |  |  |  |  | Supplied by: | OEC
| HRSG Controls |  |  |  |  | Supplied by: | N/A
| CT Controls |  |  |  |  | Supplied by: | OEC
0.6
Basic Maintenance Training
| HRSG Maintenance (vendor) |  |  | 0 |  | Supplied by: | N/A
| ST Maintenance (vendor) |  |  | 0 |  | Supplied by: | N/A
| CTG Maintenance (Vendor) |  |  | 1 |  | Supplied by: | OEC
Electrical/Controls Maintenance Training
| Excitation/Generator Maintenance (vendor) |  |  | 0.2 |  | Supplied by: | OEC
| ST Controls Maintenance (vendor) |  |  | 0 |  | Supplied by: | N/A
| Electrical System Maintenance (vendor) |  |  | 0.2 |  | Supplied by: | OEC
| DCS Maintenance (vendor) |  |  | 0.2 |  | Supplied by: | OEC
| CT Controls |  |  | 0.2 |  | Supplied by: | OEC
Total Class Training Duration (weeks) |  |  |  | 8.4
Training Plan |  |  |  | 12800
Fundamentals Training Material |  |  |  | 48000
Develop Site Specific Technical Systems Training Material |  |  |  | 148000
Instruction for Fundamentals Training Material |  |  |  | 26180
Instruction for Technical Systems Training Material |  |  |  | 96800
DCS/Speedtronics Training |  |  |  | 60000
Facilities & Catering |  |  |  | 48251
Grand Total Training Cost |  |  |  | 440031 |  | 0
Training Time Required by Position: |  |  | Weeks of | Months of | Hired
|  | # People | Training | Training | Months
Group A | Plant Manager | 1 |  |  | 7
Group B | Plant Supervisors, Maintenance Manager | 4 | 8.4 |  | 6
Group C | Technicians IV - V | 0
Group B | Technicians II & III | 5 | 8.4 |  | 4
Group D | Purchasing / Warehouse | 0 |  |  | 4

## Pay & Benefits Calcs (hidden)
Rochester Public Utilities LM6000 PC Power Project
Pay & Benefits Calculations
POSITIONS | ANNUAL* | Annual
| SALARY | Hours
| IN US $ | 2080
PLANT MANAGER | 134532.4946
MAINTENANCE MANAGER | 124133.7592
PURCHASING / WAREHOUSE | 82556.2232
CLERK | 43940.757
PLANT SUPERVISOR | 103810.0792
TECHNICIAN III | 90418.2571
TECHNICIAN II | 84116.2232
Straight Time Domestic Rates
Employee Cost Breakdown
[12 empty] | Mobilization Period |  |  | Operating Period
[12 empty] | Quantity | Hours | Total | Quantity | Hours | Total
| Base | Payroll | Workers |  | Group | General
Position or | Hourly | Tax | Comp. | O/H | Ins. | Liability | Pension | ESOP | 401(k) | Burdened | Base
Employee Name | Rate | Burdens | Ins. | Alloc. | Prem. | Ins. |  |  |  | Total | Annual
|  | 14.34% | 7.78% | 15% | 440.66 | 1% | 5% | 5% | 3% |  | Salary
Administration
Plant Manager | 41 | 5.8794 | 3.1898 | 6.15 | 2.5423 | 0.58761 | 2.05 | 2.05 | 1.23 | 64.6791 | 85280 | 1 | 1120 | 72440.574 | 1 | 2080 | 134532.4946
Maintenance Manager | 38.4615 | 5.5154 | 2.9923 | 5.7692 | 2.5423 | 0.55281 | 1.9231 | 1.9231 |  | 59.6797 | 80000 |  | 1120 | 0 |  |  | 0
Purchasing / Warehouse | 25 | 3.585 | 1.945 | 3.75 | 2.5423 | 0.36822 | 1.25 | 1.25 |  | 39.6905 | 52000 |  | 1120 | 0 |  |  | 0
Clerk | 12.25 | 1.7567 | 0.95305 | 1.8375 | 2.5423 | 0.19339 | 0.6125 | 0.6125 | 0.3675 | 21.1254 | 25480 | 1 | 1120 | 23660.4076 | 1 | 2080 | 43940.757
Operations & Maint.
Supervisor | 31.25 | 4.4813 | 2.4312 | 4.6875 | 2.5423 | 0.45392 | 1.5625 | 1.5625 | 0.9375 | 49.9087 | 65000 |  |  | 0 |  |  | 0
Technician III | 27 | 3.8718 | 2.1006 | 4.05 | 2.5423 | 0.39565 | 1.35 | 1.35 | 0.81 | 43.4703 | 56160 | 2 | 560 | 48686.7538 | 2 | 2080 | 180836.5142
Technician II | 25 | 3.585 | 1.945 | 3.75 | 2.5423 | 0.36822 | 1.25 | 1.25 | 0.75 | 40.4405 | 52000 | 3 | 160 | 19411.4361 | 3 | 640 | 77645.7445
Over Time Domestic Rates
Employee Cost Breakdown
| Base | Payroll | Workers |  | Group | General
Position or | Hourly | Tax | Comp. | O/H | Ins. | Liability | Pension | ESOP | 401(k) | Burdened
Employee Name | Rate | Burdens | Ins. | Alloc. | Prem. | Ins. |  |  |  | Total
|  | 14.34% | 7.78% | 15% | 0 | 1% | 5% | 0% | 0%
Administration
Plant Manager | 61.5 | 8.8191 | 4.7847 | 9.225 | 0 | 0.84329 | 3.075 |  |  | 88.2471 |  | 1 | 0 | 0 | 1 | 0 | 0
Maintenance Manager | 57.6923 | 8.2731 | 4.4885 | 8.6538 | 0 | 0.79108 | 2.8846 |  |  | 82.7834 |  |  |  | 0 |  |  | 0
Purchasing / Warehouse | 37.5 | 5.3775 | 2.9175 | 5.625 | 0 | 0.5142 | 1.875 |  |  | 53.8092 |  |  |  | 0 |  |  | 0
Clerk | 18.375 | 2.635 | 1.4296 | 2.7563 | 0 | 0.25196 | 0.91875 |  |  | 26.3665 |  | 1 | 0 | 0 | 1 | 0 | 0
Operations & Maint.
Supervisor | 46.875 | 6.7219 | 3.6469 | 7.0312 | 0 | 0.64275 | 2.3438 |  |  | 67.2615 |  |  |  | 0 |  |  | 0
Technician III | 40.5 | 5.8077 | 3.1509 | 6.075 | 0 | 0.55534 | 2.025 |  |  | 58.1139 |  | 2 | 112 | 13017.5217 | 2 | 300 | 34868.3616
Technician II | 37.5 | 5.3775 | 2.9175 | 5.625 | 0 | 0.5142 | 1.875 |  |  | 53.8092 |  | 3 | 32 | 5165.6832 | 3 | 75 | 12107.07
[13 empty] | Totals | 182382.3764 |  |  | 483930.9419
Note on N35: EI: Assumed to be the contract staff added for the peak season only
Note on O28: EI: 7 months
Note on O31: EI: 7 months
Note on O34: EI: 3.5 months
Note on O35: EI: 1 month during startup and commissioning. Assume this staff will stay during 1st summer peak.
Note on O52: EI: 20% overtime
Note on O53: EI: 20% overtime
Note on R35: EI: Duration of stay to be the required run season plus one additional week as transition time.
Note on R52: EI: Assumes 5 x 12 hrs/week during peak season and 40 hrs/week in off season
Note on R53: EI: Assumes 5 x 8 hrs/week during run season with 5 hrs/week for overtime, shift turnover, etc.

## LM6000 MMR
Rochester Public Utilities LM6000 PC Power Project
GE LM6000 - Major Maintenance Reserve
Gas Fired Operation |  |  |  |  | Project Life |  | 20 | Years
Lease Club Membership Fees Not Included | [6 empty] | 0 | total cost
[7 empty] | 0 | cost per engine
Total Number of Installed Units |  |  | 1 |  |  |  | 0 | cost per year/engine
[7 empty] | 0 | cost per fired hr/engine
Inputs
Annual Lease Club Fees |  |  | 0 | per engine |  |  | $201,368 for LM6000 DLE (PD) & 20% increase for liquid fuel operation
Lease Engine Usage Fee |  |  | 83650 | per week (1-26 weeks) |  |  | 48,000 hour engine refurbishment assumes assumes 12 week usage of lease engine
Preventative Maintenance |  |  | 0 | per year |  |  | Semi-Annual Preventative Maintenance
Hot Section Refurbishment / 24,000 hrs |  |  | 1403000 | per GT | (rotable exchnage) |  | excludes DLE adder
Engine Refurbishment / 48,000 hrs |  |  | 3000000 | per GT |  |  | excluding 20% adder for DLN
Labor & Engineering / Hot Section |  |  | 25000 |  |  |  | Travel & diem for GE personnel
Labor & Engineering / Major |  |  | 25000 |  |  |  | Travel & diem for GE personnel
Dispatch |  | 1200 | Fired hrs/yr
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Hours (EOY) |  | 1200 | 2400 | 3600 | 4800 | 6000 | 7200 | 8400 | 9600 | 10800 | 12000 | 13200 | 14400 | 15600 | 16800 | 18000 | 19200 | 20400 | 21600 | 22800 | 24000
Maint Inspection (H or M)
Hot Sec & Major Maint. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Preventative Miantenance |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Labor & Engineering | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lease Program |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lease Engine Usage Fee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yearly Totals | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Assumptions:
1. Hot Gas Path inspection conducted at 25,000 fired hour intervals.
2. Major inspection conducted at 50,000 fired hour intervals.
3. Maintenance and lease costs from George Graham/Stewart & Stevenson 12/10/99 e-mail.
BASE LOAD CASE
Gas Fired Operation |  |  |  |  | Project Life |  | 20 | Years
Lease Club Membership Fees Included | [6 empty] | 18013740 | total cost
[7 empty] | 18013740 | cost per engine
Total Number of Installed Units |  |  | 1 |  |  |  | 900687 | cost per year
[7 empty] | 112.5859 | cost per FIRED hour
Inputs
Annual Lease Club Fees |  |  | 170717 | per engine |  |  | $201,368 for LM6000 DLE (PD) & 20% increase for liquid fuel operation
Lease Engine Usage Fee |  |  | 23900 | per week (1-26 weeks) |  |  | 48,000 hour engine refurbishment assumes assumes 12 week usage of lease engine
Preventative Maintenance |  |  | 19000 | per year |  |  | Semi-Annual Preventative Maintenance
Hot Section Refurbishment / 24,000 hrs |  |  | 1403000 | per GT | (rotable exchnage) |  | excludes DLE adder
Engine Refurbishment / 48,000 hrs |  |  | 3000000 | per GT |  |  | excluding 20% adder for DLN
Labor & Engineering / Hot Section |  |  | 25000 |  |  |  | Travel & diem for GE personnel
Labor & Engineering / Major |  |  | 25000 |  |  |  | Travel & diem for GE personnel
Dispatch |  | 8000 | Fired hrs/yr
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Hours (EOY) |  | 8000 | 16000 | 24000 | 32000 | 40000 | 48000 | 56000 | 64000 | 72000 | 80000 | 88000 | 96000 | 104000 | 112000 | 120000 | 128000 | 136000 | 144000 | 152000 | 160000
Maint Inspection (H or M) |  |  |  | H |  |  | M |  |  |  | H |  | M |  |  | H |  |  | M
Hot Sec & Major Maint. | 0 | 0 | 0 | 1403000 | 0 | 0 | 3000000 | 0 | 0 | 0 | 1403000 | 0 | 3000000 | 0 | 0 | 1403000 | 0 | 0 | 3000000 | 0 | 0
Preventative Miantenance |  | 19000 | 19000 | 19000 | 19000 | 19000 | 19000 | 19000 | 19000 | 19000 | 19000 | 19000 | 19000 | 19000 | 19000 | 19000 | 19000 | 19000 | 19000 | 19000 | 19000
Labor & Engineering | 0 | 0 | 0 | 25000 | 0 | 0 | 25000 | 0 | 0 | 0 | 25000 | 0 | 25000 | 0 | 0 | 25000 | 0 | 0 | 25000 | 0 | 0
Lease Program |  | 170717 | 170717 | 170717 | 170717 | 170717 | 170717 | 170717 | 170717 | 170717 | 170717 | 170717 | 170717 | 170717 | 170717 | 170717 | 170717 | 170717 | 170717 | 170717 | 170717
Lease Engine Usage Fee | 0 | 0 | 0 | 0 | 0 | 0 | 286800 | 0 | 0 | 0 | 0 | 0 | 286800 | 0 | 0 | 0 | 0 | 0 | 286800 | 0 | 0
| 0 | 189717 | 189717 | 1617717 | 189717 | 189717 | 3501517 | 189717 | 189717 | 189717 | 1617717 | 189717 | 3501517 | 189717 | 189717 | 1617717 | 189717 | 189717 | 3501517 | 189717 | 189717
|  | 189717 | 379434 | 1997151 | 2186868 | 2376585 | 5878102 | 6067819 | 6257536 | 6447253 | 8064970 | 8254687 | 11756204 | 11945921 | 12135638 | 13753355 | 13943072 | 14132789 | 17634306 | 17824023 | 18013740
Assumptions:
1. Hot Gas Path inspection conducted at 25,000 fired hour intervals.
2. Major inspection conducted at 50,000 fired hour intervals.
3. Maintenance and lease costs from George Graham/Stewart & Stevenson 12/10/99 e-mail.

## Assumed ScopeSplit
Rochester Public Utilities LM6000 PC Power Project
Turnkey/O&M/Owner Scope Split
Turnkey/
| Startup | O&M | Owner | Remarks/Comments
OPERATING EXPENSES (pre-COD):
Payroll and Benefits
for Owner Personnel |  |  | x
for O&M Personnel |  | x
for Turnkey/Startup Personnel | x
Employee Expenses/Recruiting/Relocation
for Owner Personnel |  |  | x
for O&M Personnel |  | x
for Turnkey/Startup Personnel | x
Outside Services
Technical Direction of Installation (TD&I) | x
Vendor reps & startup services | x
Security before COD | x
Security after COD |  | x
O&M related services |  | x
Reliability Availability Maintainability (RAM) Study |  | x |  | EPC to assist & participate
Process Hazards Analysis (HAZOP) | x |  |  | O&M to assist & participate
Other Supplies & Expenses
for O&M Personnel |  | x
for Turnkey/Startup Personnel | x
Communications (phone bills, etc.)
for O&M Personnel |  | x
for Startup Personnel | x
Offices/Buildings/Facilities (temporary)
for O&M Personnel (admin, training, etc.) |  | x
for Startup/Commissioning Personnel | x
Training for O&M Personnel *
Vendor Familiarization Training (CT, ST, HRSG, WT/Desal) | x |  |  | Defined scope req'd
Add'l Major Equip. Vendor (CT,ST,HRSG, WT/Desal,DCS) | x |  |  | Defined scope req'd
OJT during startup/commissioning | x |  |  | Defined scope req'd
Basic Power Plant Training (& all other training) | x |  |  | Defined scope req'd
Permits/Insurance
Construction & Startup Contractor's name | x |  |  | need permit matrix
Operator's name |  | x |  | "
Owner's name |  |  | x | "
Manuals, Procedures and Plans
Startup/Commissioning Plans & Procedures | x
Job Data books | x
Engineering drawings (incl. "as builts") | x |  |  | AutoCad 14 (or apprvd substitute)
Systems Descriptions | x
Test procedures & report | x
O&M Procedures |  | x
Admin and all other Plant procedures |  | x
Punchlist resolution | x |  |  | with O&M walkdown
Purchase and transportation of fuel to plant (startup) | x |  |  | Allowance in LSTK price
Schedule fuel deliveries from supplier |  | x
Purchase of turbine generator startup power (backfeed) |  |  | x
Purchase of construction power (from fence line) | x
Purchase and delivery of Process water (hydrotests, etc) | x
Steam Blows | x |  |  | Given power, fuel and water
Chemical Cleaning (including disposal) | x
Oil Flushes | x
* O&M has overall responsibility for training O&M personnel, but Major Equip. Vendor training (for CTs, STs, HRSGs, Water
Treatment/Desal, and DCS) will be provided under the major equip. purchase orders (with O&M participation in scoping).
Turnkey/
| Startup | O&M | Owner | Remarks/Comments
Warranty Implementation | x |  |  | O&M/Owner participate
Pre-Mobilization expenses
O&M engineering review/comments |  | x
Operating plans/budgets/estimates |  | x
Other Owner directed O&M services |  | x
Fuel/water quality checking (pre-COD) | x
Procurement Expenses:
Office Furnishings & Equipment
Stationary items (built-ins) | x
PABX (internal) telephone system & wiring | x
LAN wiring | x
External communications (satellite dish) |  |  | x
Office/Building furniture |  | x
Office equipment (copiers, fax, etc.) |  | x
Computer hardware/software |  | x
CMMS computer system (incl training) |  | x |  | with Owner approval
Safety & Environmental equipment
Permanent Fire protection | x
Portable fire extinguishers (for offices & buildings) | x
Portable fire extinguishers (exterior) | x
Safety showers/eye washes | x
Permanent Environmental testing equip. | x |  |  | if required
Portable Environmental testing equip. |  | x
O&M Personnel Safety/First Aid equip. |  | x
Vehicles & Mobile Equipment
Construction/Startup Contractor requirements | x
O&M requirements (@ post Comm. Opns level) |  | x
Warehouse/Shop Furnishings & Equipment
Stationary items incl hoists (built-ins) | x
Non-stationary items (bins, furniture, etc.) |  | x
Process Monitoring & Laboratory Equipment
Installed analyzers/instruments | x
Stationary lab items (vent hoods, lab benches, etc.) | x
Analytical equipment, glassware, etc. |  | x
Shop Tools and Equipment
Machine shop/Instrument shop tools |  | x
Maint. (incl I/C&E) test equipment |  | x
Work benches, storage bins |  | x
Hand tools for O&M personnel |  | x
Hand tools for Startup personnel | x
Special Tools
Startup, Std Vendor supply | x
Optional vendor supply |  | x |  | Incl with Vendor PO
Chemicals, Lubricants, Fluids
Initial equipment/vessel fill | x
Consumption (pre-COD) | x
Consumption (post-COD) |  | x
Warehouse stock |  | x
Spare parts*
Consumption (pre-COD) | x
Consumption (post-COD) |  | x
Capital (Overhaul) Spares for major equip. |  | x |  | Incl. with Vendor PO
Operating (Initial) Spares for major equip. |  | x |  | Incl. with Vendor PO
Warehouse stock & BOP spare parts |  | x
Installed Cranes | x
* Turbine spare parts will be purchased based on competitive bids as part of and prior to Turbine vendors selection;
actual parts purchased will be approved by Owner.

## Owner's Engineer (hidden)
Rochester Public Utilities LM6000 PC Power Project
Owners' Engineer Cost Estimate
(US $)
(Contracted Service) | Monthly | No. of Mos. | Total
Engineer (Payroll Cost) | 3500 | 31 | 108500
Engineer (Benefits & Allowances) | 1750 | 31 | 54250
Home Leave & Vacation (4 X yr.) | 350 | 31 | 10850
Vehicle & Fuel | 850 | 31 | 26350
Housing and Utilities | 2000 | 31 | 62000
Misc. Off. Supplies and Exps. | 300 | 31 | 9300
Computer & Other Eqpt. | 0 | 0 | 9000
Meeting and Repr. Exp. (Local) | 300 | 31 | 9300
Off-Island Meeting & Eqpt. Inspection | 2000 | 31 | 62000
Specialized Engineering Support (2 X 15 Mos.) | 12000 | 15 | 180000
Contingency/Other |  |  | 50000
Sub- Total |  |  | 581550
10% Owner's Engineer Fee |  |  | 58155
Total Owner's Engineer Expense |  |  | 639705
Assumptions:
* Owner's Engineer contracted from the Philippine
* Scope of Work is similar to Guam services, act as Owner's QA/QC
* Owner's Engineer mobilized 2 mos. before NTP date to famliarize with construction contract
and Owner's QA/QC requirement and 1 months after COD for winddown

## Mob_Backup (hidden)
| EstimateSummary | Group Item | Budget Item | Line Item | Detail/Basis |  | Total (US $) | LOCAL | FOREIGN | Calculation and Note Area
Rochester Public Utilities LM6000 PC Power Project
O&M Pre-Mobilization / Mobilization Estimate Backup/Detail
O&M Mobilization BudgetOperating ExpensesPublic Relations Title | O&M Mobilization Budget | Operating Expenses | Public Relations | Pre-Mobilization Expenses
O&M Mobilization BudgetOperating ExpensesPublic Relations | O&M Mobilization Budget | Operating Expenses | Public Relations | Payroll and Benefits (US) |  |  | 0 | 0 | 0
[7 empty] | #REF! | #REF! | #REF!
|  |  |  | Travel Expenses in Region | 6 overseas tripsx$6000/trip + $150/dayperdiem x 90 days |  | 49500 | 49500 | 49500
|  |  |  | Travel for Expat To/From Home (UK) | 1 trip/quarter x 3 quarters x $6M/trip |  | 18000 | 18000 | 18000
|  |  |  | Temporary Living (Expat) in Houston | $3000/month x 9 months |  | 27000 | 27000 | 27000
|  |  |  | Tech Services/Studies | 15 mandaysx$75/hrx8hrs/d |  | 9000 | 9000 | 9000
|  |  |  | Miscellaneous (comms, etc.) | $1000/month x 12 months |  | 12000 | 12000 | 12000
[5 empty] | HAZOP Study (3rd party consultant) |  | 25000 | 25000 | 25000
[5 empty] | RAM Study (3rd party consultant) |  | 40000 | 40000 | 40000
|  |  |  | Expat Recruiting | 40% x Base |  | #REF! | #REF! | #REF!
O&M Mobilization BudgetOperating ExpensesPublic Relations Total | O&M Mobilization Budget | Operating Expenses | Public Relations |  | (Assumes Mob period begins 5/99) |  | 0 | 0 | #REF!
O&M Mobilization BudgetOperating ExpensesPayroll with burden Title | O&M Mobilization Budget | Operating Expenses | Payroll with burden | Payroll with burden
|  |  |  | (See detailed MobStaff schedule) |  |  | 145405.9354 | 145405.9354 | 145405.9354
O&M Mobilization BudgetOperating ExpensesPayroll with burden Total | O&M Mobilization Budget | Operating Expenses | Payroll with burden | Basis: Project Schedule |  | Sub-Total | 145405.9354 | 145405.9354 | 145405.9354
O&M Mobilization BudgetOperating ExpensesEmployee Expenses Title | O&M Mobilization Budget | Operating Expenses | Employee Expenses | Employee Expenses
O&M Mobilization BudgetOperating ExpensesEmployee Expenses | O&M Mobilization Budget | Operating Expenses | Employee Expenses | Trips to US | 5 trips to US x $6M + $150/dayperdiem x 50 days |  | 0 | 0
|  |  |  | Misc. (OT meals, Conferences,etc.) | Travel Exp./O.T. Meals (33% of Travel) |  | 0 | 0
|  |  |  | Meal Allowance | $2/day/employee x 200 days x # staff |  |  | 0
O&M Mobilization BudgetOperating ExpensesEmployee Expenses Total | O&M Mobilization Budget | Operating Expenses | Employee Expenses | Basis: HR recommends 1 meal/day subsidized by the company |  | Sub-Total | 0 | 0 | 0
O&M Mobilization BudgetOperating ExpensesRecruiting Expenses Title | O&M Mobilization Budget | Operating Expenses | Recruiting Expenses | Recruiting Expenses
O&M Mobilization BudgetOperating ExpensesRecruiting Expenses | O&M Mobilization Budget | Operating Expenses | Recruiting Expenses |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesRecruiting Expenses | O&M Mobilization Budget | Operating Expenses | Recruiting Expenses | Rest of Staff | Hire from local area |  | 0 | 0 | 0
|  |  |  | HR Support (Regional) | 120 manhrs x $75/hr |  | 9000 | 9000
|  |  |  | HR Travel (within Region) | 5 trips x $2M/trip + $150/dayperdiem x 25 days |  | 13750 | 13750
O&M Mobilization BudgetOperating ExpensesRecruiting Expenses Total | O&M Mobilization Budget | Operating Expenses | Recruiting Expenses | Basis: |  | Sub-Total | 22750 | 22750 | 0
O&M Mobilization BudgetOperating ExpensesRelocation Expenses Title | O&M Mobilization Budget | Operating Expenses | Relocation Expenses | Relocation Expenses
O&M Mobilization BudgetOperating ExpensesRelocation Expenses | O&M Mobilization Budget | Operating Expenses | Relocation Expenses | Plant manager | .5 x Annual Salary covers relocation policy benefits |  | 40000 | 40000
|  |  |  | Rest of Staff | Hire from local area |  | 0 | 0
[7 empty] | 0 | 0 | 0
[7 empty] | 0 | 0
|  |  |  | Locals | 25% of Base Salaries + $200/person for examination |  |  | 0
O&M Mobilization BudgetOperating ExpensesRelocation Expenses Total | O&M Mobilization Budget | Operating Expenses | Relocation Expenses | Basis: |  | Sub-Total | 40000 | 40000 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services Title | O&M Mobilization Budget | Operating Expenses | Outside Services | Outside Services
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Opns support (1 Opns pers) | Startup Coord: See Operations Support section |  | 0 | 0
|  |  |  | per diem(lodging, meals, travel) |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Guards | Turnkey responsibility |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Groundskeepers | Turnkey responsibility |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Translator | N/A |  |  | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Janitors | 2 x grade 10 pay x 12 months |  |  | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Drivers | Have 3 in Housing colony count |  |  | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Clerks/Receptionist |  |  |  | 0
|  |  |  | Maintenance helpers | hired after COD |  | 0 | 0
|  |  |  | Warehousemen | 2 x grade 10 pay x 12 months |  |  | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Legal | 80 manhrs X $125/hr |  | 10000 | 0 | 10000
|  |  |  | Tax | 80 manhrs X $75/hr |  | 6000 | 0 | 6000
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Accounting | 160 manhrs X $75/hr + 2 trip x $1M + 30 days perdiem x$150/day |  | 18500 | 0 | 18500
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Safety | 80 manhrs X $75/hr + 2 trip x $3M + 15 days perdiem x$150/day |  | 14250 | 0 | 14250
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Environmental | 80 manhrs X $75/hr + 1 trip x $3M + 7 days perdiem x$150/day |  | 10050 | 0 | 10050
|  |  |  | Regional Technical Support | 120 manhrs X $75/hr + 2 trip x $3M + 14 days perdiem x$150/day |  | 17100 | 0 | 17100
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | ISO 9002 Certification | Certifying consultant |  | 0 | 0 | 0
|  |  |  | Customs | Misc. agent fees |  | 0 | 0 | 0
|  |  |  | Trash/Waste Disposal | Turnkey responsibility |  | 0 | 0
|  |  |  | Electrical Testing/Calibration | Turnkey responsibility |  | 0 | 0
|  |  |  | Technical/Professional |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Office Equipment Maintenance |  |  | 2000 | 2000
O&M Mobilization BudgetOperating ExpensesOutside Services Total | O&M Mobilization Budget | Operating Expenses | Outside Services | Basis: HR Salary & Benefits Survey |  | Sub-Total | 25000 | 2000 | 75900
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses Title | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Other Supplies & Expenses
|  |  |  | Postage & Freight | $100/month x 9 months |  | 900 | 900
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Office & Misc. Supplies (usage) | $200/month x 9 months |  | 1800 | 1800
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Equipment rental/leasing | 5 equip x $100/month x 9 months |  | 4500 | 4500
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Vehicle Lease,fuel, maint. (temp.) | 2vehx$40/dayx60days |  | 4800 | 4800
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Janitorial Supplies (usage) |  |  | 1000 | 1000
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Bldg. Utilities (water, power, gas) | 9 monthsx$750/month |  | 6750 | 6750
|  |  |  | Vehicle fuel usage | assume 1/2 of avg annual usage |  | 0 | 0
|  |  |  | Vehicle maintenance | $500/vehicle/yr |  | 4000 | 4000
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses Total | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Basis: |  | Sub-Total | 23750 | 23750 | 0
O&M Mobilization BudgetOperating ExpensesCommunications Title | O&M Mobilization Budget | Operating Expenses | Communications | Communications
O&M Mobilization BudgetOperating ExpensesCommunications | O&M Mobilization Budget | Operating Expenses | Communications | Phone Service | 9 months x $1M/month (excludes cellular service) |  | 9000 | 9000
O&M Mobilization BudgetOperating ExpensesCommunications | O&M Mobilization Budget | Operating Expenses | Communications | Cellular Phones | 1ea. x 9 months x $150/month |  | 1350 | 1350
O&M Mobilization BudgetOperating ExpensesCommunications | O&M Mobilization Budget | Operating Expenses | Communications |  | cellular activation fee: 1 ea. $50 |  | 50 | 50
O&M Mobilization BudgetOperating ExpensesCommunications Total | O&M Mobilization Budget | Operating Expenses | Communications | Basis: |  | Sub-Total | 10400 | 10400 | 0
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses Title | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses | Temporary Offices/Facilities
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses | Office Bldgs. | 1000 sq ft x $20/sq ft x 6 months |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses | Trailers (admin only, ex training) | 3x6monthsx$600/month (if available) |  | 10800 | 10800
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses | Sanitary facilities | 5x6monthsx$100/month |  | 3000 | 3000
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses | Misc. Furnishings |  |  | 5000 | 5000
|  |  |  | Temporary Living Quarters | Expat covered in "Relocation" expenses |  |  | 0
Assume admin facilties complete COD minus 12 months
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses Total | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses |  |  | Sub-Total | 18800 | 18800 | 0
O&M Mobilization BudgetOperating ExpensesTraining Title | O&M Mobilization Budget | Operating Expenses | Training | Training
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Basic Plant Training | See Training sheet |  | 131827.5 | 0 | 131827.5
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Major Systems Training
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Plant Chemistry
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Control Room Training
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Basic Maintenance
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Electrical/Controls Maintenance
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Additional Vendor Training
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Per diem for instructors
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Facilities (trailer rental, hall)
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Travel
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Training Coordinator
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Additional Manuals/Documents
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Miscellaneous
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Translation
O&M Mobilization BudgetOperating ExpensesTraining Total | O&M Mobilization Budget | Operating Expenses | Training | Basis: Wilton Center training estimate |  | Sub-Total | 131827.5 | 0 | 131827.5
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures Title | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Manuals/Operating Procedures
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Administration | 5 mandays x $400/day |  | 2000 | 0 | 2000
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Operations check lists | 8 P&IDsx 2 mandays each x $400/day |  | 6400 | 0 | 6400
|  |  |  | Maintenance | 1/2 of Operating procedures |  | 3200 | 0 | 3200
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Maintenance/CMMS (excluding data) | 5 mandays @$400/manday |  | 2000 | 0 | 2000
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Warehouse/Inventory | 5 mandays @$400/manday |  | 2000 | 0 | 2000
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Emergency Plans | 40 mandays @$400/manday |  | 16000 | 0 | 16000
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Safety and Health | 5 mandays @$400/manday |  | 2000 | 0 | 2000
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Environmental Compliance | 20 mandays @$400/manday |  | 8000 | 0 | 8000
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Utility dispatch | 10 mandays @$400/manday |  | 4000 | 0 | 4000
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Government Reporting | 10 mandays @$400/manday |  | 4000 | 0 | 4000
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Owner Reports | 5 mandays @$400/manday |  | 2000 | 0 | 2000
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Houston Reports | 5 mandays @$400/manday |  | 2000 | 0 | 2000
|  |  |  | Accounting | 10 mandays @$400/manday |  | 4000 | 0 | 4000
|  |  |  | Training Program | 10 mandays @$400/manday |  | 4000 | 0 | 4000
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Document Translation | 50% of sum of mandays x $200/day |  | 0 | 0 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Reproduction/Printing |  |  | 10000 | 0 | 10000
|  |  |  | Freight | 5% of Reproduction cost |  | 500 | 0 | 500
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures Total | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Basis: Eval TM consensus |  | Sub-Total | 72100 | 0 | 72100
O&M Mobilization BudgetOperating ExpensesPermits Title | O&M Mobilization Budget | Operating Expenses | Permits | Permits
O&M Mobilization BudgetOperating ExpensesPermits | O&M Mobilization Budget | Operating Expenses | Permits |  |  |  |  | 0
O&M Mobilization BudgetOperating ExpensesPermits Total | O&M Mobilization Budget | Operating Expenses | Permits |  |  | Sub-Total | 0 | 0 | 0
O&M Mobilization BudgetOperating ExpensesInsurance Title | O&M Mobilization Budget | Operating Expenses | Insurance | Operator's Insurance
O&M Mobilization BudgetOperating ExpensesInsurance | O&M Mobilization Budget | Operating Expenses | Insurance |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesInsurance | O&M Mobilization Budget | Operating Expenses | Insurance
O&M Mobilization BudgetOperating ExpensesInsurance Total | O&M Mobilization Budget | Operating Expenses | Insurance |  |  | Sub-Total | 0 | 0 | 0
Operations Support Personnel
|  |  |  | Operations Support Personnel | 2ea.x$350/dayx180 days (includes benefits) |  | 10500 | 0 | 10500
|  |  |  | Per diem | 2ea.x$25/dayx180days (stay in Guest House) |  | 3000 | 3000
|  |  |  | Home leave, travel | 2ea.x$3000 tripx2trips (coach class) |  | 3000 | 0 | 3000
|  |  |  | Tax Protection (over 6 months) | 66% of wages |  |  | 0
|  |  |  | Basis: |  | Sub-Total | 16500 | 3000 | 13500
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies Title | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Office Furnishings, Equipment, Supplies
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Offices (desk, chair, table, misc) | 3ea @ $800/set |  | 2400 | 2400
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Chairs - misc. | 6ea @ $100 |  | 600 | 600
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Bookshelves | 5ea @ $75 |  | 375 | 375
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | File Cabinets | 5ea @ $200 |  | 1000 | 1000
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Storage Shelves/Cabinets | 5ea @ $50 |  | 250 | 250
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Conference Room (table & chairs) | 6ea @ $150 + $1500 |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Tables | 1ea @ $150 |  | 150 | 150
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Chairs | 6ea @ $75 |  | 450 | 450
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Microwave | 1 ea @ $300 |  | 300 | 300
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Coffee Pot | 2 ea. @ $50 |  | 100 | 100
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Refrig. | 1 ea @ $750 |  | 750 | 750
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Stove | 1 ea @ $600 |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Computer Tables | 3ea @ $200 |  | 600 | 600
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Computers w printers | 3ea @ $2500 |  | 7500 | 7500
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Systems Software | 3ea @ $500 |  | 1500 | 1500
|  |  |  | CMMS software/installation | $10M License + $10M installation/training |  | 20000 | 0 | 20000
|  |  |  | CMMS hardware, equipment | 1 PC's ($2500), printer |  | 2500 | 2500
|  |  |  | SUN Acctg System | Software & License |  | 0 | 0 | 0
|  |  |  | SAP Acctg System | Training & Implementation |  | 30000 | 0 | 30000
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Copiers | 1ea @ $8000 |  | 8000 | 8000
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Typewriters | 1ea @ $750 |  | 750 | 750
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Local Area Network | LAN $3M + Installation $1,000 |  | 4000 | 4000
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Calculators | 3ea @ $20 |  | 60 | 60
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Projectors (overhead, slide, screen) | 1ea @ $400,$500, $200 |  | 1100 | 1100
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | TV/VCR/Camcorders | 1ea @ $750/$500/$750 |  | 2000 | 2000
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Microfilm Reader | 1ea @ $800 |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | White Boards | 2ea @ $80 |  | 160 | 160
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | FAX machine | 1ea @ $600 |  | 600 | 600
|  |  |  | Misc Supplies | pens, paper, staplers, envelopes, etc. |  | 1500 | 1500
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Phones | 4ea @ $200 |  | 800 | 800
|  |  |  | CAD Drawing Control System (PC) | 1ea @ $25M (will contract when necessary) |  | 0 | 0
|  |  |  | Janitorial supplies |  |  | 3000 | 3000
|  |  |  | Freight | 5% of cost |  | 4522.25 | 4522.25
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies Total | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Basis: |  | Sub-Total | 94967.25 | 44967.25 | 50000
O&M Mobilization BudgetProcurement ExpensesSafety Equipment & Supplies Title | O&M Mobilization Budget | Procurement Expenses | Safety Equipment & Supplies | Safety & Environmental Equipment & Supplies
O&M Mobilization BudgetProcurement ExpensesSafety Equipment & Supplies | O&M Mobilization Budget | Procurement Expenses | Safety Equipment & Supplies | Personnel Safety equipment | Safety glasses, Hard hats, goggles, face shields, gloves, |  |  | 0
[5 empty] | locks, acid suits, SCBA respirators, safety shoes, etc. |  | 10000 | 10000
|  |  |  | Portable Fire Extinguishers | 30ea. @ $120 |  | 3600 | 3600
|  |  |  | Firehose Cabinet Accessories |  |  | 7700 | 7700
|  |  |  | First Aid equipment | First Aid kit, stretcher, water jell blanket |  | 6000 | 6000
|  |  |  | Safety test Equipment | Biosystem unit, LEL & O2 meter |  | 2500 | 0 | 2500
|  |  |  | Environmental Test Equipment | Noise level meter |  | 800 | 0 | 800
|  |  |  | 6" and 12" containment booms |  | 44700
|  |  |  | 30 ton/hr skimmer |  | 21000
|  |  |  | Misc. anchors, tow bridles, buoys, etc. |  | 17600
|  |  |  | Freight | 5% of cost |  | 1530 | 1530
O&M Mobilization BudgetProcurement ExpensesSafety Equipment & Supplies Total | O&M Mobilization Budget | Procurement Expenses | Safety Equipment & Supplies | Basis: |  | Sub-Total | 32130 | 28830 | 3300
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment Title | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | Vehicles & Mobile Equipment
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | Cars 4 WD w AC | 2ea Admin, Security | $26M | 0 | 0
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | 1/2 ton Pickup Trucks | 1ea/9 months lease | $600/month | 5400 | 5400
|  |  |  | 2 1/2 ton flat bed truck w winch | 1ea | $32M | 0 | 0
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | 6 ton Forklift (outside) | 1ea | $38M | 0 | 0
|  |  |  | 3 ton Forklift (warehouse) | 1ea/9 months lease | $500/month | 4500 | 4500
|  |  |  | 12 passenger Van w/o AC | 1ea | $24M | 0 | 0
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | 18 passenger Van w/o AC | 0ea | $30M | 0 | 0 | 0
|  |  |  | Firefighting equipment | 2ea. extinguisher cart | $1M per | 2000 | 2000
|  |  |  | Backhoe/heavy equipment |  |  | 0 | 0
|  |  |  | Compressor water wash cart | 1ea | $10M | 0 | 0
|  |  |  | 250 cfm Air Compressor (trailer mtd) | 1ea | $16M | 0 | 0
|  |  |  | 400 amp welder(diesel drvr, trailer) | 1ea | $11M | 0 | 0
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | 8 ton Crane | 1ea | $30M (used) | 0 | 0
|  |  |  | Crew Boats | 1ea | $60M (used) | 0 | 0
|  |  |  | Switch engine | 1ea (provided in EPC contract) | $300M | 0 | 0
|  |  |  | Freight | 5% of cost |  | 595 | 595
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment Total | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | Basis: Purchasing Dept. |  | Sub-Total | 12495 | 12495 | 0
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment Title | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment | Warehouse Furnishings & Equipment
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment | Bins/Racks/shelves | includes Lumber, nails, materials (to construct) |  | 14000 | 14000
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment | Equipment/Tools | dollies, scales, carpenter tools, banding & labeling machines |  | 3000 | 3000
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment | Furniture | tables, desks, chairs, file cabinets |  | 2000 | 2000
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment | Miscellaneous Supplies |  |  | 1000 | 1000
|  |  |  | Freight | 5% of cost |  | 1000 | 1000
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment Total | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment |  |  | Sub-Total | 21000 | 21000 | 0
O&M Mobilization BudgetProcurement ExpensesLaboratory Equipment Title | O&M Mobilization Budget | Procurement Expenses | Laboratory Equipment | Laboratory Equipment
O&M Mobilization BudgetProcurement ExpensesLaboratory Equipment | O&M Mobilization Budget | Procurement Expenses | Laboratory Equipment | Laboratory Analyzers (pH, conductivity, spectrophotometer) |  |  | 8000 | 0 | 8000
|  |  |  | Glassware/Misc. Equipment (centrifuge, vacuum pump, PC,scale,oven) |  |  | 0 | 0
|  |  |  | Furniture, cabinets, benches, tables, refrigerator |  |  | 0 | 0
|  |  |  | Fuel Testing equipment | Gas Chromatogragh/Atomic Absorption |  | 0 | 0 | 0
|  |  |  | Freight | 5% of cost |  | 400 | 0 | 400
O&M Mobilization BudgetProcurement ExpensesLaboratory Equipment Total | O&M Mobilization Budget | Procurement Expenses | Laboratory Equipment | Basis: |  | Sub-Total | 8400 | 0 | 8400
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment Title | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | Shop Tools & Equipment
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | Mechanic Hand Tools | tool boxes | $1200 each | 2400
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | I/E Tech Hand Tools | tool boxes | $1500 each | 1500
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | Consumables (Cleaning, Mech. supplies, compounds, I&E supplies, hoses) |  | 8000 | 8000
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | Radios (Basis: Houston 2-way Radio - Motorola HC1000, 2 channels) |  | $1000 each | 4000
|  |  |  | Radio Base |  | $900 each | 900
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | Mechanical Shop Tools & Equip. | High Pressure Hand Pump | $1200 each | 1200
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment |  | Nordstrom Hyper Grease Gun 5 gal. | $3015 each | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment |  | Rockwell Hand Held High Pressure Grease Gun | $960 each | 0
[5 empty] | Hydraulic Torque Wrench | $4000 each | 0
[5 empty] | Centrifugal Pump | $2500 each | 2500
[5 empty] | Pneumatic diaphram pump | $1000 each | 1000
[5 empty] | Bead Blaster | $1800 each | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment |  | Sand Blaster | $900 each | 0
[5 empty] | Portable Air Compressor | $600 each | 600
[5 empty] | Hydraulic Press - 25 ton | $1400 each | 1400
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment Total | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment |  | Post Hole Digger | $1200 each | 0
O&M Mobilization BudgetProcurement ExpensesChemicals, Lubricants, Hydraulic Fluids Title | O&M Mobilization Budget | Procurement Expenses | Chemicals, Lubricants, Hydraulic Fluids |  | Steel Work Bench | $160 each | 160
O&M Mobilization BudgetProcurement ExpensesChemicals, Lubricants, Hydraulic Fluids | O&M Mobilization Budget | Procurement Expenses | Chemicals, Lubricants, Hydraulic Fluids |  | Employee Lockers x 6 | $250 each | 1500
O&M Mobilization BudgetProcurement ExpensesChemicals, Lubricants, Hydraulic Fluids | O&M Mobilization Budget | Procurement Expenses | Chemicals, Lubricants, Hydraulic Fluids |  | Storage Cabinets | $300 each | 300
[5 empty] | Parts Washer | $1000 each | 1000
[5 empty] | Bench Grinder | $400 each | 400
O&M Mobilization BudgetProcurement ExpensesChemicals, Lubricants, Hydraulic Fluids Total | O&M Mobilization Budget | Procurement Expenses | Chemicals, Lubricants, Hydraulic Fluids |  | Drill Press | $2375 each | 2375
O&M Mobilization BudgetO&M Mobilization Fee Title | O&M Mobilization Budget | O&M Mobilization Fee |  |  | AC/DC Welder Generator | $3100 each | 3100
O&M Mobilization BudgetO&M Mobilization Fee | O&M Mobilization Budget | O&M Mobilization Fee |  |  | Assortment Hammer Wrenches | $5000 each | 0
[5 empty] | Flange Spreader | $250 each | 250
[5 empty] | Hoists /Come-a-longs | $1000 each | 1000
[5 empty] | Miscellaneous small hand tools | $5000 set | 5000
O&M Mobilization BudgetO&M Mobilization Fee Total | O&M Mobilization Budget | O&M Mobilization Fee |  | I/E Shop Tools & Test Equipment | Gas Detector Calibration Kit | $500 each | 500
O&M Mobilization BudgetOwner Optional Items Title | O&M Mobilization Budget | Owner Optional Items |  |  | Flow, Press, & Temp Transmitter Communicators | $5000 set | 5000
O&M Mobilization BudgetOwner Optional Items | O&M Mobilization Budget | Owner Optional Items |  |  | Digital Thickness Gauge | $1800 each | 1800
[5 empty] | UV IR Portable Test Kit | $4000 each | 0
[5 empty] | IRD Vibration Meter | $8000 each | 0
[5 empty] | Fluke Digital Multimeter | $350 each | 350
O&M Mobilization BudgetOwner Optional Items Total | O&M Mobilization Budget | Owner Optional Items |  |  | Thermocoupler Calibrator | $950 each | 950
[5 empty] | Precision Pressure Calibrator | $5700 each | 5700
[5 empty] | Simpson Multimeter | $300 each | 0
[5 empty] | RTD Calibrator | $700 each | 700
[5 empty] | Test Gauges 0 -1500 psig. | $1000 set | 1000
[5 empty] | Gravitometer | $5850 each | 0
[5 empty] | PK Tester | $4065 each | 4065
[5 empty] | Pipeline Locator | $3900 each | 0
|  |  |  | Test/Troubleshooting Equipment | Beta Engine Analyzer | $60,000 each | 0
O&M Mobilization BudgetCapital, Operating and BOP Spares (1998$) Title | O&M Mobilization Budget | Capital, Operating and BOP Spares (1996$) |  |  | Oscilloscope | $3000 each | 3000
O&M Mobilization BudgetCapital, Operating and BOP Spares (1998$) | O&M Mobilization Budget | Capital, Operating and BOP Spares (1998$) |  |  | Bore Scope (probe, light source and photo) | $15,000 each | 15000
[5 empty] | Combustible Gas Detector | $1795 each | 1795
|  |  |  | Freight | 5% |  | 3922.25
O&M Mobilization BudgetCapital, Operating and BOP Spares (1998$) Total | O&M Mobilization Budget | Capital, Operating and BOP Spares (1998$)
|  |  |  | Basis: |  | Sub-Total | 82367.25
Chemicals, Lubricants, Hydraulic Fluids
|  |  |  | Warehouse Stock | 1month's worth x chemicals |  | 4161.3 | 4161.3
0
|  |  |  | Freight | 5% of cost (included above) |  |  | 0
|  |  |  | Basis: |  | Sub-Total | 4161.3 | 4161.3 | 0
O&M Mobilization Fee
|  |  |  | Basis/Justification: |  |  | 10% | 0 | 0.1
|  |  |  | 10% of mob. money managed excluding |  |  |  | 0
|  |  |  | Spares, OE and G&A |  |  |  | 0
[6 empty] | Sub-Total | 10% | 0 | 0.1
Operator Overhead Charge (G&A)
|  |  |  | Basis/Justification: | US, UK and like | 10% | 10% | 0 | 0.1
|  |  |  | Annual % of Payroll & Burden based |  |  | 0%
on country type
|  |  |  | Basis: Eval team concensus |  | Sub-Total | 10% | 0 | 0.1
Commercial Office Mobilization
|  |  |  | Assume 75% of 1 Year's annual budget |  |  | 0 | 0 | 0
|  |  |  | Basis:same as yearly G&A |  | Sub-Total | 0 | 0 | 0
Owners' Engineer
|  |  |  | EECC provides Turnkey Contract | See Owners' Engineer detail sheet |  | 0 | 0 | 0
|  |  |  | Basis: |  | Sub-Total | 0 | 0 | 0
Capital, Operating and BOP Spares
|  |  |  | (See Capital/Operating Spares) |  |  | 974407.6 | 0 | 974407.6
0
|  |  |  | Freight | 3% of cost |  | 29232.228 | 0 | 29232.228
|  |  |  | Insurance | 0.25% of cost |  | 2436.019 | 0 | 2436.019
|  |  |  | Basis: |  | Sub-Total | 1006075.847 | 0 | 1006075.847

## O&M_Estimate (hidden)
Rochester Public Utilities LM6000 PC Power Project
Commercial Operations O&M Estimate
US$
Annual
Payroll & Burden |  |  |  | 406043.1916
Administration and Operations Expenses
| Employee Expenses |  |  | 24400
| Permanent Contract Labor |  |  | 50000
| Environmental Expense (including permit fees) |  |  | 26000
| Safety Expense |  |  | 7000
| Buildings & Grounds |  |  | 11000
| Other Supplies & Expenses |  |  | 40000
| Communications |  |  | 21000
Operating Insurance
| Control Room/Laboratory Expenses |  |  | 1000
| Operations Support (Year 1 Only) |  |  | 0
| Total Administration & Operations Expenses |  |  | 180400
Chemicals @ 14% Plant Load Factor (PLF) |  |  |  | 49935.6
Maintenance Expenses (excl. GT ScheduIed Maint. Program)
| Painting |  |  | 58795.0957
| Electrical & Controls |  |  | 28000
| Water Treatment System |  |  | 25000
| Cooling System |  |  | 25000
| Substation/Interconnects |  |  | 10000
| Gas Turbines (excluding scheduled maint.) |  |  | 225000
| Boilers |  |  | 0
| Steam Turbine (including Scheduled Maint.) |  |  | 0
| Water Supply Pipeline and Booster Station |  |  | 0
| Fuel Facility |  |  | 0
| Miscellaneous Maintenance Expense |  |  | 31850
| Total Maintenance |  |  | 403645.0957
Sustaining Capital Expenses |  |  |  | 25552.08
Total O&M Expenses (excl GT Scheduled Maint. Program) |  |  |  | 1065575.9673
GT Scheduled Maintenance Program |  | 20 yr total | 11090544 |  | Annual Avg. | 554527.2
|  |  |  | $/Mwh @ 14% PLF |  | 1.0269
Total Plant O&M Expenses |  |  |  |  | Annual Avg. | 1620103.1673
|  |  |  | $/Mwh @ 14% PLF |  | 3.0002
Housing Colony Operating Expenses
Commercial Office Expenses
Total Project Operating Expenses |  |  |  |  | Annual Avg. | 554527.2
|  |  |  | $/Mwh @14% PLF |  | 1.0269
OM&A Annual Fee |  |  | 160000
Operator Overhead Charge (G&A) |  |  | 60000

## Ops_Staff (hidden)
Rochester Public Utilities LM6000 PC Power Project
Staffing Plan | [10 empty] | Engine Status
[11 empty] | Startup | Run | Cool Down
| Headcount | Burdened | Burdened | Straight Time | Overtime | Total | Total
|  | Straight Time | Overtime | Hours | Hours | Annual Labor | Annual Labor
|  | Hourly Wage | Hourly Wage | Worked | Worked | Cost | Cost by Site
Lakefield Staff
PLANT MANAGER | 1 | 68.5736 | n/a | 2080 |  | 142633.1794
CLERK | 0 | 33.6115 | 44.9431 | 2080 | 50 | 0
PLANT SUPERVISOR | 0 | 40.5101 | n/a | 2080 |  | 0
TECHNICIAN III | 2 | 33.6115 | 44.9431 | 2080 | 120 | 150610.0122
SUMMER PEAKING STAFF | 3 | 52.2222 |  | 720 |  | 112800 | 406043.1916
Total Headcount | 6 |  | Grand Total Annual Labor Cost |  |  | 406043.1916
Straight Time Domestic Rates
Permanent Employee Cost Breakdown
Base Rate
| Base | Payroll | Workers |  | Group | General |  |  |  | Multiplier
Position or | Hourly | Tax | Comp. | O/H | Ins. | Liability | Pension | Burdened | Unburdened | for
Employee Name | Rate | Burdens | Ins. | Alloc. | Prem. | Ins. |  | Total | Annual | Benefit
|  | 14.34% | 7.78% | 15% | 440.66 | 1% | 5% |  | Salary
Administration
PLANT MANAGER | 46 | 6.5964 | 3.5788 | 6.9 | 2.5423 | 0.65617 | 2.3 | 68.5736 | 95680 | 1.4907
MAINTENANCE MANAGER | 38.4615 | 5.5154 | 2.9923 | 5.7692 | 2.5423 | 0.55281 | 1.9231 | 57.7566 | 80000
PURCHASING / WAREHOUSE | 25 | 3.585 | 1.945 | 3.75 | 2.5423 | 0.36822 | 1.25 | 38.4405 | 52000 | 1.5376
CLERK | 12.25 | 1.7567 | 0.95305 | 1.8375 | 2.5423 | 0.19339 | 0.6125 | 20.1454 | 25480 | 1.6445
Operations & Maint.
PLANT SUPERVISOR | 26.4423 | 3.7918 | 2.0572 | 3.9663 | 2.5423 | 0.388 | 1.3221 | 40.5101 | 55000
TECHNICIAN III | 21.6346 | 3.1024 | 1.6832 | 3.2452 | 2.5423 | 0.32208 | 1.0817 | 33.6115 | 45000
TECHNICIAN II | 16 | 2.2944 | 1.2448 | 2.4 | 2.5423 | 0.24481 | 0.8 | 25.5263 | 33280 | 1.5954
Over Time Domestic Rates
Permanent Employee Cost Breakdown
| Base | Payroll | Workers |  | Group | General
Position or | Hourly | Tax | Comp. | O/H | Ins. | Liability | Pension | Burdened
Employee Name | Rate | Burdens | Ins. | Alloc. | Prem. | Ins. |  | Total
|  | 14.34% | 7.78% | 15% | 0 | 1% | 0%
Administration
PLANT MANAGER | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
MAINTENANCE MANAGER | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PURCHASING / WAREHOUSE | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
CLERK | 18.375 | 2.635 | 1.4296 | 2.7563 | 0 | 0.25196 | 0 | 25.4478
Operations & Maint.
PLANT SUPERVISOR | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
TECHNICIAN III | 32.4519 | 4.6536 | 2.5248 | 4.8678 | 0 | 0.44498 | 0 | 44.9431
TECHNICIAN II | 24 | 3.4416 | 1.8672 | 3.6 | 0 | 0.32909 | 0 | 33.2379
Summer Peaking Staff Cost Breakdown
| Flat | Per | Move in/
Position or | Hourly | Diem | Move out |  |  | All In
Employee Name | Rate | $/wk/man | Expenses | Hrs/wk | wks/yr | Total
$/yr/man
Operations & Maint.
PEAKING OPERATOR | 45 | 280 | 1000 | 48 | 15 | 52.2222
Typical Dispatch Day (Mon.-Fri) in Peak Season
|  | Shift Technicians |  |  |  |  | Engine Status
Tech III | Hour | A | B | C | D | E | Startup | Run | Cool Down
Summer Peaking Staff | 0000 | X |  |  |  | X
| 0100 | X |  |  |  | X
| 0200 | X |  |  |  | X
Shift Change | 0300 | X |  |  |  | X
| 0400 | X |  | X
| 0500 | X |  | X |  |  | X
| 0600 | X |  | X |  |  |  | X
| 0700 | X |  | X |  |  |  | X
| 0800 | X |  | X |  |  |  | X
| 0900 | X |  | X |  |  |  | X
| 1000 | X |  | X |  |  |  | X
Shift Change | 1100 | X |  | X |  |  |  | X
| 1200 |  | X |  | X |  |  | X
| 1300 |  | X |  | X |  |  | X
| 1400 |  | X |  | X |  |  | X
| 1500 |  | X |  | X |  |  | X
| 1600 |  | X |  | X |  |  | X
| 1700 |  | X |  | X |  |  | X
| 1800 |  | X |  | X |  |  | X
Shift Change | 1900 |  | X |  | X |  |  | X
| 2000 |  | X |  |  | X |  | X
| 2100 |  | X |  |  | X |  | X
| 2200 |  | X |  |  | X |  |  | X
| 2300 |  | X |  |  | X
Typical Day | ST Hours | 8 | 8 | 8 | 8 | 8
| OT Hours | 4 | 4 | 0 | 0 | 0
|  | A | B | C | D | E
Week | ST Hours | 40 | 40 | 40 | 40 | 40
1 | OT Hours | 20 | 20 | 0 | 0 | 0
Week | ST Hours | 40 | 40 | 60 | 40 | 40
2 | OT Hours | 0 | 20 | 0 | 0 | 0
Week | ST Hours | 40 | 40 | 60 | 60 | 40
3 | OT Hours | 0 | 0 | 0 | 0 | 0
Week | ST Hours | 40 | 40 | 40 | 60 | 60
4 | OT Hours | 0 | 0 | 0 | 0 | 0
Week | ST Hours | 40 | 40 | 40 | 40 | 60
5 | OT Hours | 20 | 0 | 0 | 0 | 0
5 Week | ST Hours | 200 | 200 | 240 | 240 | 240
Totals | OT Hours | 40 | 40 | 0 | 0 | 0
15 Week | ST Hours | 600 | 600 | 720 | 720 | 720
Totals | OT Hours | 120 | 120 | 0 | 0 | 0
Balance of Year | ST Hours | 1480 | 1480 | 0 | 0 | 0
Totals (37 Wks) | OT Hours | 0 | 0 | 0 | 0 | 0
Annual | ST Hours | 2080 | 2080 | 720 | 720 | 720
Totals | OT Hours | 120 | 120 | 0 | 0 | 0

## Contract_Staff (hidden)
Rochester Public Utilities LM6000 PC Power Project
Contract & Opns Support Staffing Plan
(US$)
PERMANENT CONTRACT LABOR:
|  |  | INDIVIDUAL | TOTAL ANNUAL | TOTAL
| STAFFING | GRADE | SALARY | SALARIES | BENEFITS | TOTAL
SECURITY GUARDS | 0 | 9 | 45000 | 0 | 0 | 0
JANITORS | 0 | 10 | 27000 | 0 | 0 | 0
GROUNDS/GENERAL WORKS | 0 | 10 | 27000 | 0 | 0 | 0
WAREHOUSE HELPER | 0 | 10 | 27000 | 0 | 0 | 0
O&M TRAINEES/HELPERS | 0 | 10 | 27000 | 0 | 0 | 0
CHEMIST HELPER | 0 | 10 | 27000 | 0 | 0
TOTAL CONTRACT STAFF | 0 |  |  | 0 | 0 | 0
OPERATIONS SUPPORT (duration of 6 months after COD):
|  | PAYROLL, |  | HOME LEAVE
| STAFFING | TAX PROT. | PER DIEM | TRAVEL | TOTAL
OPNS SUPPORT PERSONNEL (EXPATS) | 2 | 0 | 0 | 0 | 0
TOTAL OPNS SUPPORT STAFF | 2 |  | 0 | 0 | 0

## SALARY-BENEFITS LOOKUP TABLE (hidden)
Rochester Public Utilities LM6000 PC Power Project
Salary-Benefits Lookup Table
|  | BASE SALARY |  |  |  | BENEFITS | [6 empty] | TOTAL
|  | MONTHLY | MONTHLY | MONTHLY | ANNUAL | REIMBURSABLE | NON-REIM | 20% ON BASE |  | 30% HOUSING | BENEFITS | TOTAL | SALARY &
| GRADE | MIN | MAX | AVG | AVG | ALLOWANCES | ALLOWANCES | BONUS | RETIREMENT | ALLOWANCE | IN KIND | BENEFITS | BENEFITS
Vice President | 1 | 55000 | 80000 | 67500 | 810000 | 111250 | 762600 | 162000 | 251100 | 243000 | 669800 | 2199750 | 3009750
General Manager | 2 | 40000 | 50000 | 45000 | 540000 | 77500 | 417600 | 108000 | 167100 | 162000 | 491200 | 1423400 | 1963400
Sr. Mgr/Perf.Mgr/Purch.Mgr/Ctrl | 3 | 23000 | 31000 | 27000 | 324000 | 50500 | 226200 | 64800 | 100440 | 97200 | 346320 | 885460 | 1209460
HR Manager/Shift Mgr. | 4 | 19000 | 22500 | 20750 | 249000 | 41125 | 190500 | 49800 | 77190 | 74700 | 190320 | 623635 | 872635
Asst. Mgr/Ctrl Rm Optr/Chemist | 5 | 14000 | 19500 | 16750 | 201000 | 35125 | 154500 | 40200 | 62310 | 60300 | 160180 | 512615 | 713615
Sr. Operator/Accountant | 6 | 8500 | 14350 | 11425 | 137100 | 21425 | 97530 | 27420 | 42501 | 41130 | 122328 | 352334 | 489434
Operator/Mechanic/Jr. Acct. | 7 | 8500 | 10900 | 9700 | 116400 | 19700 | 65280 | 23280 | 36084 | 34920 | 78052 | 257316 | 373716
Jr Operator/Jr. Mechanic/Secr. | 8 | 3800 | 5250 | 4525 | 54300 | 9050 | 32860 | 10860 | 16833 | 16290 | 7474 | 93367 | 147667
Assistant/Grounds Supvr. | 9 | 2500 | 5000 | 3750 | 45000 | 7500 | 24000 | 9000 | 13950 | 13500 | 3600 | 71550 | 116550
Jr. Asst./Driver/Janitor | 10 | 1500 | 3000 | 2250 | 27000 | 4500 | 6000 | 5400 | 8370 | 8100 | 3360 | 35730 | 62730
| US DOLLAR: |  |  | 1
| CUMULATIVE INFLATION MULTIPLIER: |  |  | 0%
| YEAR THAT DATA IS BEING USED: |  |  | 2000 | Enter here the year that the above data is being used.
| YEAR THAT DATA WAS SUPPLIED: |  |  | 2000
| DIFFERENCE IN YEARS: |  |  | 0
| AVG ANNUAL US INFLATION RATE: |  |  | 9% | Enter here the desired annual Indian inflation rate used to convert 1999 Rupees to present terms.
Source: Salary and benefits information provided by HR (Ranen Sengupta) Sept. 1999.
1/ Annual 30% Housing & Utilities allowance provided

## Local_Benefits (hidden)
Rochester Public Utilities LM6000 PC Power Project
Personnel Benefits
Benefits
| Retirement1 | 31.3% | of Base Salary
| Allowances3 | note 2
| Bonus | 20% | of Base Salary
| Benefits in Kind4 | note 2
NOTES:
1/ Includes PF (FICA) -12%; Gratuity (severence) - 4.3%; and Superannuation - 15%.
2/ These vary based on annual salary. See Salary & Benefits table for each pay grade.
3/ Allowances include:
- Disturbance and House Rent (one year only)
- Housing Maintenance
- Conveyance (Transportation allowance for grade 4 and lower)
- Leave Travel Assistance
- Education
- Driver (grade 2 and higher)
4/ Benefits in Kind include:
- Furniture
- Car lease, maintenance and fuel (grade 3 and higher)
- Interest free transportation loans (grades 4-6)
- Medical insurance premium
5/ Housing & Utilities Allowance not provided since a Housing Colony is assumed.
6/ Source: Salaries and benefits from Enron HR and DPC (late 1997).

## O&M_Backup (hidden)
Line Item | Detail/Basis |  | Total (US $) | LOCAL | FOREIGN | Calculation and Note Area
Rochester Public Utilities LM6000 PC Power Project
O&M Estimate Backup/Detail
Payroll & Burden (Total over project life) |  |  |  | 0% | 100%
Salaries & Benefits |  |  | 406043.1916 | 0 | 406043.1916
|  |  | 0 | 0 | 0
|  |  | 0 | 0 | 0
|  |  | 0 | 0 | 0
Basis: HR data |  | Sub-Total | 406043.1916 | 0 | 406043.1916
Employee Expenses |  |  |  | 100% | 0%
Training | Training ($ 2,700 /tech x 2 tech) |  | 5400 | 5400 | 0
HO Meetings (Travel & Expense) | 3 trips @ $ 1,000/trip |  | 3000 | 3000 | 0
Participation in Industry Groups | 2 meetings @ $1,500/meeting |  | 3000 | 3000 | 0
Commercial Business Trips | 3 trips @ $ 1000/trip |  | 3000 | 3000 | 0
Misc Expense | $ 10,000/yr |  | 10000 | 10000 | 0
|  |  | 0 | 0 | 0
|  |  | 0 | 0 | 0
Basis: |  | Sub-Total | 24400 | 24400 | 0
Permanent Contract Labor |  |  |  | #DIV/0! | #DIV/0!
Contract Labor - General | Weekend/Night Security | Fixed | 50000 | 50000 | 0
| 52 weeks x 5 days x 12 hours x $20 | 62400
| 52 weekends x 48 hours x $20 | 49920 |  | 50000 | 0
Basis: Based on Caledonia estimate |  |  | 50000
Environmental Expense (including permit fees) |  |  |  | 88.46% | 11.54%
CEMS Testing Consultant | $ 16,000/site/yr |  | 16000 | 16000 | 0
Special Gases CEMS testing | $ 2,000/site/yr |  | 2000 | 2000 | 0
CEMS Maintenance | $ 5,000/site/yr |  | 5000 | 5000 | 0
Misc Environmental Costs | $ 3,000/site/yr |  | 3000 | 0 | 3000
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
Basis: Based on Caledonia estimate |  | Sub-Total | 26000 | 23000 | 3000
Safety Expense |  |  |  | 100% | 0%
Safety Training | $3,000/site/yr |  | 3000 | 3000 | 0
Routine Safety Supplies | $ 4,000/site/yr |  | 4000 | 4000 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
Basis: Based on Caledonia estimate |  | Sub-Total | 7000 | 7000 | 0
Buildings & Grounds |  |  |  | 81.82% | 18.18%
Building Repairs | $ 2,000/site/yr |  | 2000 | 0 | 2000
Painting | $ 6,000/site/yr |  | 6000 | 6000 | 0
Landscaping and Site Maintenance | $ 3,000/site/yr |  | 3000 | 3000 | 0
|  |  |  | 0 | 0
Basis: Based on Caledonia estimate |  | Sub-Total | 11000 | 9000 | 2000
Other Supplies & Expenses |  |  |  | 92% | 8%
Office Supplies & Expenses |  |  | 5000 | 5000 | 0
Materials, Small Equip & Supplies |  |  | 1250 | 1250 | 0
Outside Services | Garbage & Trash, Janitorial, & Pest Control |  | 2000 | 2000 | 0
Employee Uniforms |  |  | 2000 | 2000 | 0
Office Equipment Rental |  |  | 1250 | 0 | 1250
Other Rents |  |  | 375 | 0 | 375
PC Hardware/Software |  |  | 750 | 750 | 0
PC Maintenance |  |  | 375 | 0 | 375
Postage & Freight Expenses, FedEx |  |  | 1200 | 0 | 1200
Utilities (office water, garbage removal) |  |  | 1200 | 1200 | 0
Public relations/Contributions |  |  | 2000 | 2000 | 0
|  |  |  | 0 | 0
|  |  | 2000 | 2000 | 0
|  |  | 2400 | 2400 | 0
|  |  |  | 0 | 0
|  |  | 1800 | 1800 | 0
|  |  | 3000 | 3000 | 0
|  |  | 2000 | 2000 | 0
|  |  |  | 0 | 0
|  |  | 4000 | 4000 | 0
|  |  | 2400 | 2400 | 0
|  |  | 0 | 0 | 0
|  |  | 0 | 0 | 0
|  |  | 0 | 0 | 0
|  |  | 5000 | 5000 | 0
|  |  | 0 | 0 | 0
0
Basis: Based on Caledonia estimate |  | Sub-Total | 40000 | 36800 | 3200
Communications |  |  |  | 91.43% | 8.571%
Phone service | Admin-$18,000/yr + $1200/site/yr |  | 19200 | 19200 | 0
Pagers | 9 x $15/mo x 12 mo. |  |  | 0 | 0
Cellular phone service | 1 x $150/mo x 12 mo. |  | 1800
Basis: Based on Caledonia estimate |  | Sub-Total | 21000 | 19200 | 0
Operating Insurance
Operating Insurance | Estimated by Risk Management |  |  |  | 0
It will add incrementally to the Enron Pool of insured assets
Basis: |  | Sub-Total | 0 | 0 | 0
Control Room/Laboratory Expenses |  |  |  | 50% | 50%
Oil Analysis |  |  | 1000 | 500 | 500
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
Basis: Based on Caledonia estimate |  | Sub-Total | 1000 | 500 | 500
Operations Support (Year 1 Only) |  |  |  | #DIV/0! | #DIV/0!
Operations Support Personnel | 2ea.x$350/dayx180days (includes benefits) |  |  | 0 | 0
Per diem | 2ea.x$25/dayx180days (stay in Guest House) |  |  | 0 | 0
Home leave, travel | 2ea.x$3000 trip x 2trips (coach class) |  |  | 0 | 0
Tax Protection (over 6 months) | 66% of wages |  |  | 0 | 0
2 US Expats for 6 months to aid in Initial Operating Period |  | Sub-Total | 0 | 0 | 0
Chemicals (including Water treatment & Lubricity Agent) |  |  |  | 100% | 0%
Technical/Professional Services | 1 trip x $3M |  | 0 | 0 | 0
Pretreatment chemicals | Chlorine/Clarifier/filter | 80% | 0 | 0 | 0
Demin Water for Water Wash | $8.80/1000 gal*500 gal/wash/wk*15 wks*6 units |  | 396 | 396 | 0
Resin Replacement | Boiler/Steam Cycle Treatment | 80% | 0 | 0 | 0
Water Wash Detergent | $500/wash/wk/unit x 15wks x 6 units |  | 45000 | 45000 | 0
Boiler Chemicals |  |  | 0 | 0 | 0
Desal RO Chemicals & Membrane replacement |  |  | 0 | 0 | 0
Potable Water Chemicals |  |  | 0 | 0 | 0
Hydrogen (generators) | Assume air cooled |  | 0 | 0 | 0
Waste Water Treatment |  |  | 0 | 0 | 0
Lubricity Agent | n/a with PCFD installed on GTs (GTs will have PCFD per Dev. Eng.) |  | 0 | 0 | 0
taxes/freight | 10% of total |  | 4539.6 | 4539.6 | 0
|  |  |  | 0 | 0
Basis: Based on Caledonia estimate |  | Sub-Total | 49935.6 | 49935.6 | 0
Painting |  |  |  | 100% | 0%
Paint & Materials | Scaled on MW |  | 58795.0957 | 58795.0957 | 0
Basis: 13 years of Actuals from Tx City/Clear Lake Plants |  | Sub-Total | 58795.0957 | 58795.0957 | 0
Electrical & Controls |  |  |  | 40% | 60%
Controls (DCS) | $ 8,000/yr/site |  | 8000 | 1200 | 6800
Meters and Relay work | $ 7,000/yr/site |  | 7000 | 3500 | 3500
Switchgear / Breakers | $ 9,000/yr/site |  | 9000 | 4500 | 4500
Instrumention Calibration | $ 2,000/yr/site |  | 2000 | 1000 | 1000
Motor Overhauls | $ 2,000/yr/site |  | 2000 | 1000 | 1000
|  |  |  | 0 | 0
|  |  |  | 0 | 0
Basis: Based on Caledonia estimate |  | Sub-Total | 28000 | 11200 | 16800
Water Treatment System |  |  |  | #DIV/0! | #DIV/0!
Repair Parts | Scaled on Steam Turbine MW |  |  | 0 | 0
Outside Repair Services | $140,000 x (1ST/1ST) x (178MW/140MW)^0.6 x 75% |  |  | 0 | 0
Technical/Professional Services | 75% factor for lower local labor |  |  | 0 | 0
Outside Contract Labor |  |  |  | 0 | 0
Equipment rental |  |  |  | 0 | 0
Miscellaneous |  |  |  | 0 | 0
Freight | 5% of 75% of total |  |  | 0 | 0
Basis: 7 years of Actuals from Tx City Plant |  | Sub-Total | 0 | 0 | 0
Cooling System |  |  |  | #DIV/0! | #DIV/0!
Repair Parts | Scaled on MW |  |  | 0 | 0
Outside Repair Services | scaled: $179,000 x (500MW/414MW)^0.6*75%labor |  |  | 0 | 0
Technical/Professional Services | 75% factor for lower local labor |  |  | 0 | 0
Outside Contract Labor |  |  |  | 0 | 0
Equipment rental |  |  |  | 0 | 0
Miscellaneous |  |  |  | 0 | 0
Freight | 5% of 75% of total |  |  | 0 | 0
Basis: 13 years of Actuals from Tx City/Clear Lake Plants |  | Sub-Total | 0 | 0 | 0
Substation/Interconnects |  |  |  | #DIV/0! | #DIV/0!
Repair Parts | Scaled on genrator MW and # generators |  |  | 0 | 0
Electric Meter Calibration & Testing | Scaled cost = Labor Cost + Materials Cost |  |  | 0 | 0
Outside Repair Services | Labor cost (50% of total) = 50% x $94,000 x 50% |  |  | 0 | 0
Technical/Professional Services | Material Cost (50% of total) = 50% x $94,000 x (4gens/4.5gens) |  |  | 0 | 0
Outside Contract Labor | x (112MW/104MW)^0.6 |  |  | 0 | 0
Equipment rental |  |  |  | 0 | 0
Miscellaneous |  |  |  | 0 | 0
Freight | 5% of 11% of total |  |  | 0 | 0
Basis: 12 years of Actuals from Tx City/Clear Lake Plants |  | Sub-Total | 0 | 0 | 0
Gas Turbines (excluding scheduled maint.) |  |  |  | 36% | 64%
Repair Parts | Scaled on # turbines and turbine MW |  |  | 0 | 0
6 - 7EA | $ 30k/unit x 6 unit |  | 180000 | 45000 | 135000
Instruments | $ 6k/unit x 6 unit |  | 36000 | 9000 | 27000
Filters | $ 13k/unit x 6 unit |  | 78000 | 19500 | 58500
Misc. | $ 5k/unit x 6 unit |  | 30000 | 7500 | 22500
|  |  |  | 0 | 0
Freight | 5% of 75% of total |  | 0 | 0 | 0
Basis: Based on Caledonia estimate |  | Sub-Total | 225000 | 81000 | 243000
Boilers |  |  |  | 25% | 75%
Repair Parts | Scaled on Gas Turbine MW. |  |  | 0 | 0
Outside Repair Services | $337,000 x (3GTs/3GTs) x (112MW/104MW)^0.6 x 75% x 75% |  |  | 0 | 0
Technical/Professional Services | 75% factor due to Tx City/Clear Lk were cogen plants & suppl. fired |  |  | 0 | 0
Outside Contract Labor | 75% factor for lower local labor |  |  | 0 | 0
Equipment rental | Triple pressure boilers |  |  | 0 | 0
Miscellaneous |  |  |  | 0 | 0
Freight | 5% of 75% of total |  |  | 0 | 0
Assume non-local manufacturer
Basis: 13 years of Actuals from Tx City/Clear Lake Plants |  | Sub-Total | 0 | 0 | 0
Steam Turbine (including Scheduled Maint.) |  |  |  | #DIV/0! | #DIV/0!
Non-scheduled maint. parts/repairs | Scaled on Steam Turbine MW |  |  | 0 | 0
Outside Repair Services | $460,000x(178MW/140MW)^.6x75% labor factor |  |  | 0 | 0
Technical/Professional Services | 75% factor for lower local labor |  |  | 0 | 0
Scheduled Maint. |  |  |  | 0 | 0
Equipment rental | this includes annualized cost for Major Maint Program |  |  | 0 | 0
Miscellaneous | This is an ANNUALIZED FIGURE for ST MMR planning |  |  | 0 | 0
Auxiliary Parts |  |  |  | 0 | 0
Freight | 1% of 75% of total |  | 0 | 0 | 0
Basis: 7 yrs of TX City Plant actuals on 140MW steam turbine including Schedule Maint. |  | Sub-Total | 0 | 0 | 0
Water Supply Pipeline and Booster Station |  |  |  | 0% | 100%
Repair Parts | 1.5% of TIC ($6,000,000) |  | 0 | 0 | 0
Outside Repair Services | ROW maint., pigging, pump repair, cathodic protection
Technical/Professional Services | 61 kms of 16" cast iron pipe
Outside Contract Labor
Equipment rental | Deleted from scope
Miscellaneous
Freight
|  | Sub-Total | 0 | 0 | 0
Fuel Facility |  |  |  | 0% | 100%
Repair Parts | Misc. repairs (yearly average) |  | 0 | 0 | 0
Outside Repair Services | plus Dredging cost ($200M every 2 years) |  | 0 | 0 | 0
Technical/Professional Services |  |  |  | 0 | 0
Outside Contract Labor |  |  |  | 0 | 0
Equipment rental |  |  |  | 0 | 0
Miscellaneous | Deleted from Scope
Freight
|  | Sub-Total | 0 | 0 | 0
Miscellaneous Maintenance Expense |  |  |  | 69.51% | 30.49%
Misc Maint Materials & Consumables | $ 7000/site/yr. |  | 7000 | 3500 | 3500
Vehicle (s) |  |  |  | 0 | 0
P/U Truck Fuel; Repairs & maintenance; lease (5ea @ $600/mo.) |  |  | 7200 | 5400 | 1800
Forklift Fuel, Maint. & Lease | (3 ea @ $450/mo.) |  | 5400 | 4050 | 1350
Lubricants/Turbine Oil/Grease/Compounds/Gear oil $ 2000/site/yr |  |  | 2000 | 1500 | 500
Tools & Tool Repair/Replacement |  |  |  | 0 | 0
Mechanical | $ 500/site/yr |  | 500 | 375 | 125
Electrical | $ 250/site/yr |  | 250 | 187.5 | 62.5
Radio Parts and repairs | $ 500/site/yr |  | 500 | 375 | 125
Equipment Rental |  |  |  | 0 | 0
Assorted Equipment | $ 4,000/site/yr |  | 4000 | 3000 | 1000
Professional Specialty Services | $ 17,500/yr |  | 5000 | 3750 | 1250
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
Basis: Based on Caledonia estimate |  | Sub-Total | 31850 | 22137.5 | 9712.5
O&M Annual Fee |  |  |  | 0% | 100%
Basis/Justification: | Raiwind (BC Hydro) (120MW) $3.67/MW | $440M/yr | 160000 | 0 | 160000
| Dabhol (2150 MW) $1.72/MW | $3700M/yr
Use 10% of O&M costs managed | East Java (500 MW)(GE quote) $2.00/MW | $1000M/yr
including Comm. Office and GT | Multan (800 MW) $2.50/MW | $2000M/yr
Scheduled Maint. | Hainan (150 MW) $4.40/MW | $660M/yr
| Guam (88 MW) $6.81/MW | $600M/yr
| Tapal (Wartsila) (126 MW) $1.90/MW (18 mo.) | $240M/yr
|  | Sub-Total | 160000 | 0 | 160000
Operator Overhead Charge (G&A) |  |  |  | 0% | 100%
Basis/Justification: | US, UK and like | 10% |  | 0 | 0
Annual % of Payroll & Burden based | India, Brazil, Argentina and like | 15% | 15%
on country type | Bangladesh and like | 20%
Basis: Eval team concensus |  | Sub-Total | 15% | 0 | 0
Major Equipment Maintenance Program (20 year total) |  |  |  | 20% | 80%
See detailed Schedule |  |  | 11090544 | 2218108.8 | 8872435.2
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  | Sub-Total | 11090544 | 2218108.8 | 8872435.2
Commercial Office Expenses |  |  |  | #DIV/0! | #DIV/0!
Administrative/Technical |  |  |  | 0 | 0
Basis: |  | Sub-Total | 0 | 0 | 0
Sustaining Project Expenses |  |  |  | 75% | 25%
| 10% of procurement items |  | 25552.08 | 19164.06 | 6388.02
|  |  |  | 0 | 0
Basis: Eval team concensus |  | Sub-Total | 25552.08 | 19164.06 | 6388.02
Vehicular Fuel Usage |  |  |  | #DIV/0! | #DIV/0!
3 Trucks:
3 x gal/15 miles x $1.5/gal x 20000 miles/yr |  |  |  | 0 | 0
1 Van & 1 Flat-bed Truck: |  |  |  |  | 0
2 x gal/ 10 miles x $1.5/gal x 20 miles/day x 365 days/year |  |  |  | 0 | 0
2 Forklifts: |  |  |  |  | 0
2 x 2 gal/hr x $1.5/gal x 2 hr/day x 365 days/yr |  |  |  | 0 | 0
1 Crane: |  |  |  |  | 0
5 gal/hr x $1.5/gal x 40 days/yr x 8 hours/day |  |  |  | 0 | 0
1 Crew Boats: |  |  |  |  | 0
20 gal/hr x 1hr/30 miles x 30 miles x 2rd trips/d x365 days/yr x $1.5/gal x 2.0 (idle factor) |  |  |  | 0 | 0
THESE COSTS ARE ALREADY INCLUDED ABOVE IN "OFFICE SUPPLIES/EXPENSES"
Basis: |  | Sub-Total | 0 | 0 | 0

## Cap Spares (hidden)
Rochester Public Utilities LM6000 PC Power Project
Capital & Operational Spares
Assorted Plant Operational Spares for: |  | Total | Lakefield
| Fuel System (Nozzles + Accessories) | 461760 | 310000
| Turbine Control / DCS Panels / Excitation | 168000 | 160000
| Starting System (Torque Converter + Misc) | 40000 | 40000
| CT Operational Spares | 205000 | 180000
| CT Misc. Auxiliary Systems | 75000 | 75000
| CEMS | 15000 | 15000
Total Capital & Operational Spares |  | 964760 | 780000
Freight |  | 9647.6 | 7800
GrandTotal Capital & Operational Spares |  | 974407.6 | 787800

## GE7EA (hidden)
DATE |  | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020
YEAR | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
UNIT 1 GE7000EA | bar: 2004; 2008; 2012; 2016; 2020
OPERATING HOURS |  | 1200 | 2400 | 3600 | 4800 | 6000 | 7200 | 8400 | 9600 | 10800 | 12000 | 13200 | 14400 | 15600 | 16800 | 18000 | 19200 | 20400 | 21600 | 22800 | 24000
STARTS |  | 100 | 200 | 300 | 400 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000
NEW PARTS | [21 empty] | Total
Liners | 1198.8 | [20 empty] | 0
Transition Pieces | 436.852 | [20 empty] | 0
Transition Seals | NA | [20 empty] | 0 | bar: 2012
Fuel Nozzles | 461.76 | 2012: 461.76 | 461.76
Row 1 Blades | 859.0001 | [20 empty] | 0
Row 2 Blades | 850.9108 | [20 empty] | 0
Row 3 Blades | 746.4668 | [20 empty] | 0
Row 1 Nozzles | 848.573 | [20 empty] | 0
Row 2 Nozzles | 874.5008 | [20 empty] | 0
Row 3 Nozzles | 930.725 | [20 empty] | 0
1st Stage Support Ring | 36.5589 | [20 empty] | 0
1st Stage Shroud Blocks | 172.5484 | [20 empty] | 0
2nd & 3rd Stage Shroud Blocks | 200.1662 | [20 empty] | 0
IGV Blades | 798 | [20 empty] | 0
Comp Rotor Blades | 765.4657 | [20 empty] | 0
Comp Diaphrams | 1042 | [20 empty] | 0
Turb/Gen Bearings | NA | [20 empty] | 0
Renewables Comb Insp | 19.882 | 2004: 19.882; 2008: 19.882; 2016: 19.882 | 59.646
Renewables HGP Insp | 12.018 | 2012: 12.018 | 12.018
Renewables Major Insp | 122.319 | [20 empty] | 0
Generator Field | NA | [20 empty] | 0
Generator Stator | NA | [20 empty] | 0
0
Parts Total |  | 0 | 0 | 0 | 19.882 | 0 | 0 | 0 | 19.882 | 0 | 0 | 0 | 473.778 | 0 | 0 | 0 | 19.882 | 0 | 0 | 0 | 0 | 533.424
Repairs Total |  | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 775 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 1315 |  |  | Cost per
Start
Total Maintenance Costs |  | 0 | 0 | 0 | 199.882 | 0 | 0 | 0 | 199.882 | 0 | 0 | 0 | 1248.778 | 0 | 0 | 0 | 199.882 | 0 | 0 | 0 | 0 | 1848.424 |  |  | 770.1767
DATE |  | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020
YEAR | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
UNIT 1 GE7000EA |  | 0 | 0 | 0 | C | 0 | 0 | 0 | C | 0 | 0 | 0 | H | 0 | 0 | 0 | C | 0 | 0 | 0 | C
OPERATING HOURS |  | 1200 | 2400 | 3600 | 4800 | 6000 | 7200 | 8400 | 9600 | 10800 | 12000 | 13200 | 14400 | 15600 | 16800 | 18000 | 19200 | 20400 | 21600 | 22800 | 24000
STARTS |  | 100 | 200 | 300 | 400 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000 | Total
LABOR AND ENGINEERING |  | 2004: 25; 2008: 25; 2012: 100; 2016: 25 | 175
REPAIR COSTS
Liners | 50 | 2004: 50; 2008: 50; 2012: 50; 2016: 50 | 200
Transition Pieces | 30 | 2004: 30; 2008: 30; 2012: 30; 2016: 30 | 120
Transition Seals | NA | [20 empty] | 0
Fuel Nozzles | 75 | 2004: 75; 2008: 75; 2016: 75 | 225
Row 1 Blades | 75 | 2012: 75 | 75
Row 2 Blades | 75 | 2012: 75 | 75
Row 3 Blades | 75 | 2012: 75 | 75
Row 1 Nozzles | 100 | 2012: 100 | 100
Row 2 Nozzles | 75 | 2012: 75 | 75
Row 3 Nozzles | 75 | 2012: 75 | 75
Row 1 Support Ring | 30 | 2012: 30 | 30
1st Stage Shroud Blocks | 30 | 2012: 30 | 30
2nd & 3rd Stage Shroud Blocks | 60 | 2012: 60 | 60
IGV Blades | NA | [20 empty] | 0
Comp Rotor Blades | 40 | [20 empty] | 0
Comp Diaphrams | 40 | [20 empty] | 0
Turb/Gen Bearings | 25 | [20 empty] | 0
Renewables Comb Insp | NA | [20 empty] | 0
Renewables HGP Insp | NA | [20 empty] | 0
Renewables Major Insp | NA | [20 empty] | 0
Generator Field | 75 | [20 empty] | 0
Generator Stator | 50 | [20 empty] | 0
0
REPAIR TOTAL (parts) |  | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 675 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 1140
REPAIR TOTAL (parts &labor) |  | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 775 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 1315
SPARE PARTS ROTATION GE7000EA
YEAR | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024
INSPECTION | [23 empty] | M | bar: 2003; 2007; 2011; 2015; 2019
HOURS | 1500 | 2400 | 3600 | 4800 | 6000 | 7200 | 8400 | 9600 | 10800 | 12000 | 13200 | 14400 | 15600 | 16800 | 18000 | 19200 | 20400 | 21600 | 22800 | 24000 | 0 | 0 | 0 | 0
STARTS | 120 | 200 | 300 | 400 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000 | 0 | 0 | 0 | 0
TRANSITIONS REPAIR 8000hrs, 400 starts REPLACE 48000hrs, 2400 starts
REPAIR | N | [20 empty] | N | N | N | bar: 2001 to 2020
REPLACE | N | [20 empty] | N | N | Y | bar: 2001 to 2020
LINERS REPAIR 8000hrs, 400Starts REPLACE 40,000hrs, 2000starts
REPAIR | N | [20 empty] | N | N | Y | bar: 2001 to 2020
REPLACE | N | [20 empty] | N | N | N | bar: 2001 to 2020
FUEL NOZZLES REPAIR 8000hrs, 400 starts REPLACE 24000 hrs, 1200 starts
REPAIR | N | [20 empty] | N | N | N | bar: 2001 to 2020
REPLACE | N | [20 empty] | N | N | Y | bar: 2001 to 2020
1st, 2nd, 3rd STAGE NOZZLES, 1st STAGE SUPPORT RING REPAIR 24000 hrs, 1200 starts REPLACE 72000hrs, 3600 starts
REPAIR | N | [20 empty] | N | N | Y | bar: 2001 to 2020
REPLACE | N | [20 empty] | N | N | N | bar: 2001 to 2020
2nd & 3rd STAGE BLADES, 2ND & 3RD STAGE SHROUD BLOCKS REPAIR 24000hrs, 1200starts REPLACE 72000hrs, 4800 starts
REPAIR | N | [20 empty] | N | N | Y | bar: 2001 to 2020
REPLACE | N | [20 empty] | N | N | N | bar: 2001 to 2020
COMPRESSOR BLADES & DIAPHRAMS REPAIR 48000hrs, 2400starts REPLACE 120000 hrs, 6000 starts
REPAIR | N | [20 empty] | N | N | Y | bar: 2001 to 2020
REPLACE | N | [20 empty] | N | N | N | bar: 2001 to 2020
1ST STAGE SHROUD BLOCKS REPAIR 24000hrs, 1200starts REPLACE 48000hrs, 2400starts
REPAIR | N | [20 empty] | N | N | N | bar: 2001 to 2020
REPLACE | N | [20 empty] | N | N | Y | bar: 2001 to 2020
1st STAGE BLADES REPAIR 24000hrs, 1200starts REPLACE 48000 hrs, 3600starts
REPAIR | N | [20 empty] | N | N | Y | bar: 2001 to 2020
REPLACE | N | [20 empty] | N | N | N | bar: 2001 to 2020
MAINTENANCE LIFE CYCLE COSTS
GENERAL ELECTRIC 7000EA (DLN)
Part |  | 2001: New Cost; 2002: Replacement Interval; 2005: Repair Cost; 2006: Repair Interval
|  | ($x1000) | (hours) | (starts) |  | ($x1000) | (hours) | (starts)
Liners |  | 2001: 1198.8; 2002: 40000; 2003: 2000; 2005: 50; 2006: 8000; 2007: 400
Transition Pieces |  | 2001: 436.852; 2002: 48000; 2003: 2400; 2005: 30; 2006: 8000; 2007: 400
Transition Seals | bar: 2001 to 2003; 2005 to 2006
Fuel Nozzles |  | 2001: 461.76; 2002: 24000; 2003: 1200; 2005: 75; 2006: 8000; 2007: 400
Row 1 Blades |  | 2001: 859.0001; 2002: 48000; 2003: 3600; 2005: 75; 2006: 24000; 2007: 1200
Row 2 Blades |  | 2001: 850.9108; 2002: 72000; 2003: 4800; 2005: 75; 2006: 24000; 2007: 1200
Row 3 Blades |  | 2001: 746.4668; 2002: 72000; 2003: 4800; 2005: 75; 2006: 24000; 2007: 1200
Row 1 Nozzles |  | 2001: 848.573; 2002: 72000; 2003: 3600; 2005: 100; 2006: 24000; 2007: 1200
Row 2 Nozzles |  | 2001: 874.5008; 2002: 72000; 2003: 3600; 2005: 75; 2006: 24000; 2007: 1200
Row 3 Nozzles |  | 2001: 930.725; 2002: 72000; 2003: 3600; 2005: 75; 2006: 24000; 2007: 1200
Row 1 Support Ring |  | 2001: 36.5589; 2002: 72000; 2003: 3600; 2005: 30; 2006: 24000; 2007: 1200
1st Stage Shroud Blocks |  | 2001: 172.5484; 2002: 48000; 2003: 2400; 2005: 30; 2006: 24000; 2007: 1200
2nd & 3rd Stage Shroud Blocks |  | 2001: 200.1662; 2002: 72000; 2003: 4800; 2005: 60; 2006: 48000; 2007: 1200
IGV Blades |  | 2001: 798; 2002: 96000; 2003: 4800; 2005: NA; 2006: NA
Comp Rotor Blades |  | 2001: 765.4657; 2002: 120000; 2003: 6000; 2005: 40; 2006: 48000; 2007: 2400
Comp Diaphrams |  | 2001: 1042; 2002: 120000; 2003: 6000; 2005: 40; 2006: 48000; 2007: 2400
Turb/Gen Bearings |  | 2001: NA; 2002: NA; 2005: 25; 2006: 48000; 2007: 2400
Renewables Comb Insp |  | 2001: 19.882; 2002: 8000; 2003: 400; 2005: NA; 2006: NA
Renewables HGP Insp |  | 2001: 12.018; 2002: 24000; 2003: 1200; 2005: NA; 2006: NA
Renewables Major Insp |  | 2001: 122.319; 2002: 48000; 2003: 2400; 2005: NA; 2006: NA
Generator Field |  | 2001: NA; 2002: NA; 2005: 75; 2006: 48000; 2007: 2400
Generator Stator |  | 2001: NA; 2002: NA; 2005: 50; 2006: 48000; 2007: 2400
LABOR/ENGINEERING
Combustion inspection |  | 2005: 25; 2006: 8000; 2007: 400
Hot gas path inspection |  | 2005: 100; 2006: 24000; 2007: 1200
Major inspection |  | 2005: 175; 2006: 48000; 2007: 2400
Assumes all inspection labor will be by plant staff except for OEM TD