## Summary
Sun Devil Pipeline Project
San Juan to Phoenix
San Juan and Mainline Expansions
Executive Summary
Conclusion
Several scenarios were reviewed with input from various groups. The following selections were
considered the best two options (Case VI. A. & B.) by Facility Planning. Other scenarios are in the
cases attached. All studies assumed base loading with no swings and one other customer attached
which is Big Sandy. Also the assumption is made that Sun Devil is flowing at 400 MMcf/d. Total
capacity is reduced if Sun Devil is at 0 MMcf/d.
| VI. A. | San Juan to Phoenix - Compression and 30" Loop, No MAOP Increase
The total project costs is approximately $597,000,000 which would include expansion of the San
Juan lateral with about 97 miles of 36" pipe, expansion of the Blanco Hub facilities, Bloomfield
compressor add and mods, two mainline mid-point stations, and mods to the Gallup CS. The
mainline will have approximately 129 miles of 30" pipe, and Station #4 is assumed completed with
the Red Rock expansion. The Sun Devil pipeline would start at the discharge of Station #2 and
basically follow major highways. The pipeline is approximately 160 miles of 30" pipe with no
compression. The San Juan analysis included about 65 MMcf/d of total fuel which should be
enough to handle total fuel requirements. The San Juan lateral expansion is 670 MMcf/d of which
160 MMcf/d must go east. Total flow west is 1750 MMcf/d which includes 400 MMcf/d to Sun Devil,
90 MMcf/d to Big Sandy and 20 MMcf/d west of the California border.
System Impacts
Adds a little more line pack to handle potential future swings with power plant loads. Additional
compression and less pipe loop reduces the initial project costs. Additional future loops would
be cost effective for the next expansions.
| VI. B. | San Juan to Phoenix - Compression and 30" Loop, MAOP Increase
This total project costs is approximately $507,000,000 which would include expansion of the San
Juan lateral with about 97 miles of 36" pipe, expansion of the Blanco Hub facilities, Bloomfield
compressor add and mods, one mainline mid-point station, and mods to the Gallup CS. The
mainline will have approximately 78 miles of 30" pipe, and Station #4 is assumed completed with
the Red Rock expansion. The Sun Devil pipeline would start at the discharge of Station #2 and
basically follow major highways. The pipeline is approximately 160 miles of 30" pipe with no
compression. The San Juan analysis included about 65 MMcf/d of total fuel which should be
enough to handle total fuel requirements. The San Juan lateral expansion is 670 MMcf/d of which
190 MMcf/d must go east. Total flow west is 1830 MMcf/d which includes 400 MMcf/d to Sun
Devil, 90 MMcf/d to Big Sandy and 100 MMcf/d west of the California border.
System Impacts
Adds a little more line pack to handle potential future swings with power plant loads. Additional
compression and less pipe loop reduces the initial project costs. Additional O&M expenses with
the added compression will be reviewed by the Financial group. Future loops should increase
flows west without new compression.

## Station #2 Discharge (3)
Sun Devil Project
San Juan to Phoenix
400 MMcf/d Expansion
Estimated Costs of Facilities
CASE VI. | A. | 30" MAINLINE LOOP,AND HP
NO MAOP UPGRADE
SUN DEVIL FROM STATION #2 DISCHARGE
510 MMCF/D EXPANSION (1750 MMCF/D TOTAL)
From |  | To |  | Miles |  | Size (") |  | Est. Costs
BLFD CS |  | SJCT |  | 96.83 |  | 36 | " | 126886032
|  | Bloomfield Hp (7000 Hp) | [5 empty] | 13000000
|  | Bloomfield Mods | [5 empty] | 1000000
|  | Blanco Hub Mods | [5 empty] | 2000000
|  | Bisti CS Mods | [5 empty] | 1000000
|  | Gallup CS Mods | [5 empty] | 5000000
|  |  | Total San Juan Expansion | 96.83 |  |  |  | 148886032
SJCT | - | Sta. #4 |  | 43.9 |  | 30 | " | 47938800
Sta. #4 | - | Sta. #3 |  | 41.2 |  | 30 | " | 44990400
Sta. #3 | - | Sta. #2 |  | 13.434 |  | 30 | " | 14669928
Sta. #2 |  | Sta. #1 |  | 0 |  | 30 | " | 0
Sta. #1 |  | Needles |  | 30 |  | 30 | " | 32760000
|  | CS35 (15,000 Hp) | [5 empty] | 14000000
|  | CS25 (25,000 Hp) | [5 empty] | 19000000
|  |  | Total Mainline Expansion | 128.534 |  |  |  | 173359128
Sta. #2 | - | I40 |  | 3 |  | 30 | " | 3276000
I40 | - | I17 |  | 12.5 |  | 30 | " | 13650000
I17 | - | Phoenix |  | 144.1 |  | 30 | " | 157357200
|  |  | Total Sun Devil Pipeline | 159.6 |  |  |  | 174283200
|  |  | Total Project | 384.964 |  |  |  | 496528360
Sun Devil Project
San Juan to Phoenix
400 MMcf/d Expansion
Estimated Costs of Facilities
CASE VI. | B. | 30" MAINLINE LOOP,HP, AND MAOP UPGRADE
MAOP UPGRADE TO 1120 PSIG
SUN DEVIL FROM STATION #2 DISCHARGE
590 MMCF/D EXPANSION (1830 MMCF/D TOTAL)
From |  | To |  | Miles |  | Size (") |  | Est. Costs
From |  | To |  | Miles |  | Size (") |  | Est. Costs
BLFD CS |  | SJCT |  | 96.83 |  | 36 | " | 126886032
|  | Bloomfield Hp (7000 Hp) | [5 empty] | 13000000
|  | Bloomfield Mods | [5 empty] | 1000000
|  | Blanco Hub Mods | [5 empty] | 2000000
|  | Bisti CS Mods | [5 empty] | 1000000
|  | Gallup CS Mods | [5 empty] | 5000000
|  |  | Total San Juan Expansion | 96.83 |  |  |  | 148886032
SJCT | - | Sta. #4 |  | 16.5 |  | 30 | " | 18018000
Sta. #4 | - | Sta. #3 |  | 31.1 |  | 30 | " | 33961200
Sta. #3 | - | Sta. #2 |  | 20.644 |  | 30 | " | 22543248
Sta. #2 |  | Sta. #1 |  | 0 |  | 30 | " | 0
Sta. #1 |  | Needles |  | 10.2 |  | 30 | " | 11138400
|  | CS4 (25,000 Hp) | [5 empty] | 19000000
|  | CS35 (30,000 Hp) | [5 empty] | 20000000
|  | CS3 (28,000 Hp) | [5 empty] | 20000000
|  | CS2 (25,000 Hp) | [5 empty] | 19000000
|  | CS1 (27,500 Hp) | [5 empty] | 20000000
|  |  | Total Mainline Expansion | 78.444 |  |  |  | 183660848
Sta. #2 | - | I40 |  | 3 |  | 30 | " | 3276000
I40 | - | I17 |  | 12.5 |  | 30 | " | 13650000
I17 | - | Phoenix |  | 144.1 |  | 30 | " | 157357200
|  |  | Total Sun Devil Pipeline | 159.6 |  |  |  | 174283200
|  |  | Total Project | 334.874 |  |  |  | 506830080

## Fuel Summary
SUN DEVIL PROJECT
RED ROCK EXPANSION BASE
Fuel req'd
Station | HP (ISO) | HP (site) | HP (req'd) | MMcf/d
Sta. #4 | 41500 | 25000 | 18285 | 3.2
Sta. #3 | 41500 | 28000 | 20926 | 3.7
Sta. #2 | 41500 | 25000 | 21441 | 3.8
Sta. #1 | 41500 | 27500 | 21203 | 3.7
| TOTAL |  | 81855 | 14.4
SUN DEVIL FUEL CHANGES
|  |  | CASE VI. A. |  | CASE VI. B.
|  |  | No MAOP Increase |  | MAOP Increase
|  |  | 30" Loop and Hp |  | 30" Loop and Hp
|  |  |  | Fuel req'd |  | Fuel req'd
Station | HP (ISO) | HP (site) | HP (req'd) | MMcf/d | HP (req'd) | MMcf/d
Sta. #4 | 41500 | 25000 | 25000 | 4.375 | 50000 | 8.75
Sat. #35 | 0 | 0 | 15000 | 2.625 | 30000 | 5.25
Sta. #3 | 41500 | 28000 | 28000 | 4.9 | 51900 | 9.077
Sta. #25 | 0 | 0 | 25000 | 5 | 0 | 0
Sta. #2 | 41500 | 25000 | 25000 | 4.375 | 50000 | 8.75
Sta. #1 | 41500 | 27500 | 27500 | 4.813 | 31690 | 5.544
Bloomfield U #5 | 13000 | 8200 | 7000 | 1.54 | 7000 | 1.54
| TOTAL |  | 152500 | 27.628 | 220590 | 38.911
| NOTE: | 1. Stations #1 - #4 have doubled in size. Identical units installed in parallel.
2. New unit at Bloomfield goes on the low side. Low side unit moved to the
high side with a new compressor the same as the other turbine units.