## Hp Sizing
Sun Devil Compressor Operating Points ( Rev 1 ) 01/07/02
[19 empty] | Generic | MFGR
Station |  | SG | Isentr | amb | Ps | Pd | Ts | Compress | Ratio | H | Q | Q | Q | Q | Compr | TRV | Td | Mech | BHp | BHp |  | BHp | BHp | Data
& | Elev |  | Exp | °F | (Psig) | (Psig) | °F | ability |  | (feet) | (MMSCFD) | (ACFM) | (MMSCFD) | (ACFM) | Efficny |  | * | Effcy | Req'd | Req'd | RPM | Avail | Margin | Date
Unit | Feet | [9 empty] | Station | Station | New Unit | New Unit | Adiab |  | °F |  | New Unit | Mfgr |  | New Unit | New Unit
BLOOMFIELD | 5580 | 0.595 | 1.29 | 95 | 850 | 1050 | 85 | 0.89662 | 1.2313 | 9338.7571 | 525 | 5836.0545 | 525 | 5836.0545 | 0.83 | 1.3852 | 117.4593 | 0.96 | 5731.6532 |  | 8500 | 10339.0475 | 4607.3943 |  | Mars 100-15000 Hp 122°F Match
|  | 0.595 | 1.29 | 95 | 870 | 1091 | 90 | 0.89769 | 1.2498 | 10129.4761 | 551 | 6048.7974 | 551 | 6048.7974 | 0.83 | 1.3852 | 125.1797 | 0.96 | 6524.8436 |  | 8500 | 10339.0475 | 3814.2039 |  | Mars 100-15000 Hp 122°F Match
|  | 0.595 | 1.29 | 95 | 900 | 1195 | 95 | 0.89776 | 1.3225 | 12897.0576 | 575 | 6161.1975 | 575 | 6161.1975 | 0.83 | 1.3852 | 139.8571 | 0.96 | 8669.4193 |  | 8500 | 10339.0475 | 1669.6282 |  | Mars 100-15000 Hp 122°F Match
[8 empty] | 1 | 1
BISTI | 5798 | 0.595 | 1.29 | 95 | 970 | 1090 | 85 | 0.88372 | 1.1219 | 5033.7757 | 1590 | 15297.7554 | 1590 | 15297.7554 | 0.83 | 1.3852 | 102.7071 | 0.96 | 9356.6958 | @Motor Shaft | 0 | 0 |  |  | Rebundle
STANDING ROCK | 6250 | 0.595 | 1.29 | 95 | 976 | 976 | 82 | 0.88089 | 1 | 0 | 0 | 0 | 0 | 0 | 0.83 | 1.3852 | 82 | 0.98 | #DIV/0! |  | 8500 | 10076.3512 | #DIV/0! |  | Mars 100-15000 Hp 122°F Match
|  | 0.595 | 1.29 | 95 | 976 | 976 | 85 | 0.88308 | 1 | 0 | 0 | 0 | 0 | 0 | 0.83 | 1.3852 | 85 | 0.98 | #DIV/0! |  | 8500 | 10076.3512 | #DIV/0! |  | Mars 100-15000 Hp 122°F Match
|  | 0.595 | 1.29 | 95 | 976 | 976 | 88 | 0.88523 | 1 | 0 | 0 | 0 | 0 | 0 | 0.83 | 1.3852 | 88 | 0.98 | #DIV/0! |  | 8500 | 10076.3512 | #DIV/0! |  | Mars 100-15000 Hp 122°F Match
GALLUP | 6600 | 0.595 | 1.29 | 95 | 863 | 970 | 82 | 0.8932 | 1.1219 | 5061.569 | 1590 | 17251.3594 | 1590 | 17251.3594 | 0.83 | 1.3852 | 99.6158 | 0.96 | 9408.3575 | 5012 | 0 |  |  |  | New Comp
|  | 0.595 | 1.29 | 95 | 863 | 970 | 0 | 0.81704 | 1.1219 | 3929.5099 | 0 | 0 | 0 | 0 | 0.83 | 1.3852 | 14.9507 | 0.96 | 0 | 5347 | 0 |  |  |  | New Comp
|  | 0.595 | 1.29 | 95 | 863 | 970 | 82 | 0.8932 | 1.1219 | 5061.569 | 1590 | 17251.3594 | 1590 | 17251.3594 | 0.83 | 1.3852 | 99.6158 | 0.96 | 9408.3575 | 5836 | 0 |  |  |  | New Comp - LOW HEAD- HI Hp….LIKELY PROB W/ MOTOR CAPABILITY
CS#4 | 7300 | 0.595 | 1.29 | 95 | 830 | 1000 | 78 | 0.89422 | 1.2012 | 8080.0779 | 1762 | 19740.1288 | 1762 | 19740.1288 | 0.83 | 1.3852 | 106.141 | 0.98 | 16304.1489 | 5239 | 6100 | 28111.2534 | 11807.1045 |  | TurnDown? / New Bundle
CS#2 | 7450 | 0.595 | 1.29 | 95 | 820 | 1004 | 82 | 0.89798 | 1.2204 | 8896.6747 | 1747 | 20037.8521 | 1747 | 20037.8521 | 0.83 | 1.3852 | 112.8683 | 0.98 | 17799.0694 | 10742 | 6100 | 28111.2534 | 10312.184 |  | New Bundle
CS#1 | 5049 | 0.595 | 1.29 | 95 | 672 | 1005 | 85 | 0.91646 | 1.4849 | 18528.3962 | 1243 | 17784.0723 | 1243 | 17784.0723 | 0.83 | 1.3852 | 148.3291 | 0.98 | 26374.5852 | 11586 | 6100 | 30758.3343 | 4383.7491 |  | New Bundle
CS#3 | 4768 | 0.595 | 1.29 | 95 | 775 | 1004 | 85 | 0.90487 | 1.29 | 11594.9451 | 1758 | 21595.3679 | 1758 | 21595.3679 | 0.83 | 1.3852 | 124.9842 | 0.98 | 23343.4073 |  | 6100 | 31131.1626 | 7787.7553 |  | New Bundle
CS#1.5 | 5120 | 0.595 | 1.29 | 95 | 901 | 901 | 75 | 0.88402 | 1 | 0 | 0 | 0 | 0 | 0 | 0.83 | 1.3852 | 75 | 0.98 | #DIV/0! | 5365 | 6100 | 30758.3343 | #DIV/0! |  | New Bundle
|  | 0.595 | 1.29 | 95 | 901 | 901 | 92 | 0.89574 | 1 | 0 | 0 | 0 | 0 | 0 | 0.83 | 1.3852 | 92 | 0.98 | #DIV/0! | 5369 | 6100 | 30758.3343 | #DIV/0! |  | New Bundle
|  | 0.595 | 1.29 | 95 | 901 | 901 | 95 | 0.89766 | 1 | 0 | 0 | 0 | 0 | 0 | 0.83 | 1.3852 | 95 | 0.98 | #DIV/0! | 5386 | 6100 | 30758.3343 | #DIV/0! |  | New Bundle
KINGMAN | 2610 | 0.595 | 1.29 | 95 | 895 | 895 | 85 | 0.89174 | 1 | 0 | 0 | 0 | 0 | 0 | 0.83 | 1.3852 | 85 | 0.98 | #DIV/0! | 5235 | 6100 | 33927.3748 | #DIV/0! |  | New Bundle
|  | 0.595 | 1.29 | 95 | 895 | 895 | 92 | 0.89636 | 1 | 0 | 0 | 0 | 0 | 0 | 0.83 | 1.3852 | 92 | 0.98 | #DIV/0! | 5326 | 6100 | 33927.3748 | #DIV/0! |  | New Bundle
|  | 0.595 | 1.29 | 95 | 895 | 895 | 98 | 0.90014 | 1 | 0 | 0 | 0 | 0 | 0 | 0.83 | 1.3852 | 98 | 0.98 | #DIV/0! | 5316 | 6100 | 33927.3748 | #DIV/0! |  | New Bundle
*Note: When sizing gas coolers add 5°F to the shown gas discharge temp to account for any recycle and possible efficiency issues

## Header & Unit Sizing
| Station | Unit
BLOOMFIELD | 30 | 24
BISTI | 36 | 36
STANDING ROCK | 36 | 36
GALLUP | 36 | 36
CS#4 | GT 38" | GT 38"
CS#2 | GT 40" | GT 40"
CS#1 | GT 38" | GT 38"
CS#3 | GT 38" | GT 38"
CS#1.5 | GT 38" | GT 38"
KINGMAN | 36" | 36"