## LIQ SAMPLES GS
DATE | TIME | FACILITY | SAMPLE ID | SAMPLE LOCATION | MATRIX | RESULT | UNITS | COMMENTS
1999-06-26 |  | GOLDEN SHORES | SLX-001D | PIG RECEIVER | SOLIDS | <1.00 | UG/G | PIPELINE RUST
1999-06-26 |  | GOLDEN SHORES | SLX-002 | PIG RECEIVER | SOLIDS | 1.4 | UG/G | PIPELINE SOLIDS
1999-06-26 |  | GOLDEN SHORES | SLX-003 | PIPELINE LIQUIDS TANK | WATER | 6.5 | UG/L
1999-06-26 |  | GOLDEN SHORES | SLX-004W | PIG RECEIVER | WATER | 75.6 | UG/L | SAME RUN AS SLX-003
1999-06-26 |  | GOLDEN SHORES | SLX-004S | PIG RECEIVER | SOLIDS | 4.66 | UG.G | SAME RUN AS SLX-003
1999-06-27 | 08:00 | GOLDEN SHORES | SLX-005 | PIPELINE LIQUIDS TANK | WATER | 7.7 | UG/L | 2,572 GAL. H20 COLLECT INTO TANK
1999-06-27 | 13:10 | GOLDEN SHORES | SLX-006 | PIPELINE LIQUIDS TANK | DIESEL | <8.00 | UG/G | 850 GALLONS H2O COLLECTED INTO TANK
1999-06-27 | 19:10 | GOLDEN SHORES | SLX-007W | PIPELINE LIQUIDS TANK | WATER | 28 | UG/L | 0 GAL. H2O COLLECTED INTO TANK
1999-06-27 | 19:10 | GOLDEN SHORES | SLX-007O | PIPELINE LIQUIDS TANK | DIESEL | 2.1 | UG/G | 0 GAL. H2O COLLECTED INTO TANK
1999-06-28 | 7:05 | GOLDEN SHORES | SLX-010 | PIPELINE LIQUIDS TANK | DIESEL | 1.3 | UG/G | 1324 GAL. DIESEL COLLECTED INTO TANK
1999-06-28 | 16:18 | GOLDEN SHORES | SLX-018 | PIPELINE LIQUIDS TANK | DIESEL | 1.6 | UG/G | 200 GAL. DIESEL COLLECTED INTO TANK
1999-06-28 | 18:20 | GOLDEN SHORES | SLX-019 | PIPELINE LIQUIDS TANK | DIESEL | 1.7 | UG/G
1999-06-29 | 8:00 | GOLDEN SHORES | SLX-020 | PIPELINE LIQUIDS TANK | DIESEL | 0.59 | UG/G | 300 GAL. DIESEL COLLECTED INTO TANK
1999-06-29 | 10:15 | GOLDEN SHORES | SLX-026 | PIPELINE LIQUIDS TANK | DIESEL | 1.3 | UG/G | 306 GAL. DIESEL COLLECTED INTO TANK
1999-06-29 | 14:10 | GOLDEN SHORES | SLX-027 | PIPELINE LIQUIDS TANK | DIESEL | <0.30 | UG/G | 991 GAL. DIESEL COLLECTED INTO TANK
1999-06-29 | 17:01 | GOLDEN SHORES | SLX-033 | PIPELINE LIQUIDS TANK | DIESEL | <0.32 | UG/G | 490 GAL. DIESEL COLLECTED INTO TANK
1999-06-29 | 18:43 | GOLDEN SHORES | SLX-034S | PIPELINE LIQUIDS TANK | SLUDGE | <0.32 | UG/G | SLUDGE FROM SAMPLE SLX-033
1999-06-30 | 7:15 | GOLDEN SHORES | SLX-035 | PIPELINE LIQUIDS TANK | DIESEL | <0.34 | UG/G | 100 GAL. DIESEL COLLECTED INTO TANK
1999-06-30 | 9:35 | GOLDEN SHORES | SLX-036 | PIPELINE LIQUIDS TANK | DIESEL | <0.33 | UG/G | 633 GAL. DIESEL COLLECTED INTO TANK
1999-06-30 | 12:30 | GOLDEN SHORES | SLX-037 | PIPELINE LIQUIDS TANK | DIESEL | <0.30 | UG/G | 20 GAL. DIESEL COLLECTED INTO TANK
1999-06-30 | 17:10 | GOLDEN SHORES | SLX-038 | PIPELINE LIQUIDS TANK | DIESEL | <0.32 | UG/G | 490 GAL. DIESEL COLLECTED INTO TANK
1999-06-30 | 18:30 | GOLDEN SHORES | SLX-044 | PIPELINE LIQUIDS TANK | DIESEL | <0.32 | UG/G | 195 GAL. DIESEL COLLECTED INTO TANK
1999-06-30 | 22:00 | GOLDEN SHORES | SLX-045 | PIPELINE LIQUIDS TANK | DIESEL | <0.33 | UG/G | 430 GAL. DIESEL COLLECTED INTO TANK

## WIPE SAMPLES GS
DATE | TIME | FACILITY | SAMPLE ID | SAMPLE LOCATION | MATRIX | RESULT | UNITS | COMMENTS
1999-06-28 | 5:30 | GOLDEN SHORES | SLX-008W | L-SHAPED PIPE PUP | WIPE | < 3.00 | UG/WIPE | SAMPLE TAKEN FROM 9'X24" PIPE
1999-06-28 | 5:40 | GOLDEN SHORES | SLX-009W | 24" PIPE PUP | WIPE | 5 | UG/WIPE | REMOVED FROM FILTER SEPARATOR
1999-06-28 | 7:35 | GOLDEN SHORES | SLX-011W | FILTER SEP. MANIFOLD | WIPE | 13.3 | UG/WIPE | NOT 100 SQ. CM.
1999-06-28 | 8:05 | GOLDEN SHORES | SLX-012W | INSIDE DOOR OF TOWER | WIPE | 9.6 | UG/WIPE | NOT 100 SQ. CM.
1999-06-28 | 8:05 | GOLDEN SHORES | SLX-013W | INSIDE DOOR OF TOWER | WIPE | 9.2 | UG/WIPE | NOT 100 SQ. CM.
1999-06-28 |  | GOLDEN SHORES | SLX-017W | LIQUID COLL. ON RAG | WIPE | <1.00 | UG/WIPE | 882 GAL. DIESEL COLLECTED INTO TANK
1999-06-30 | 16:45 | GOLDEN SHORES | SLX-042W | FILTER SEPARATOR | WIPE | <1.00 | UG/WIPE | PGE FILTER SEP. WHICH WAS MOVED
1999-06-30 | 16:55 | GOLDEN SHORES | SLX-043W | FILTER SEPARATOR | WIPE | 2.3 | UG/WIPE | EAST SIDEWALL OF NEW PGE FILTER SEP.

## WIPE SAMPLES MS
DATE | TIME | FACILITY | SAMPLE ID | SAMPLE LOCATION | MATRIX | RESULT | UNITS | COMMENTS
1999-06-28 | 11:00 | PG&E MEAS. STA. | PGEMS-014W | METER RUN # 1 | WIPE | 140 | UG/WIPE | NOT 100 CM SQ. WIPE
1999-06-28 | 11:00 | PG&E MEAS. STA. | PGEMS-015W | METER RUN # 2 | WIPE | 110 | UG/WIPE | NOT 100 CM SQ. WIPE
1999-06-28 | 11:05 | PG&E MEAS. STA. | PGEMS-016W | METER RUN # 3 | WIPE | 17 | UG/WIPE | NOT 100 CM SQ. WIPE
1999-06-29 | 10:33 | PG&E MEAS. STA. | PGEMS-021W | # 1 REGULATOR | WIPE | 62 | UG/WIPE | NOT 100 CM SQ. WIPE
1999-06-29 | 10:35 | PG&E MEAS. STA. | PGEMS-022W | 24" PIPE FROM SEP. | WIPE | < 3.00 | UG/WIPE | 100 CM SQ. WIPE
1999-06-29 |  | PG&E MEAS. STA. | PGEMS-023W | INLET TO STATION 24" | WIPE | 1.2 | UG/WIPE | 100 CM SQ. WIPE
1999-06-29 |  | PG&E MEAS. STA. | PGEMS-024W | UPSTREAM HEADER 24" | WIPE | 2.7 | UG/WIPE | 100 CM SQ. WIPE
1999-06-29 |  | PG&E MEAS. STA. | PGEMS-025W | SOCAL INLET HEADER | WIPE | 1.5 | UG/WIPE | 100 CM SQ. WIPE
1999-06-29 |  | PG&E MEAS. STA. | PGEMS-027W | CHECK VALVE | WIPE | 57 | UG/WIPE | NOT 100 CM SQ. WIPE
1999-06-29 |  | PG&E MEAS. STA. | PGEMS-028W | OUTLET DOWN HEADER | WIPE | < 3.00 | UG/WIPE | NOT 100 CM SQ. WIPE
1999-06-29 |  | PG&E MEAS. STA. | PGEMS-029W | PGE-TW METER RUN | WIPE | 9.3 | UG/WIPE | NOT 100 CM SQ. WIPE
1999-06-29 |  | PG&E MEAS. STA. | PGEMS-030W | OUTLET HEADER REG. | WIPE | < 10.00 | UG/WIPE | NOT 100 CM SQ. WIPE
1999-06-29 |  | PG&E MEAS. STA. | PGEMS-034W | BLOWDOWN C/S YARD | WIPE | 5.3 | UG/WIPE | NOT 100 CM SQ. WIPE
1999-06-30 |  | PG&E MEAS. STA. | PGEMS-039W | PGE INLET HEADER | WIPE | 5.5 | UG/WIPE | NOT 100 CM SQ. WIPE
1999-06-30 |  | PG&E MEAS. STA. | PGEMS-040W | REGULATOR HEADER |  | <5.00 | UG/WIPE | NOT 100 CM SQ WIPE
1999-06-30 |  | PG&E MEAS. STA. | PGEMS-041W | PGE OUTLET HEADER | WIPE | <7.00 | UG/WIPE | NOT 100 CM SQ WIPE

## LIQ SAMPLES MS
DATE | TIME | FACILITY | SAMPLE ID | SAMPLE LOCATION | MATRIX | RESULT | UNITS | COMMENTS
1999-06-30 | 14:00 | PG&E MEAS. STA. | PGEMS-037L | DOWNSTREAM HEADER | RINSE WATER | 129 | UG/L | FINAL CLEANING RINSE
1999-06-30 | 14:10 | PG&E MEAS. STA. | PGEMS-038L | PIPELINE LIQUIDS TANK | DETERGENT | <8.00 | UG/L | COMPOSITE OF TANK LIQUIDS

## PIGGING INFORMATION
|  | FACILITY | FACILITY |  | VOLUME | VOLUME
DATE | TIME | INJECTION POINT | RECOVERY POINT | PIPELINE SOLVENT | INJECTED (GAL) | RECOVERED (GAL)
1999-06-26 | 5:20 | PG&E M/S | GOLDEN SHORES | WATER | 500 | 0
1999-06-26 |  | PG&E M/S | GOLDEN SHORES | WATER | 1000 | <1
1999-06-26 |  | PG&E M/S | GOLDEN SHORES | WATER | 1000 | 1102
[5 empty] | 2500 | 1102
1999-06-27 | 5:00 | PG&E M/S | GOLDEN SHORES | WATER | 2500 | 2572
1999-06-27 | 11:15 | PG&E M/S | GOLDEN SHORES | WATER | 1000 | 850
1999-06-27 | 14:30 | PG&E M/S | GOLDEN SHORES | DRY | 0 | 0
1999-06-27 | 16:45 | PG&E M/S | GOLDEN SHORES | DIESEL | 1000 | 0
[5 empty] | 4500 | 3422
1999-06-28 | 5:15 | PG&E M/S | GOLDEN SHORES | DIESEL | 1000 | 1324
1999-06-28 | 13:30 | PG&E M/S | GOLDEN SHORES | DIESEL | 1000 | 200
1999-06-28 | 16:28 | PG&E M/S | GOLDEN SHORES | DIESEL | 1000 | 2041
[5 empty] | 3000 | 3565
1999-06-29 | 5:30 | PG&E M/S | GOLDEN SHORES | DIESEL | 1000 | 300
1999-06-29 | 8:30 | PG&E M/S | GOLDEN SHORES | DRY | 0 | 306
1999-06-29 |  | PG&E M/S | GOLDEN SHORES | DRY | 0 | 0
1999-06-29 | 15:00 | PG&E M/S | GOLDEN SHORES | DIESEL | 1000 | 991
1999-06-29 | 17:01 | PG&E M/S | GOLDEN SHORES | DIESEL | 1000 | 490
[5 empty] | 3000 | 2087
1999-06-30 | 7:15 | PG&E M/S | GOLDEN SHORES | DRY | 0 | 100
1999-06-30 | 9:35 | PG&E M/S | GOLDEN SHORES | DRY | 0 | 663
1999-06-30 | 12:30 | PG&E M/S | GOLDEN SHORES | DRY | 0 | 20
1999-06-30 | 13:50 | PG&E M/S | GOLDEN SHORES | DIESEL | 1500 | 490
1999-06-30 | 18:30 | PG&E M/S | GOLDEN SHORES | DRY | 0 | 195
1999-06-30 | 22:00 | PG&E M/S | GOLDEN SHORES | DRY | 0 | 430
1999-06-30 |  | GOLDEN SHORES | PG&E M/S | DRY | 0 | 7
[5 empty] | 1500 | 1905
|  |  |  | TOTALS | 14,500 GALLONS | 12,081 GALLONS

## VECTOR WIPE SAMPLES (1)
DATE | TIME | FACILITY | SAMPLE ID | SAMPLE LOCATION | MATRIX | RESULT | UNITS | COMMENTS
1999-06-29 | 13:30 | PG&E M/S | TWN-001 | METER RUN #1 NORTH END | WIPE | <1.0 | UG/WIPE | 100 CM SQ WIPE TEST
1999-06-29 | 13:31 | PG&E M/S | TWN-002 | METER RUN #1 SOUTH END | WIPE | <1.0 | UG/WIPE | 100 CM SQ WIPE TEST
1999-06-29 | 13:32 | PG&E M/S | TWN-003 | METER RUN #2 NORTH END | WIPE | <1.0 | UG/WIPE | 100 CM SQ WIPE TEST
1999-06-29 | 13:33 | PG&E M/S | TWN-004 | METER RUN #2 SOUTH END | WIPE | <1.0 | UG/WIPE | 100 CM SQ WIPE TEST
1999-06-29 | 13:34 | PG&E M/S | TWN-005 | METER RUN #3 NORTH END | WIPE | <1.0 | UG/WIPE | 100 CM SQ WIPE TEST
1999-06-29 | 13:35 | PG&E M/S | TWN-006 | METER RUN #3 SOUTH END | WIPE | <1.0 | UG/WIPE | 100 CM SQ WIPE TEST
1999-06-29 | 16:00 | PG&E M/S | TWN-007 | REGULATOR RUN #1 NORTH | WIPE | <3.0 | UG/WIPE | 100 CM SQ WIPE TEST
1999-06-29 | 16:00 | PG&E M/S | TWN-008 | REGULATOR RUN #1 SOUTH | WIPE | <3.0 | UG/WIPE | 100 CM SQ WIPE TEST
1999-06-29 | 16:00 | PG&E M/S | TWN-009 | REGULATOR RUN #2 NORTH | WIPE | 3.7 | UG/WIPE | 100 CM SQ WIPE TEST
1999-06-29 | 16:00 | PG&E M/S | TWN-010 | REGULATOR RUN #2 SOUTH | WIPE | <3.0 | UG/WIPE | 100 CM SQ WIPE TEST
1999-06-30 | 12:05 | GOLDEN SHORES | TWN-011 | RELOCATED SEPARATOR | WIPE | <1.0 | UG/WIPE | 100 CM SQ WIPE TEST. MOVED TO GOLDEN SHORES
1999-06-30 | 12:10 | GOLDEN SHORES | TWN-012 | RELOCATED SEPARATOR | WIPE | <1.0 | UG/WIPE | 100 CM SQ WIPE TEST. MOVED TO GOLDEN SHORES
1999-06-30 | 11:45 | PURCHASE DIESEL | TWN-013 | DIESEL | DIESEL | <1.0 | UG/G | FOR AROCLOR 1016
1999-06-30 | 11:45 | PURCHASE DIESEL | TWN-013 | DIESEL | DIESEL | 2.1 | UG/G | FOR AROCLOR 1254 ESTIIMATED