## Sheet1
station ID | station name | audit finding | action | date found | date resolved
009780-01,02 | Rio Puerco | 1) oily orifice plates | condition is better; just a very thin film 9/25/01 | ongoing | open
|  | 4) 6 valves could leak and pass unmetered gas | schedule down time and check (maybe in Oct/Nov) | 2001-08-07 | open
009702-01,02 | WMS Milagro | 3) possibility of bypass vlvs leaking | will blind off; scheduled for mid October | 2001-07-10 | open
010160-01,02 | Amoco LaPlata | 1) Daniel 2500 orifice; using upstream static; calc wrong | notify Cessac to chk program software for error | 2001-08-01 | open
19080 | Conoco Maljamar | 1) oily liquid causing orifice plate issues as well as gas | Conoco will install coalescing filter/scrubber | ongoing | open
|  | sampling problems | scheduled for mid Nov.
47044 | EOG Pronghorn | 1) dripping glycol on orifice plate | EOG to install scrubber | ongoing | open
91940/91941 | Atoka 2 chk sta | 1) dirty/oily plate problems | Eng. To review problem and make suggestions | ongoing | open
|  | 2) pulsation issues at meter tube | work order submitted; no response | ongoing | open
000010-01-12 | Needles Station | 1) oily plates all tubes | filters changed on 9/19/01; have not chked plates since | ongoing | open
|  | 2) run-switching valves, 4,5,6, all leak when closed | team/advisor will discuss/resolve | ongoing | open
009216 - 1,2,3 | PGE Topock | pos-shut-in-valves leak (dwn stream of regs) | team/advisor will discuss; next time down will grease/chk | ongoing | open
when station down, both leak mucho gas
094039-01 | El Paso Blanco | oily orifice plates - minimal SRE | San Juan - oil will go away when 010162 oil clears up | ongoing | open
094039-02 | El Paso Blanco | Ditto | Ditto | ongoing | open
094039-03 | El Paso Blanco | Ditto | Ditto | ongoing | open
010162-01 | WFS Lamaquina | oily plates | San Juan Team / continue to work w/ WFS/ marketing | ongoing | open
010162-02 | WFS Lamaquina | oily plates | Ditto | ongoing | open