## Notes
NOTES
1 | The model shows only an example of the economics for a LM6000 project. Please modify the model for the specific transaction
you are trying to model (Please see the contact list below)
2 | Please double check the model/pages before sending out to clients as certain information/comment cells/notes etc. may be too detailed to be disclosed
3 | All yellow shaded cells are required input cells
4 | Turbine carrying cost are based on assumptions on the WestLB Structure, the numbers may change after 03/15/00
5 | The dispatch template is attached. Please check with Jim Simpson for the required inputs
SOURCES
Source
1 | Federal Tax, Franchise Tax, Sales & Used Tax, NOL |  |  | Patrick Maloy
calculations
2 | 15 year MACRS |  |  | Patrick Maloy
3 | Book Depreciation |  |  | Use GenCo assumption as per Jody Pierce
4 | Fin Fan Cooler |  |  | Bernstein's cost model, calculated by Bruce Golden
5 | No Capacity Degradation for LM 6000 Peaker model |  |  | Bruce Golden
6 | Spread Option Model |  |  | Jim Simpson
7 | Estimated drawdown schedule |  |  | Bruce Golden
8 | Property Tax, State Tax |  |  | Jim Curry
9 | Heat Rate Degradation |  |  | Bruce Golden
CONTACTS
| Subjects | Contacts | Extension
| Model | Clement Lau | x 3-9446
|  | Ben Rogers | x 3-7998
| Turbine/Technical Info | Doug Sewell | x 3-6337
| Engineers | Mike Coleman | x 6-6385
|  | Bruce Golden | x 6-6063
|  | Chris Booth | x 6-7089
| O&M | Scot Chambers | x 6-8371
| Spread Option Model | Jim Simpson | x 3-7202
| Accounting | Jody Pierce | x 5-7405
| Federal Tax, misc. Tax | Mike Fredell | x 3-7022
|  | Matt Gockerman | x 3-3979
|  | Patrick Maloy | x 3-6174
| State/Property Tax | Warren Schick | x 3-0689
|  | Jim Curry | x 3-6367

## Tracking Sheet
PROJECT NAME: UAE-Lowell
TRACKING SHEET
| EQUITY IRR WITH NO | DSCR
| RESIDUAL VALUE | MIN | AVG.
Current | 2.551% | 1.3 | 1.3
Track Changes | 2.551% | 1.3 | 1.3

## Assumptions
Unhide Sub Debt, 1999 Columns
PROJECT NAME: UAE-Lowell
UAE Cost Sceanrio
ASSUMPTIONS & SUMMARY OUTPUT
SOURCES & USES: |  |  |  | PROJECT DESCRIPTION: |  |  |  | OPERATING COSTS ASSUMPTIONS (FROM ENGINEERS/ASSET MANAGEMENT): |  |  |  | Fuel | Capacity $ | VOM | Residual Value | Capacity | Chillers | Compressor | Debt | New Debt | Versions
[8 empty] | (1st year Annualized) |  |  |  | Index | Base | Pass-through | EBITDA Exit Multiple | ISO | Yes | Yes | Bank LT Debt | 10-Yr. Debt | Optimal Debt
Sources of Funds | % | 000 $ | $/kW | Type of Turbine |  | LM6000 | [5 empty] | Fixed | Low | Not Pass-through | % of Project Cost | 95 degrees | No | No | Capital Market | 7-Yr. Debt | New Debt
Total Equity | 40.38% | 46878.2365 | 203.8184 | Cost Per Turbine (w Carry Cost) (000$) |  | 14260 |  | CPI Escalator (%) | 3% |  |  | Custom | Index |  | 000$/MW |  |  |  | Mini-perm | Lease
Debt Issuance | 59.62% | 69202.7635 | 300.8816 | Number of Turbines |  | 5 | [6 empty] | Custom |  | None
|  |  |  | Net Turbine Rating (MW) |  | 46 |  | Escalated Costs: |  |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 2 | 1
Total Sources | 100% | 116081 | 504.7 | Heat Rate-New and Clean (HHV) |  | 10100 |  |  | 000$ -year | $/kW-year | $/mWh | Index | Base | Pass-through | EBITDA Exit Multiple | 2 | 20 | Yes | Bank LT Debt | 7-Yr. Debt | 1
|  |  |  | Heat Rate-Degraded (HHV) |  | 10200 |  | Variable Operating Cost |  |  | 0.3
|  |  |  | No. of Construction Months |  | 7 |  | Major Maintenance |  |  | 1.9 |  | With Chillers | Without Chillers
Uses of Funds |  |  |  | Start of Commercial Operation |  | 2001-05-01 |  | Total VOM | 0 |  | 2.2 | ISO | 11 | 21
|  |  |  | No. of Months in the 1st Operating year |  | 8 |  |  |  |  | ESC. | 95o | 12 | 22
EPC (From Engineers/Nepco): |  | ENA Turbines with UAE Costs |  | Project Life (Years) |  | 20 |  | Labor, Ann. Inspection, Fixed (Maint), Op. Fee | 494 | 2.1478
Turbine (with Carrying Cost) | 61.42% | 71300 | 310 | Location (State) |  | MA |  | Property & BI Insurance | 400 | 1.7391
Sprint Package Adder | 0% | 0 | 0 |  |  |  |  | Water Supply Discharge | 0 | 0
BOP & Construction | 8.804% | 10220 | 44.4348 | Residual Value (at year 20) |  |  |  | Nox Budget/Audit Costs | 125 | 0.54348
Pipeline | 1.292% | 1500 | 6.5217 | EBITDA Exit Multiple |  | 5 |  | Water / Supply Discharge | 100 | 0.43478
Switchgear/MCC/Relays | 1.077% | 1250 | 5.4348 | % of Initial Project Cost |  | 20% |  | Asset Mhmt. Cost | 100 | 0.43478
SCR, CO oxidation Catalyst, DLE Combuster Turbine | 5.298% | 6150 | 26.7391 | $/kW |  | 200 |  | Interconnect & Nepool Fees | 100 | 0.43478
Dual Fuel | 0% | 0 | 0 |  |  |  |  | Total Fixed Escalating Cost | 1319 | 5.7348
Black Start | 0% | 0 | 0 | FINANCING ASSUMPTIONS:
Gas Compression | 1.292% | 1500 | 6.5217 | DEBT |  | Construction Loan |  | Non-Escalated Costs:
Demineralized Water Facility | 0% | 0 | 0 | Debt Issued | 2000-10-01 |  | Debt Versions | Fuel | 18727.7949 | 81.4252
Stacks, Noise Mitigation, Buildings | 1.292% | 1500 | 6.5217 | Treasury Rate as of: | 2000-02-15 |  |  | Property Tax | 500 | 2.1739 | 2%
Freight | 0.4307% | 500 | 2.1739 |  |  |  |  | Franchise Tax | 0 | 0
Overhead & Fees - EE&CC | 0% | 0 | 0 | Amount ('000 $) | 69202.7635 |  | Debt Options | Gross Receipts Tax | 0 | 0
Overhead & Fees - Nepco | 0% | 0 | 0 | Term (yrs) | 20 |  |  | Debt Service Reserve Fee | 0 | 0
LMP Cost Adder | 0% | 0 | 0 | Final Maturity | 2017-04-01
Chillers (Check that BOP did not already include this) | 0% | 0 | 0 | Average Life (yrs) | -4.5166 |  |  | DEPRECIATION ASSUMPTIONS:
Sub Total | 80.91% | 93920 | 408.3478
|  |  |  | Treasury Rate (%) | 6.5% | 6.5% |  |  | Year | Method | Residual (%)
Soft Cost (From Engineers/Asset Management): |  |  |  | Spread (%) | 1.75% | 1.75% |  | Federal & State Tax Depreciation
Spare Parts Inventory | 0.3015% | 350 | 1.5217 | All-In Rate (%) | 8.25% | 8.25% |  | EPC Costs | 15 | MACRS | 0%
Owners Cost | 13.37% | 15521 | 67.4826 |  |  |  |  | Start-Up Cost | 5 | SL | 0%
Others Costs | 0.6461% | 750 | 3.2609 | Maximum DSR Amount (000 $) | 0 | 0 | (months/year) | Transaction Costs | 20 | SL | 0%
Environmental Permitting | 0% | 0 | 0 | Debt Service Reserve LOC Fee | 2%
Insurance | 0% | 0 | 0 | Interest Income Rate | 0% |  |  | Book Depreciation
Capitalized Salaries | 0% | 0 | 0 |  |  |  |  | EPC Costs | 30 | SL | 10%
Owner's Engineer | 0% | 0 | 0 | EQUITY |  |  |  | Start-Up Cost | 5 | SL | 0%
Development Expenses | 0% | 0 | 0 | Equity Closed | 2000-06-01 |  |  | Transaction Costs | 20 | SL | 0%
Legal Expense | 0% | 0 | 0 | Equity Partner's Share | 0% | 0
Interconnect Study | 0% | 0 | 0 | Enron's Share | 100% | 46878.2365 |  | TAX ASSUMPTIONS (PROJECT MAY INCLUDE SPECIFIC TAXES):
IDC | 0% | 0 | 0
Land | 0.8615% | 1000 | 4.3478 | PPA ASSUMPTIONS (MAKE CHANGES AS NEEDED): |  |  |  | Federal Income Tax Rate (%) | 35%
Sales & Used Tax | 3.911% | 4540 | 19.7391 |  |  |  |  | State Income Tax Rate (average %) | 7% | (Project Specific)
Contingency | 0% | 0 | 0 | Fixed Price PPA |  |  |  | Franchise Tax (% on Net Asset) | 0% | (Project Specific)
Sub Total | 19.09% | 22161 | 96.3522 | No. of years |  | 20 |  | Gross Receipts Tax (%) | 0% | (Project Specific)
|  |  |  | Capacity Charge ($/kW-mo.) |  | 4.5 |  | Sales & Used Tax Rate on Fuel (%) | 1.5% | (Project Specific)
Financing Costs: | [7 empty] | Sales & Used Tax Rate on Hard Cost (%) | 5% | (Project Specific)
Lender's Engineer | 0% | 0 | 0 | Merchant Price Period
Lender's Counsel | 0% | 0 | 0 | No. of years |  | 0
Financing Fee (All-in Fees) | 0% | 0 | 0 | Capacity Charge ($/kW-mo.)
Sub Total | 0% | 0 | 0
|  |  |  | Variable Payment ($/mWh) |  | 2.2
Total Uses | 100% | 116081 | 504.7
|  |  |  | Net Generation (MWh) |  | 563500
SUMMARY OUTPUT:
TECHNICAL ASSUMPTIONS:
All-in Capital Cost ($/kW) |  | 504.7
|  |  |  | Site Condition (MW) |  | 230
|  | Avg. | Min | Evaporative Cooler (MW) |  | 0
DSCR |  | 1.3 | 1.3 | Net Output (MW) |  | 230
Enron Equity Returns |  |  |  | No. of Starts per year |  | 140
20 Yrs After-Tax Cashflow with Zero Residual Value |  | 2.551% |  | Available PSIG |  | 400
20 Yrs After-Tax Cashflow with 5x EBITDA Exit Multiple Residual Value |  | 3.783% | Target | No. of Run Hours per year |  | 2450
20 Yrs After-Tax Cashflow with 20% Initial Project Cost Residual Value |  | 4.478% | 12%
20 Yrs After-Tax Cashflow with $200/kW Residual Value |  | 5.765%
Key Stats | 2001 | 2002 | 2003
EBITDA (000 $) | 6859 | 10551.43 | 10503.5629
Net Income (000 $) | -998.0226 | -1240.9908 | -1140.498
Pre-Tax Cashflow (000 $) | 4467.4548 | 4969.3592 | 5129.7755
Cashflow to Equity (000 $) | 3550.5921 | 2490.7614 | 2414.7191
Note on C21: clau: $62,000/turbine as per Bruce Golden
Note on C41: Ben Rogers: Make sure that ENA is not operating the facility, thus there will be no mobilization costs
Note on C58: Ben Rogers: Based on company's estimate
Note on H11: clau: Calculated to include Carry Cost on a separate spreadsheet.
Note on H13: clau: This is an estimate, please check with Engineers for specific project
Note on H14: clau: This is an estimate, please check with Engineers for specific project
Note on H15: clau: This is an estimate, please check with Engineers for specific project
Note on H61: clau: As per Bruce Golden for simple cycle LM6000
Note on H72: Ben Rogers: Based on company's estimates
Note on L38: clau: Assumption checked with Patrick Maloy on 2/4/00.
Note on L43: clau: Assumption used for GenCo. Verified with Jody Pierce 2/3/00.
Note on N55: Ben Rogers: Need to check with Patrick Maloy the states tax rate

## IS
PROJECT NAME: UAE-Lowell
INCOME STATEMENT
|  | 0.66667 | 1.6667 | 2.6667 | 3.6667 | 4.6667 | 5.6667 | 6.6667 | 7.6667 | 8.6667 | 9.6667 | 10.6667 | 11.6667 | 12.6667 | 13.6667 | 14.6667 | 15.6667 | 16.6667 | 17.6667 | 18.6667 | 19.6667 | 20.6667 | 21.6667 | 22.6667 | 23.6667 | 24.6667 | 25.6667 | 26.6667 | 27.6667 | 28.6667 | 29.6667 | 30.6667
('000 $) |  | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
|  | 2001-12-31 | 2002-12-31 | 2003-12-31 | 2004-12-31 | 2005-12-31 | 2006-12-31 | 2007-12-31 | 2008-12-31 | 2009-12-31 | 2010-12-31 | 2011-12-31 | 2012-12-31 | 2013-12-31 | 2014-12-31 | 2015-12-31 | 2016-12-31 | 2017-12-31 | 2018-12-31 | 2019-12-31 | 2020-12-31 | 2021-12-31 | 2022-12-31 | 2023-12-31 | 2024-12-31 | 2025-12-31 | 2026-12-31 | 2027-12-31 | 2028-12-31 | 2029-12-31 | 2030-12-31 | 2031-12-31
Revenue
Capacity Revenue |  | 8280 | 12420 | 12420 | 12420 | 12420 | 12420 | 12420 | 12420 | 12420 | 12420 | 12420 | 12420 | 12420 | 12420 | 12420 | 12420 | 12420 | 12420 | 12420 | 12420 | 5753.7592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy Revenue |  | 19992.1665 | 19919.8634 | 20147.7302 | 20477.6739 | 20867.7473 | 21281.1602 | 21708.1293 | 22165.8789 | 22654.4486 | 23173.879 | 23724.2122 | 24235.5209 | 24698.0292 | 25561.0674 | 26235.4573 | 26940.9796 | 27677.6843 | 28445.6233 | 29244.8495 | 30075.4178 | 30937.3847 | 15315.064 | 15385.6271 | 15458.3071 | 15533.1675 | 15610.2737 | 15689.6931 | 15771.4951 | 15855.7511 | 15942.5349 | 16031.9221
Ancillary Services |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Revenue |  | 28272.1665 | 32339.8634 | 32567.7302 | 32897.6739 | 33287.7473 | 33701.1602 | 34128.1293 | 34585.8789 | 35074.4486 | 35593.879 | 36144.2122 | 36655.5209 | 37118.0292 | 37981.0674 | 38655.4573 | 39360.9796 | 40097.6843 | 40865.6233 | 41664.8495 | 42495.4178 | 36691.144 | 15315.064 | 15385.6271 | 15458.3071 | 15533.1675 | 15610.2737 | 15689.6931 | 15771.4951 | 15855.7511 | 15942.5349 | 16031.9221
Expense
Fuel |  | 18727.7949 | 18617.5606 | 18806.3583 | 19096.0608 | 19444.6859 | 19815.4069 | 20198.4034 | 20610.8613 | 21052.7804 | 21524.1607 | 22025.0024 | 22485.3348 | 22895.3375 | 23704.295 | 24322.9817 | 24971.1297 | 25648.739 | 26355.8096 | 27092.3414 | 27858.3345 | 28653.7889 | 12962.9602 | 12962.9602 | 12962.9602 | 12962.9602 | 12962.9602 | 12962.9602 | 12962.9602 | 12962.9602 | 12962.9602 | 12962.9602
Fixed Operating Expenses |  | 329.3333 | 508.82 | 524.0846 | 539.8071 | 556.0014 | 572.6814 | 589.8618 | 607.5577 | 625.7844 | 644.558 | 663.8947 | 683.8115 | 704.3259 | 725.4557 | 747.2193 | 769.6359 | 792.725 | 816.5067 | 841.0019 | 866.232 | 892.2189 | 918.9855 | 946.5551 | 974.9517 | 1004.2003 | 1034.3263 | 1065.3561 | 1097.3168 | 1130.2363 | 1164.1434 | 1199.0677
Variable Operating Expenses |  | 172.4143 | 177.5867 | 182.9143 | 188.4018 | 194.0538 | 199.8754 | 205.8717 | 212.0479 | 218.4093 | 224.9616 | 231.7104 | 238.6617 | 245.8216 | 253.1962 | 260.7921 | 268.6159 | 276.6744 | 284.9746 | 293.5238 | 302.3295 | 311.3994 | 320.7414 | 330.3637 | 340.2746 | 350.4828 | 360.9973 | 371.8272 | 382.982 | 394.4715 | 406.3056 | 418.4948
Major Maintenance |  | 1091.9573 | 1124.7161 | 1158.4575 | 1193.2113 | 1229.0076 | 1265.8778 | 1303.8542 | 1342.9698 | 1383.2589 | 1424.7567 | 1467.4994 | 1511.5243 | 1556.8701 | 1603.5762 | 1651.6834 | 1701.234 | 1752.271 | 1804.8391 | 1858.9843 | 1914.7538 | 1972.1964 | 2031.3623 | 2092.3032 | 2155.0723 | 2219.7244 | 2286.3162 | 2354.9057 | 2425.5528 | 2498.3194 | 2573.269 | 2650.4671
Insurance |  | 266.6667 | 412 | 424.36 | 437.0908 | 450.2035 | 463.7096 | 477.6209 | 491.9495 | 506.708 | 521.9093 | 537.5666 | 553.6935 | 570.3044 | 587.4135 | 605.0359 | 623.187 | 641.8826 | 661.1391 | 680.9732 | 701.4024 | 722.4445 | 744.1178 | 766.4414 | 789.4346 | 813.1176 | 837.5112 | 862.6365 | 888.5156 | 915.1711 | 942.6262 | 970.905
SG&A |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Start Charge |  | 125 | 128.75 | 132.6125 | 136.5909 | 140.6886 | 144.9093 | 149.2565 | 153.7342 | 158.3463 | 163.0966 | 167.9895 | 173.0292 | 178.2201 | 183.5667 | 189.0737 | 194.7459 | 200.5883 | 206.606 | 212.8041 | 219.1883 | 225.7639 | 232.5368 | 239.5129 | 246.6983 | 254.0993 | 261.7222 | 269.5739 | 277.6611 | 285.991 | 294.5707 | 303.4078
Property Tax |  | 500 | 510 | 520.2 | 530.604 | 541.2161 | 552.0404 | 563.0812 | 574.3428 | 585.8297 | 597.5463 | 609.4972 | 621.6872 | 634.1209 | 646.8033 | 659.7394 | 672.9342 | 686.3929 | 700.1207 | 714.1231 | 728.4056 | 742.9737 | 757.8332 | 772.9898 | 788.4496 | 804.2186 | 820.303 | 836.7091 | 853.4432 | 870.5121 | 887.9223 | 905.6808
Franchise Tax |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gross Receipts Tax |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Debt Service Reserve LOC Fee |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Marketing Fee |  | 66.6667 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103
Administrative Fee |  | 66.6667 | 103 | 106.09 | 109.2727 | 112.5509 | 115.9274 | 119.4052 | 122.9874 | 126.677 | 130.4773 | 134.3916 | 138.4234 | 142.5761 | 146.8534 | 151.259 | 155.7967 | 160.4706 | 165.2848 | 170.2433 | 175.3506 | 180.6111 | 186.0295 | 191.6103 | 197.3587 | 203.2794 | 209.3778 | 215.6591 | 222.1289 | 228.7928 | 235.6566 | 242.7262
O&M Fees |  | 66.6667 | 103 | 106.09 | 109.2727 | 112.5509 | 115.9274 | 119.4052 | 122.9874 | 126.677 | 130.4773 | 134.3916 | 138.4234 | 142.5761 | 146.8534 | 151.259 | 155.7967 | 160.4706 | 165.2848 | 170.2433 | 175.3506 | 180.6111 | 186.0295 | 191.6103 | 197.3587 | 203.2794 | 209.3778 | 215.6591 | 222.1289 | 228.7928 | 235.6566 | 242.7262
Total Expense |  | 21413.1665 | 21788.4334 | 22064.1673 | 22443.3121 | 22883.9586 | 23349.3557 | 23829.7603 | 24342.438 | 24887.471 | 25464.9438 | 26074.9434 | 26647.5891 | 27173.1526 | 28101.0133 | 28842.0435 | 29616.076 | 30423.2143 | 31263.5652 | 32137.2385 | 33044.3473 | 33985.008 | 18443.5962 | 18597.347 | 18755.5587 | 18918.3621 | 19085.892 | 19258.2869 | 19435.6896 | 19618.2471 | 19806.1106 | 19999.4359
EBITDA |  | 6859 | 10551.43 | 10503.5629 | 10454.3618 | 10403.7887 | 10351.8045 | 10298.369 | 10243.4409 | 10186.9776 | 10128.9352 | 10069.2687 | 10007.9318 | 9944.8766 | 9880.0541 | 9813.4137 | 9744.9036 | 9674.47 | 9602.058 | 9527.611 | 9451.0705 | 2706.1359 | -3128.5323 | -3211.7199 | -3297.2516 | -3385.1946 | -3475.6183 | -3568.5938 | -3664.1945 | -3762.4959 | -3863.5757 | -3967.5137
Depreciation & Amortization |  | 4714.8667 | 7072.3 | 7072.3 | 7072.3 | 7072.3 | 4250.8333 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 946.7
EBIT |  | 2144.1333 | 3479.13 | 3431.2629 | 3382.0618 | 3331.4887 | 6100.9712 | 7458.269 | 7403.3409 | 7346.8776 | 7288.8352 | 7229.1687 | 7167.8318 | 7104.7766 | 7039.9541 | 6973.3137 | 6904.8036 | 6834.37 | 6761.958 | 6687.511 | 6610.9705 | -133.9641 | -5968.6323 | -6051.8199 | -6137.3516 | -6225.2946 | -6315.7183 | -6408.6938 | -6504.2945 | -6602.5959 | -6703.6757 | -4914.2137
Interest Expense |  | 3795.1219 | 5532.0511 | 5317.9428 | 5086.818 | 4838.0351 | 4572.5464 | 4287.9331 | 3983.4644 | 3655.5203 | 3304.6147 | 2927.7755 | 2523.7267 | 2088.2091 | 1621.1407 | 1118.783 | 579.1117 | 73.5973 | 0 | 0 | 0 | 0 | 53.6606 | 215.2314 | 442.5358 | 695.0857 | 974.2506 | 1282.9014 | 1623.342 | 1999.3187 | 2412.8857 | 2948.5285
Pretax Book Income |  | -1650.9886 | -2052.9211 | -1886.6799 | -1704.7562 | -1506.5464 | 1528.4248 | 3170.3359 | 3419.8766 | 3691.3573 | 3984.2205 | 4301.3932 | 4644.1051 | 5016.5675 | 5418.8134 | 5854.5307 | 6325.6919 | 6760.7727 | 6761.958 | 6687.511 | 6610.9705 | -133.9641 | -6022.2929 | -6267.0513 | -6579.8874 | -6920.3804 | -7289.9689 | -7691.5952 | -8127.6365 | -8601.9146 | -9116.5614 | -7862.7422
Book State Tax Benefit / (Expense) | 7% | 115.5692 | 143.7045 | 132.0676 | 119.3329 | 105.4582 | -106.9897 | -221.9235 | -239.3914 | -258.395 | -278.8954 | -301.0975 | -325.0874 | -351.1597 | -379.3169 | -409.8172 | -442.7984 | -473.2541 | -473.3371 | -468.1258 | -462.7679 | 9.3775 | 421.5605 | 438.6936 | 460.5921 | 484.4266 | 510.2978 | 538.4117 | 568.9346 | 602.134 | 638.1593 | 550.392
Shareholder Fed. Tax Benefit / (Expense) | 35% | 537.3968 | 668.2258 | 614.1143 | 554.8981 | 490.3809 | -497.5023 | -1031.9443 | -1113.1698 | -1201.5368 | -1296.8638 | -1400.1035 | -1511.6562 | -1632.8927 | -1763.8238 | -1905.6497 | -2059.0127 | -2200.6315 | -2201.0173 | -2176.7848 | -2151.8709 | 43.6053 | 1960.2563 | 2039.9252 | 2141.7534 | 2252.5838 | 2372.8849 | 2503.6142 | 2645.5457 | 2799.9232 | 2967.4407 | 2559.3226
Net Income |  | -998.0226 | -1240.9908 | -1140.498 | -1030.5251 | -910.7073 | 923.9328 | 1916.4681 | 2067.3154 | 2231.4255 | 2408.4613 | 2600.1922 | 2807.3615 | 3032.515 | 3275.6727 | 3539.0638 | 3823.8808 | 4086.8871 | 4087.6036 | 4042.6004 | 3996.3317 | -80.9813 | -3640.4761 | -3788.4325 | -3977.542 | -4183.3699 | -4406.7862 | -4649.5693 | -4913.1563 | -5199.8574 | -5510.9614 | -4753.0277

## Capital Budget
UAE Lowell Power Expansion |  | PRELIMINARY DATA; ENGINEERING STUDY UNDERWAY TO CONFIRM ASSUMPTIONS
Capital Cost Breakdown ($ = 000's)
| 5x GE LM 6000 Base Package - Simple Cycle | DLE Combustor | 0 | (1=yes, 0=no)
Feb 23 Meeting with Enron Capital and Trade
|  | Lowell Expansion |  |  |  | GT Pro
Gas Turbine Package |  | Equipment | Installation | Total | Per Unit
| Gas Turbine Generator | 69000 | 1000 | 70000 | 14000 | 70000 | 0
| Sprint Package Adder (unavail w/DLE) | 1500 | 0 | 1500 | 300 |  | 1500
| Inlet Air Chiller | 3800 | 250 | 4050 | 810 | 4278 | -228
| Switchgear/MCC/Relays/Breaker Set | 1000 | 250 | 1250 | 250 | 770 | 480
| Stack(s)/Noise Attenuation/Buildings | 1250 | 250 | 1500 | 300 |  | 1500
| Water Tube Oil Cooler | 0 | 0 | 0 | 0 |  | 0
| Freight | 500 | 0 | 500 | 100 |  | 500
| Spare Parts Inventory | 350 | 0 | 350 | 70 | 250 | 100
Total Base Package |  | 77400 | 1750 | 79150 | 15830 | 75298 | 3852
Emissions Controls
| Vanadium-Titanium SCR (to 2 ppm NOX) | 4600 | 250 | 4850 | 970
| CO Oxidation Catalyst (to 10ppm CO) | 1000 | 100 | 1100 | 220
| Dry Low Emissions (DLE) Combustor Adder | 0 | 200 | 200 | 40
|  | 5600 | 550 | 6150 | 1230
Balance Of Plant
| Pads and Grading | 1200 | 400 | 1600 | 320
| Fuel Gas Compressors | 1000 | 250 | 1250 | 250
| Control Room (upgrade to existing unit) | 250 | 100 | 350 | 70
| Controls For Remote Operation | 50 | 50 | 100 | 20
| Demin Water Treatment (for Sprint/Water Inj) | 500 | 100 | 600 | 120
| Fire Protection | 300 | 100 | 400 | 80
| Cooling Tower for Chiller | 1200 | 350 | 1550 | 310
| Ammonia System (Tanks, Unldg./Fwdg. Pumps) | 250 | 50 | 300 | 60
| Step-Up Transformer(s) | 1500 | 300 | 1800 | 360
| Piping | 300 | 120 | 420 | 84
| Wiring | 700 | 450 | 1150 | 230
| Continuous Emissions Monitoring | 550 | 150 | 700 | 140
| Other | 0 | 0 | 0 | 0
Total Emissions and BOP |  | 13400 | 2970 | 16370 | 3274
Total EPC |  |  |  | 95520 | 19104
Owner's Cost
| Air Permitting | 500 |  |  | 100
| Air Permit Fees | 25 |  |  | 5
| Boston Gas Upgrades | 2000 |  |  | 400
| Utility Connection Cost (NEP) | 750 |  |  | 150
| Interconnect Study (NEP) | 250 |  |  | 50
| Property Purchase | 1000 |  |  | 200
| Water/Sewer Connect | 200 |  |  | 40
| Phase I/Phase II Environmental Review | 35 |  |  | 7
| Engineering Plant Specification | 50 |  |  | 10
| Engineering (Studies/Services/Conceptual) | 75 |  |  | 15
| Development/Construction Management | 600 |  |  | 120
| Interest During Construction | 3220 |  |  | 644
| Misc. Permits/Fees |  |  |  | 0
| Legal Fees | 500 |  |  | 100
| Bank Fees | 500 |  |  | 100
| Emissions Offsets | 350 |  |  | 70
| Working Capital | 2500 |  |  | 500
| Miscellaneous Consultants | 100 |  |  | 20
| Owner's Contingency (3% of EPC) | 2865.6 |  |  | 573.12
Total Owner's |  | 15520.6 |  |  | 3104.12
Commissioning
| Site Infrastructure (roads, landscape, neighbors) | 250 |  |  | 50
| Start Up | 500 |  |  | 100
Total Commissioning |  | 750 |  |  | 150
Total
| Base Package | 79150 |  |  | 15830
| BOP | 16370 |  |  | 3274
| Sales Tax (5.0%) | 4540 |  |  | 908
| Owner's Cost | 15520.6 |  |  | 3104.12
| Other Costs | 750 |  |  | 150
Total Capital Cost |  | 116330.6 |  |  | 23266.12
ISO Output (MW) |  | 227.5 |  |  | 45.5
$/kW |  | 511.3433 |  |  | 511.3433
| DLE Estimated Output at 90 deg F | 221.6
| Sprint/Water Inj Estimated Output at 90 deg F | 227.5

## Gas Curve
Total Price to
| Tenn Zone 6 | Annual | Year | Price
2001-01-01 | 4.0555 |  | 2001 | 3.1784
2001-02-01 | 3.8955 |  | 2002 | 3.1597
2001-03-01 | 3.343 |  | 2003 | 3.1917 | 1.0101
2001-04-01 | 2.863 |  | 2004 | 3.2409 | 1.0154
2001-05-01 | 2.781 |  | 2005 | 3.3 | 1.0183
2001-06-01 | 2.793 |  | 2006 | 3.363 | 1.0191
2001-07-01 | 2.816 |  | 2007 | 3.428 | 1.0193
2001-08-01 | 2.8155 |  | 2008 | 3.498 | 1.0204
2001-09-01 | 2.796 |  | 2009 | 3.573 | 1.0214
2001-10-01 | 2.8405 |  | 2010 | 3.653 | 1.0224
2001-11-01 | 3.2795 |  | 2011 | 3.738 | 1.0233
2001-12-01 | 3.862 | 3.1784 | 2012 | 3.8161 | 1.0209
2002-01-01 | 4.0725 |  | 2013 | 3.8857 | 1.0182
2002-02-01 | 3.925 |  | 2014 | 4.023 | 1.0353
2002-03-01 | 3.3155 |  | 2015 | 4.128 | 1.0261
2002-04-01 | 2.829 |  | 2016 | 4.238 | 1.0266
2002-05-01 | 2.77 |  | 2017 | 4.353 | 1.0271
2002-06-01 | 2.782 |  | 2018 | 4.473 | 1.0276
2002-07-01 | 2.799 |  | 2019 | 4.598 | 1.0279
2002-08-01 | 2.8025 |  | 2020 | 4.728 | 1.0283
2002-09-01 | 2.782 |  | 2021 | 4.863 | 1.0286
2002-10-01 | 2.8255
2002-11-01 | 3.2965
2002-12-01 | 3.7165 | 3.1597
2003-01-01 | 4.0725
2003-02-01 | 3.937
2003-03-01 | 3.358
2003-04-01 | 2.864
2003-05-01 | 2.805
2003-06-01 | 2.817
2003-07-01 | 2.834
2003-08-01 | 2.8375
2003-09-01 | 2.817
2003-10-01 | 2.8605
2003-11-01 | 3.3365
2003-12-01 | 3.7615 | 3.1917
2004-01-01 | 4.1325
2004-02-01 | 3.997
2004-03-01 | 3.408
2004-04-01 | 2.909
2004-05-01 | 2.85
2004-06-01 | 2.862
2004-07-01 | 2.879
2004-08-01 | 2.8825
2004-09-01 | 2.862
2004-10-01 | 2.9055
2004-11-01 | 3.3865
2004-12-01 | 3.8165 | 3.2409
2005-01-01 | 4.2025
2005-02-01 | 4.067
2005-03-01 | 3.468
2005-04-01 | 2.964
2005-05-01 | 2.905
2005-06-01 | 2.917
2005-07-01 | 2.934
2005-08-01 | 2.9375
2005-09-01 | 2.917
2005-10-01 | 2.9605
2005-11-01 | 3.4465
2005-12-01 | 3.8815 | 3.3
2006-01-01 | 4.2775
2006-02-01 | 4.142
2006-03-01 | 3.533
2006-04-01 | 3.024
2006-05-01 | 2.965
2006-06-01 | 2.977
2006-07-01 | 2.994
2006-08-01 | 2.9975
2006-09-01 | 2.977
2006-10-01 | 3.0205
2006-11-01 | 3.5065
2006-12-01 | 3.9415 | 3.363
2007-01-01 | 4.3425
2007-02-01 | 4.207
2007-03-01 | 3.598
2007-04-01 | 3.089
2007-05-01 | 3.03
2007-06-01 | 3.042
2007-07-01 | 3.059
2007-08-01 | 3.0625
2007-09-01 | 3.042
2007-10-01 | 3.0855
2007-11-01 | 3.5715
2007-12-01 | 4.0065 | 3.428
2008-01-01 | 4.4125
2008-02-01 | 4.277
2008-03-01 | 3.668
2008-04-01 | 3.159
2008-05-01 | 3.1
2008-06-01 | 3.112
2008-07-01 | 3.129
2008-08-01 | 3.1325
2008-09-01 | 3.112
2008-10-01 | 3.1555
2008-11-01 | 3.6415
2008-12-01 | 4.0765 | 3.498
2009-01-01 | 4.4875
2009-02-01 | 4.352
2009-03-01 | 3.743
2009-04-01 | 3.234
2009-05-01 | 3.175
2009-06-01 | 3.187
2009-07-01 | 3.204
2009-08-01 | 3.2075
2009-09-01 | 3.187
2009-10-01 | 3.2305
2009-11-01 | 3.7165
2009-12-01 | 4.1515 | 3.573
2010-01-01 | 4.5675
2010-02-01 | 4.432
2010-03-01 | 3.823
2010-04-01 | 3.314
2010-05-01 | 3.255
2010-06-01 | 3.267
2010-07-01 | 3.284
2010-08-01 | 3.2875
2010-09-01 | 3.267
2010-10-01 | 3.3105
2010-11-01 | 3.7965
2010-12-01 | 4.2315 | 3.653
2011-01-01 | 4.6525
2011-02-01 | 4.517
2011-03-01 | 3.908
2011-04-01 | 3.399
2011-05-01 | 3.34
2011-06-01 | 3.352
2011-07-01 | 3.369
2011-08-01 | 3.3725
2011-09-01 | 3.352
2011-10-01 | 3.3955
2011-11-01 | 3.8815
2011-12-01 | 4.3165 | 3.738
2012-01-01 | 4.7425
2012-02-01 | 4.607
2012-03-01 | 3.998
2012-04-01 | 3.489
2012-05-01 | 3.43
2012-06-01 | 3.442
2012-07-01 | 3.459
2012-08-01 | 3.4625
2012-09-01 | 3.442
2012-10-01 | 3.4855
2012-11-01 | 3.9715
2012-12-01 | 4.264 | 3.8161
2013-01-01 | 4.39
2013-02-01 | 4.702
2013-03-01 | 4.093
2013-04-01 | 3.584
2013-05-01 | 3.525
2013-06-01 | 3.537
2013-07-01 | 3.554
2013-08-01 | 3.5575
2013-09-01 | 3.537
2013-10-01 | 3.5805
2013-11-01 | 4.0665
2013-12-01 | 4.5015 | 3.8857
2014-01-01 | 4.9375
2014-02-01 | 4.802
2014-03-01 | 4.193
2014-04-01 | 3.684
2014-05-01 | 3.625
2014-06-01 | 3.637
2014-07-01 | 3.654
2014-08-01 | 3.6575
2014-09-01 | 3.637
2014-10-01 | 3.6805
2014-11-01 | 4.1665
2014-12-01 | 4.6015 | 4.023
2015-01-01 | 5.0425
2015-02-01 | 4.907
2015-03-01 | 4.298
2015-04-01 | 3.789
2015-05-01 | 3.73
2015-06-01 | 3.742
2015-07-01 | 3.759
2015-08-01 | 3.7625
2015-09-01 | 3.742
2015-10-01 | 3.7855
2015-11-01 | 4.2715
2015-12-01 | 4.7065 | 4.128
2016-01-01 | 5.1525
2016-02-01 | 5.017
2016-03-01 | 4.408
2016-04-01 | 3.899
2016-05-01 | 3.84
2016-06-01 | 3.852
2016-07-01 | 3.869
2016-08-01 | 3.8725
2016-09-01 | 3.852
2016-10-01 | 3.8955
2016-11-01 | 4.3815
2016-12-01 | 4.8165 | 4.238
2017-01-01 | 5.2675
2017-02-01 | 5.132
2017-03-01 | 4.523
2017-04-01 | 4.014
2017-05-01 | 3.955
2017-06-01 | 3.967
2017-07-01 | 3.984
2017-08-01 | 3.9875
2017-09-01 | 3.967
2017-10-01 | 4.0105
2017-11-01 | 4.4965
2017-12-01 | 4.9315 | 4.353
2018-01-01 | 5.3875
2018-02-01 | 5.252
2018-03-01 | 4.643
2018-04-01 | 4.134
2018-05-01 | 4.075
2018-06-01 | 4.087
2018-07-01 | 4.104
2018-08-01 | 4.1075
2018-09-01 | 4.087
2018-10-01 | 4.1305
2018-11-01 | 4.6165
2018-12-01 | 5.0515 | 4.473
2019-01-01 | 5.5125
2019-02-01 | 5.377
2019-03-01 | 4.768
2019-04-01 | 4.259
2019-05-01 | 4.2
2019-06-01 | 4.212
2019-07-01 | 4.229
2019-08-01 | 4.2325
2019-09-01 | 4.212
2019-10-01 | 4.2555
2019-11-01 | 4.7415
2019-12-01 | 5.1765 | 4.598
2020-01-01 | 5.6425
2020-02-01 | 5.507
2020-03-01 | 4.898
2020-04-01 | 4.389
2020-05-01 | 4.33
2020-06-01 | 4.342
2020-07-01 | 4.359
2020-08-01 | 4.3625
2020-09-01 | 4.342
2020-10-01 | 4.3855
2020-11-01 | 4.8715
2020-12-01 | 5.3065 | 4.728
2021-01-01 | 5.7775
2021-02-01 | 5.642
2021-03-01 | 5.033
2021-04-01 | 4.524
2021-05-01 | 4.465
2021-06-01 | 4.477
2021-07-01 | 4.494
2021-08-01 | 4.4975
2021-09-01 | 4.477
2021-10-01 | 4.5205
2021-11-01 | 5.0065
2021-12-01 | 5.4415 | 4.863

## Fixed and Variable Costs
United American Energy | PRELIMINARY ECONOMIC ANALYSIS
Lowell Power Expansion
Feb 23 Meeting with Enron Capital and Trade
Operations Summary
FIXED COSTS
Labor |  | 100 | add one+ maintenance
Annual Inspection of Gas Turbines |  | 100
Fixed - maint & consum |  | 193.75 | per S&S
Operator Fee |  | 100
G&A
Property & BI Insurance |  | 400
Replacement Power Insurance |  | discuss
Real Property Taxes |  | 500 | same as existing PILOT
Water Supply/Discharge |  | 100 | cooling tower
Interconnect and NEPOOL Fees |  | 150
Audit/Miscellaneous |  | 50
NOx Budget |  | 75
Asset Mgt. Cost |  | 100
1868.75
VARIABLE COSTS | $/mwhr | Cost | Energy | hrs/yr | Capacity
LM6000 | 2.3187 | 1258.9348 | 542942.5855 | 2450.1019 | 221.6
Consumables | 0.15418 | 83.7091 | 542942.5855

## Returns Analysis
PROJECT NAME: UAE-Lowell
RETURNS ANALYSIS
| 0 | 0.66667 | 1.6667 | 2.6667 | 3.6667 | 4.6667 | 5.6667 | 6.6667 | 7.6667 | 8.6667 | 9.6667 | 10.6667 | 11.6667 | 12.6667 | 13.6667 | 14.6667 | 15.6667 | 16.6667 | 17.6667 | 18.6667 | 19.6667 | 20.6667 | 21.6667 | 22.6667 | 23.6667 | 24.6667 | 25.6667 | 26.6667 | 27.6667 | 28.6667 | 29.6667 | 30.6667
('000 $) | Close | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| 2000-06-01 | 2001-12-30 12:00 | 2002-12-30 18:00 | 2003-12-31 | 2004-12-30 06:00 | 2005-12-30 12:00 | 2006-12-30 18:00 | 2007-12-31 | 2008-12-30 06:00 | 2009-12-30 12:00 | 2010-12-30 18:00 | 2011-12-31 | 2012-12-30 06:00 | 2013-12-30 12:00 | 2014-12-30 18:00 | 2015-12-31 | 2016-12-30 06:00 | 2017-12-30 12:00 | 2018-12-30 18:00 | 2019-12-31 | 2020-12-30 06:00 | 2021-12-30 12:00 | 2022-12-30 18:00 | 2023-12-31 | 2024-12-30 06:00 | 2025-12-30 12:00 | 2026-12-30 18:00 | 2027-12-31 | 2028-12-30 06:00 | 2029-12-30 12:00 | 2030-12-30 18:00 | 2031-12-31
EBITDA | 0 | 6859 | 10551.43 | 10503.5629 | 10454.3618 | 10403.7887 | 10351.8045 | 10298.369 | 10243.4409 | 10186.9776 | 10128.9352 | 10069.2687 | 10007.9318 | 9944.8766 | 9880.0541 | 9813.4137 | 9744.9036 | 9674.47 | 9602.058 | 9527.611 | 9451.0705 | 2706.1359 | -3128.5323 | -3211.7199 | -3297.2516 | -3385.1946 | -3475.6183 | -3568.5938 | -3664.1945 | -3762.4959 | -3863.5757 | -3967.5137
Less Interest Payments | 0 | -2391.5452 | -5582.0708 | -5373.7874 | -5149.9876 | -4898.5908 | -4641.0769 | -4361.3769 | -4064.8587 | -3737.3344 | -3395.2674 | -3025.1042 | -2629.9024 | -2198.8947 | -1741.8898 | -1248.6305 | -719.0807 | -146.9935 | 0 | 0 | 0 | 0 | -26.6292 | -161.4238 | -383.1717 | -628.5945 | -901.0825 | -1202.0811 | -1535.3543 | -1899.9085 | -2304.75 | -1550.5265
Pre-Tax Cashflow | 0 | 4467.4548 | 4969.3592 | 5129.7755 | 5304.3742 | 5505.1978 | 5710.7276 | 5936.9921 | 6178.5822 | 6449.6432 | 6733.6679 | 7044.1645 | 7378.0294 | 7745.9819 | 8138.1643 | 8564.7833 | 9025.8229 | 9527.4765 | 9602.058 | 9527.611 | 9451.0705 | 2706.1359 | -3155.1615 | -3373.1437 | -3680.4233 | -4013.7892 | -4376.7008 | -4770.6749 | -5199.5489 | -5662.4045 | -6168.3257 | -5518.0402
Less Cash Taxes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -290.4899 | -2988.6615 | -3768.1701 | -3737.8984 | -1070.2768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Principal Payments | 0 | -916.8627 | -2478.5978 | -2715.0563 | -2906.743 | -3108.5445 | -3331.8192 | -3570.6933 | -3830.6129 | -4104.2633 | -4407.3527 | -4731.93 | -5085.514 | -5457.8591 | -5870.5836 | -6312.9297 | -6795.2442 | -3578.1573 | 0 | 0 | 0 | 0 | 1314.215 | 2616.0237 | 2904.8435 | 3213.9969 | 3557.2935 | 3929.3224 | 4337.5512 | 4773.3638 | 5257.3461 | 5343.4199
Less Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cashflow to Equity | 0 | 3550.5921 | 2490.7614 | 2414.7191 | 2397.6312 | 2396.6534 | 2378.9084 | 2366.2988 | 2347.9693 | 2345.3799 | 2326.3152 | 2312.2345 | 2292.5154 | 2288.1228 | 2267.5808 | 2251.8536 | 2230.5787 | 5658.8293 | 6613.3965 | 5759.4408 | 5713.1721 | 1635.8592 | -1840.9464 | -757.1199 | -775.5798 | -799.7923 | -819.4073 | -841.3526 | -861.9977 | -889.0406 | -910.9796 | -174.6204
Distribution to Equity | 2000-06-01: 100%
| 0 | 3550.5921 | 2490.7614 | 2414.7191 | 2397.6312 | 2396.6534 | 2378.9084 | 2366.2988 | 2347.9693 | 2345.3799 | 2326.3152 | 2312.2345 | 2292.5154 | 2288.1228 | 2267.5808 | 2251.8536 | 2230.5787 | 5658.8293 | 6613.3965 | 5759.4408 | 5713.1721 | 1635.8592 | -1840.9464 | -757.1199 | -775.5798 | -799.7923 | -819.4073 | -841.3526 | -861.9977 | -889.0406 | -910.9796 | -174.6204
Equity RROR | 2000-06-01: 14%
Beginning Balance | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46827.7931 | -46827.7931 | -46827.7931 | -46827.7931 | -46827.7931 | -46827.7931 | -46827.7931 | -46827.7931 | -46827.7931 | -46827.7931 | -46827.7931 | -46827.7931 | -46827.7931
RROR Target Coupon | 0 | 6562.9531 | 6562.9531 | 6562.9531 | 6562.9531 | 6562.9531 | 6562.9531 | 6562.9531 | 6562.9531 | 6562.9531 | 6562.9531 | 6562.9531 | 6562.9531 | 6562.9531 | 6562.9531 | 6562.9531 | 6562.9531 | 6562.9531 | 6562.9531 | 6555.891 | 6555.891 | 6555.891 | 6555.891 | 6555.891 | 6555.891 | 6555.891 | 6555.891 | 6555.891 | 6555.891 | 6555.891 | 6555.891 | 6555.891
Actual Cash Flow | 0 | 3550.5921 | 2490.7614 | 2414.7191 | 2397.6312 | 2396.6534 | 2378.9084 | 2366.2988 | 2347.9693 | 2345.3799 | 2326.3152 | 2312.2345 | 2292.5154 | 2288.1228 | 2267.5808 | 2251.8536 | 2230.5787 | 5658.8293 | 6613.3965 | 5759.4408 | 5713.1721 | 1635.8592 | -1840.9464 | -757.1199 | -775.5798 | -799.7923 | -819.4073 | -841.3526 | -861.9977 | -889.0406 | -910.9796 | -174.6204
Equity Paydown | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.4434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ending Balance | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46878.2365 | -46827.7931 | -46827.7931 | -46827.7931 | -46827.7931 | -46827.7931 | -46827.7931 | -46827.7931 | -46827.7931 | -46827.7931 | -46827.7931 | -46827.7931 | -46827.7931 | -46827.7931 | -46827.7931
ENRON'S RETURNS ANALYSIS
Zero Residual Value
Equity Return | 2000-06-01: -46878.2365
Actual Cash Flow | 0 | 3550.5921 | 2490.7614 | 2414.7191 | 2397.6312 | 2396.6534 | 2378.9084 | 2366.2988 | 2347.9693 | 2345.3799 | 2326.3152 | 2312.2345 | 2292.5154 | 2288.1228 | 2267.5808 | 2251.8536 | 2230.5787 | 5658.8293 | 6613.3965 | 5759.4408 | 5713.1721 | 1635.8592 | -1840.9464 | -757.1199 | -775.5798 | -799.7923 | -819.4073 | -841.3526 | -861.9977 | -889.0406 | -910.9796 | -174.6204
Total Cash Flow | -46878.2365 | 3550.5921 | 2490.7614 | 2414.7191 | 2397.6312 | 2396.6534 | 2378.9084 | 2366.2988 | 2347.9693 | 2345.3799 | 2326.3152 | 2312.2345 | 2292.5154 | 2288.1228 | 2267.5808 | 2251.8536 | 2230.5787 | 5658.8293 | 6613.3965 | 5759.4408 | 5713.1721 | 1635.8592 | -1840.9464 | -757.1199 | -775.5798 | -799.7923 | -819.4073 | -841.3526 | -861.9977 | -889.0406 | -910.9796 | -174.6204
| IRR | 2.551%
With 5x EBITDA Exit Multiple
Equity Return | 2000-06-01: -46878.2365
Actual Cash Flow | 0 | 3550.5921 | 2490.7614 | 2414.7191 | 2397.6312 | 2396.6534 | 2378.9084 | 2366.2988 | 2347.9693 | 2345.3799 | 2326.3152 | 2312.2345 | 2292.5154 | 2288.1228 | 2267.5808 | 2251.8536 | 2230.5787 | 5658.8293 | 6613.3965 | 5759.4408 | 5713.1721 | 1635.8592 | -1840.9464 | -757.1199 | -775.5798 | -799.7923 | -819.4073 | -841.3526 | -861.9977 | -889.0406 | -910.9796 | -174.6204
Residual Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13530.6797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -19317.8785
Total Cash Flow | -46878.2365 | 3550.5921 | 2490.7614 | 2414.7191 | 2397.6312 | 2396.6534 | 2378.9084 | 2366.2988 | 2347.9693 | 2345.3799 | 2326.3152 | 2312.2345 | 2292.5154 | 2288.1228 | 2267.5808 | 2251.8536 | 2230.5787 | 5658.8293 | 6613.3965 | 5759.4408 | 5713.1721 | 15166.5389 | -1840.9464 | -757.1199 | -775.5798 | -799.7923 | -819.4073 | -841.3526 | -861.9977 | -889.0406 | -910.9796 | -19492.4989
| IRR | 3.783%
With 20% Initial Project Cost
Equity Return | 2000-06-01: -46878.2365
Actual Cash Flow | 0 | 3550.5921 | 2490.7614 | 2414.7191 | 2397.6312 | 2396.6534 | 2378.9084 | 2366.2988 | 2347.9693 | 2345.3799 | 2326.3152 | 2312.2345 | 2292.5154 | 2288.1228 | 2267.5808 | 2251.8536 | 2230.5787 | 5658.8293 | 6613.3965 | 5759.4408 | 5713.1721 | 1635.8592 | -1840.9464 | -757.1199 | -775.5798 | -799.7923 | -819.4073 | -841.3526 | -861.9977 | -889.0406 | -910.9796 | -174.6204
Residual Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23216.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23216.2
Total Cash Flow | -46878.2365 | 3550.5921 | 2490.7614 | 2414.7191 | 2397.6312 | 2396.6534 | 2378.9084 | 2366.2988 | 2347.9693 | 2345.3799 | 2326.3152 | 2312.2345 | 2292.5154 | 2288.1228 | 2267.5808 | 2251.8536 | 2230.5787 | 5658.8293 | 6613.3965 | 5759.4408 | 5713.1721 | 24852.0592 | -1840.9464 | -757.1199 | -775.5798 | -799.7923 | -819.4073 | -841.3526 | -861.9977 | -889.0406 | -910.9796 | 23041.5796
| IRR | 4.478%
With $200/kW
Equity Return | 2000-06-01: -46878.2365
Actual Cash Flow | 0 | 3550.5921 | 2490.7614 | 2414.7191 | 2397.6312 | 2396.6534 | 2378.9084 | 2366.2988 | 2347.9693 | 2345.3799 | 2326.3152 | 2312.2345 | 2292.5154 | 2288.1228 | 2267.5808 | 2251.8536 | 2230.5787 | 5658.8293 | 6613.3965 | 5759.4408 | 5713.1721 | 1635.8592 | -1840.9464 | -757.1199 | -775.5798 | -799.7923 | -819.4073 | -841.3526 | -861.9977 | -889.0406 | -910.9796 | -174.6204
Residual Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46000
Total Cash Flow | -46878.2365 | 3550.5921 | 2490.7614 | 2414.7191 | 2397.6312 | 2396.6534 | 2378.9084 | 2366.2988 | 2347.9693 | 2345.3799 | 2326.3152 | 2312.2345 | 2292.5154 | 2288.1228 | 2267.5808 | 2251.8536 | 2230.5787 | 5658.8293 | 6613.3965 | 5759.4408 | 5713.1721 | 47635.8592 | -1840.9464 | -757.1199 | -775.5798 | -799.7923 | -819.4073 | -841.3526 | -861.9977 | -889.0406 | -910.9796 | 45825.3796
| IRR | 5.765%

## Price_Technical Assumption
PROJECT NAME: UAE-Lowell
PRICE/TECHNICAL ASSUMPTIONS
|  | 0.66667 | 1.6667 | 2.6667 | 3.6667 | 4.6667 | 5.6667 | 6.6667 | 7.6667 | 8.6667 | 9.6667 | 10.6667 | 11.6667 | 12.6667 | 13.6667 | 14.6667 | 15.6667 | 16.6667 | 17.6667 | 18.6667 | 19.6667 | 20.6667 | 21.6667 | 22.6667 | 23.6667 | 24.6667 | 25.6667 | 26.6667 | 27.6667 | 28.6667 | 29.6667 | 30.6667
|  | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
CAPACITY PRICE $/kW-MONTH
| Fixed Price | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Merchant Price
1 | Base | 5.4933 | 5.6581 | 5.6458 | 5.7213 | 5.6998 | 5.7713 | 5.8419 | 5.9116 | 6.0889 | 6.1596 | 6.3444 | 6.4159 | 6.6084 | 6.6806 | 6.7512 | 6.82 | 6.8869 | 6.9516 | 7.014 | 7.0739 | 7.1311 | 7.1854 | 7.2396 | 7.2939 | 7.3482 | 7.4024 | 7.4567 | 7.5109 | 7.5652 | 7.6195 | 7.6737
2 | Low | 4.3775 | 4.5088 | 4.7352 | 4.8772 | 5.0235 | 5.1742 | 5.3295 | 5.2782 | 5.2191 | 5.0397 | 4.9602 | 4.8713 | 4.8951 | 4.9159 | 4.8037 | 4.8141 | 4.8208 | 4.9654 | 5.1144 | 5.1173 | 5.2708 | 5.429 | 5.5871 | 5.7452 | 5.9033 | 6.0615 | 6.2196 | 6.3777 | 6.5358 | 6.694 | 6.8521
3 | Index | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Custom | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | Market Price Scenario | 5.4933 | 5.6581 | 5.6458 | 5.7213 | 5.6998 | 5.7713 | 5.8419 | 5.9116 | 6.0889 | 6.1596 | 6.3444 | 6.4159 | 6.6084 | 6.6806 | 6.7512 | 6.82 | 6.8869 | 6.9516 | 7.014 | 7.0739 | 7.1311 | 7.1854 | 7.2396 | 7.2939 | 7.3482 | 7.4024 | 7.4567 | 7.5109 | 7.5652 | 7.6195 | 7.6737
| Blended Capacity Price | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 6.2541 | 7.1854 | 7.2396 | 7.2939 | 7.3482 | 7.4024 | 7.4567 | 7.5109 | 7.5652 | 7.6195 | 7.6737
GAS PRICE $/MMBTU
1 | Index (Tenn Zone 6) | 3.1784 | 3.1597 | 3.1917 | 3.2409 | 3.3 | 3.363 | 3.428 | 3.498 | 3.573 | 3.653 | 3.738 | 3.8161 | 3.8857 | 4.023 | 4.128 | 4.238 | 4.353 | 4.473 | 4.598 | 4.728 | 4.863 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
2 | Fixed | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
3 | Custom | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
| Sales Tax Rate | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5%
1 | Gas Price Assumption | 3.2261 | 3.2071 | 3.2396 | 3.2895 | 3.3495 | 3.4134 | 3.4794 | 3.5504 | 3.6266 | 3.7078 | 3.794 | 3.8733 | 3.944 | 4.0833 | 4.1899 | 4.3015 | 4.4183 | 4.5401 | 4.6669 | 4.7989 | 4.9359 | 2.233 | 2.233 | 2.233 | 2.233 | 2.233 | 2.233 | 2.233 | 2.233 | 2.233 | 2.233
ENERGY PRICE $/MWH
| Fuel | 33.2348 | 33.0391 | 33.3742 | 33.8883 | 34.507 | 35.1649 | 35.8445 | 36.5765 | 37.3607 | 38.1973 | 39.0861 | 39.903 | 40.6306 | 42.0662 | 43.1641 | 44.3143 | 45.5168 | 46.7716 | 48.0787 | 49.438 | 50.8497 | 23.0044 | 23.0044 | 23.0044 | 23.0044 | 23.0044 | 23.0044 | 23.0044 | 23.0044 | 23.0044 | 23.0044
| Variable O&M | 2.2438 | 2.3111 | 2.3804 | 2.4518 | 2.5254 | 2.6012 | 2.6792 | 2.7596 | 2.8424 | 2.9276 | 3.0155 | 3.1059 | 3.1991 | 3.2951 | 3.3939 | 3.4957 | 3.6006 | 3.7086 | 3.8199 | 3.9345 | 4.0525 | 4.1741 | 4.2993 | 4.4283 | 4.5611 | 4.698 | 4.8389 | 4.9841 | 5.1336 | 5.2876 | 5.4462
| Marginal Cost of Generation | 35.4786 | 35.3502 | 35.7546 | 36.3401 | 37.0324 | 37.766 | 38.5237 | 39.3361 | 40.2031 | 41.1249 | 42.1015 | 43.0089 | 43.8297 | 45.3613 | 46.558 | 47.8101 | 49.1175 | 50.4803 | 51.8986 | 53.3725 | 54.9022 | 27.1785 | 27.3037 | 27.4327 | 27.5655 | 27.7023 | 27.8433 | 27.9885 | 28.138 | 28.292 | 28.4506
Pass-through | Energy Price Assumption | 35.4786 | 35.3502 | 35.7546 | 36.3401 | 37.0324 | 37.766 | 38.5237 | 39.3361 | 40.2031 | 41.1249 | 42.1015 | 43.0089 | 43.8297 | 45.3613 | 46.558 | 47.8101 | 49.1175 | 50.4803 | 51.8986 | 53.3725 | 54.9022 | 27.1785 | 27.3037 | 27.4327 | 27.5655 | 27.7023 | 27.8433 | 27.9885 | 28.138 | 28.292 | 28.4506
HEAT RATE (HHV)
| New and Clean | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100
Degradation (%) | bar: 2001 to 2031
| Net Heat Rate | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302

## Cash Flows
PROJECT NAME: UAE-Lowell
Debt Structures
| 0 | 0.66667 | 1.6667 | 2.6667 | 3.6667 | 4.6667 | 5.6667 | 6.6667 | 7.6667 | 8.6667 | 9.6667 | 10.6667 | 11.6667 | 12.6667 | 13.6667 | 14.6667 | 15.6667 | 16.6667 | 17.6667 | 18.6667 | 19.6667 | 20.6667
('000 $) | Close | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
| 2000-06-01 | 2001-12-30 12:00 | 2002-12-30 18:00 | 2003-12-31 | 2004-12-30 06:00 | 2005-12-30 12:00 | 2006-12-30 18:00 | 2007-12-31 | 2008-12-30 06:00 | 2009-12-30 12:00 | 2010-12-30 18:00 | 2011-12-31 | 2012-12-30 06:00 | 2013-12-30 12:00 | 2014-12-30 18:00 | 2015-12-31 | 2016-12-30 06:00 | 2017-12-30 12:00 | 2018-12-30 18:00 | 2019-12-31 | 2020-12-30 06:00 | 2021-12-30 12:00
EBITDA | 0 | 6859 | 10551.43 | 10503.5629 | 10454.3618 | 10403.7887 | 10351.8045 | 10298.369 | 10243.4409 | 10186.9776 | 10128.9352 | 10069.2687 | 10007.9318 | 9944.8766 | 9880.0541 | 9813.4137 | 9744.9036 | 9674.47 | 9602.058 | 9527.611 | 9451.0705 | 2706.1359
Less Interest Payments | 2000-06-01: 0; 2001-12-30 12:00: -7719.3865; 2002-12-30 18:00: -7347.4069; 2003-12-31: -6940.0893; 2004-12-30 06:00: -6494.0764; 2005-12-30 12:00: -6005.6924; 2006-12-30 18:00: -5470.9118; 2007-12-31: -4885.3272; 2008-12-30 06:00: 0; 2009-12-30 12:00: 0; 2010-12-30 18:00: 0
Pre-Tax Cashflow | 2000-06-01: 0; 2001-12-30 12:00: -860.3865; 2002-12-30 18:00: 3204.0231; 2003-12-31: 3563.4736; 2004-12-30 06:00: 3960.2854; 2005-12-30 12:00: 4398.0963; 2006-12-30 18:00: 4880.8927; 2007-12-31: 5413.0419; 2008-12-30 06:00: 10243.4409; 2009-12-30 12:00: 10186.9776; 2010-12-30 18:00: 10128.9352
Less Cash Taxes | 2000-06-01: 0; 2001-12-30 12:00: 0; 2002-12-30 18:00: 0; 2003-12-31: 0; 2004-12-30 06:00: 0; 2005-12-30 12:00: 0; 2006-12-30 18:00: 0; 2007-12-31: 0; 2008-12-30 06:00: 0; 2009-12-30 12:00: 0; 2010-12-30 18:00: 0
Less Principal Payments | 2000-06-01: 0; 2001-12-30 12:00: -3915.5746; 2002-12-30 18:00: -4287.5542; 2003-12-31: -4694.8719; 2004-12-30 06:00: -5140.8847; 2005-12-30 12:00: -5629.2688; 2006-12-30 18:00: -6164.0493; 2007-12-31: 0; 2008-12-30 06:00: 0; 2009-12-30 12:00: 0; 2010-12-30 18:00: 0
Depreciation | 2000-06-01: 0; 2001-12-30 12:00: 0; 2002-12-30 18:00: 0; 2003-12-31: 0; 2004-12-30 06:00: 0; 2005-12-30 12:00: 0; 2006-12-30 18:00: 0; 2007-12-31: 0; 2008-12-30 06:00: 0; 2009-12-30 12:00: 0; 2010-12-30 18:00: 0
Less Capex | 2000-06-01: 0; 2001-12-30 12:00: 0; 2002-12-30 18:00: 0; 2003-12-31: 0; 2004-12-30 06:00: 0; 2005-12-30 12:00: 0; 2006-12-30 18:00: 0; 2007-12-31: 0; 2008-12-30 06:00: 0; 2009-12-30 12:00: 0; 2010-12-30 18:00: 0
Cashflow to Equity | 2000-06-01: 0; 2001-12-30 12:00: -4775.9611; 2002-12-30 18:00: -1083.5311; 2003-12-31: -1131.3982; 2004-12-30 06:00: -1180.5994; 2005-12-30 12:00: -1231.1725; 2006-12-30 18:00: -1283.1566; 2007-12-31: 5413.0419; 2008-12-30 06:00: 10243.4409; 2009-12-30 12:00: 10186.9776; 2010-12-30 18:00: 10128.9352
100%
Distribution to Equity | 2000-06-01: 0; 2001-12-30 12:00: -4775.9611; 2002-12-30 18:00: -1083.5311; 2003-12-31: -1131.3982; 2004-12-30 06:00: -1180.5994; 2005-12-30 12:00: -1231.1725; 2006-12-30 18:00: -1283.1566; 2007-12-31: 5413.0419; 2008-12-30 06:00: 10243.4409; 2009-12-30 12:00: 10186.9776; 2010-12-30 18:00: 10128.9352
ENRON'S RETURNS ANALYSIS
Residuel Value | 2000-06-01: 20%
Lease Option
With 20% of Initial Project Costs |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Equity Return | 0
Actual Cash Flow | -116081 | 1: -4775.9611; 2: -1083.5311; 3: -1131.3982; 4: -1180.5994; 5: -1231.1725
Debt Repayment - Bullet | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 5: 116081
Total Cash Flow | -116081 | 1: -4775.9611; 2: -1083.5311; 3: -1131.3982; 4: -1180.5994; 5: 114849.8275
| IRR | 1: -1.441%
7-Yr. Debt Option
With 20% of Initial Project Costs
Equity Return | -34824.3
Actual Cash Flow | 0 | -4775.9611 | -1083.5311 | -1131.3982 | -1180.5994 | -1231.1725 | -1283.1566 | 5413.0419
Debt Repayment - Bullet | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51424.4965
Total Cash Flow | -34824.3 | -4775.9611 | -1083.5311 | -1131.3982 | -1180.5994 | -1231.1725 | -1283.1566 | 56837.5384
| IRR | 1: 3.294%
10-Yr. Debt Option
With 20% of Initial Project Costs
Equity Return | -34824.3
Actual Cash Flow | 0 | -4775.9611 | -1083.5311 | -1131.3982 | -1180.5994 | -1231.1725 | -1283.1566 | 5413.0419 | 10243.4409 | 10186.9776 | 10128.9352
Debt Repayment - Bullet | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11818.6684
Total Cash Flow | -34824.3 | -4775.9611 | -1083.5311 | -1131.3982 | -1180.5994 | -1231.1725 | -1283.1566 | 5413.0419 | 10243.4409 | 10186.9776 | 21947.6036
| IRR | 1: 0.5549%

## Summary
Deal Structure | Capacity Price | IRR | Debt | Equity
Lease | 4.5 | 5.7% | 100% | 0%
| 5 | 6.6% | 100% | 0%
| 6 | 8.5% | 100% | 0%
| 6.5 | 9.4% | 100% | 0%
70%/30% Debt/Equity
7Yr. Debt Option
12 Yr. Amort.
4.5
5
6
6.5

## Debt Structs
|  |  | Debt | Lease
|  | Plant Turnkey Price | 116081 | 116081
|  | Debt Term (yrs) | 7 | 5
|  | Rate (%) | 9.5% | 7.5%
|  | Princ Amort Sched (yrs) | 12 | 0
|  | Equity (%) | 30% | 0%
|  | Equity ($) | 34824.3 | 0
|  | Posted LC | 0 | 0
|  | Turbines (#) | 5 | 5
|  | Capacity (MW) | 230 | 230
|  | Capacity Pmt ($/kw-mo) | 6.5 | 4.25
[15 empty] | Total $ | $/kw/mo
| 12 yr Amort |  |  |  |  | 7 yr Term with 12 yr. Amort. |  |  |  |  | 100% Lease |  |  |  | Pmt Diff | Pmt Diff
| Prin Bal | Pmt | Int Pmt | Prin Pmt |  | Prin Bal | Pmt | Int Pmt | Prin Pmt |  | Prin Bal | Pmt | Int Pmt | Prin Pmt
1 | 81256.7 | 11634.9611 | 7719.3865 | 3915.5746 | 1 | 81256.7 | 11634.9611 | 7719.3865 | 3915.5746 | 1 | 116081 | 8706.075 | 8706.075 | 0 | 2928.8861 | 1.0612
2 | 77341.1254 | 11634.9611 | 7347.4069 | 4287.5542 | 2 | 77341.1254 | 11634.9611 | 7347.4069 | 4287.5542 | 2 | 116081 | 8706.075 | 8706.075 | 0
3 | 73053.5711 | 11634.9611 | 6940.0893 | 4694.8719 | 3 | 73053.5711 | 11634.9611 | 6940.0893 | 4694.8719 | 3 | 116081 | 8706.075 | 8706.075 | 0 | 42000
4 | 68358.6992 | 11634.9611 | 6494.0764 | 5140.8847 | 4 | 68358.6992 | 11634.9611 | 6494.0764 | 5140.8847 | 4 | 116081 | 8706.075 | 8706.075 | 0 | 0.15
5 | 63217.8145 | 11634.9611 | 6005.6924 | 5629.2688 | 5 | 63217.8145 | 11634.9611 | 6005.6924 | 5629.2688 | 5 | 116081 | 8706.075 | 8706.075 | 0 | 6300 | 2.2826
6 | 57588.5458 | 11634.9611 | 5470.9118 | 6164.0493 | 6 | 57588.5458 | 11634.9611 | 5470.9118 | 6164.0493
7 | 51424.4965 | 11634.9611 | 4885.3272 | 6749.634 | 7 | 51424.4965 | 11634.9611 | 4885.3272 | 6749.634 | [6 empty] | 3.3438
8 | 44674.8625 | 11634.9611 | 4244.1119 | 7390.8492
9 | 37284.0133 | 11634.9611 | 3541.9813 | 8092.9799
10 | 29191.0334 | 11634.9611 | 2773.1482 | 8861.813
11 | 20329.2205 | 11634.9611 | 1931.2759 | 9703.6852
12 | 10625.5353 | 11634.9611 | 1009.4259 | 10625.5353
10 yr Amort
| Prin Bal | Pmt | Int Pmt | Prin Pmt
1 | 81256.7 | 12941.4419 | 7719.3865 | 5222.0554
2 | 76034.6446 | 12941.4419 | 7223.2912 | 5718.1507
3 | 70316.4939 | 12941.4419 | 6680.0669 | 6261.375
4 | 64055.1189 | 12941.4419 | 6085.2363 | 6856.2056
5 | 57198.9133 | 12941.4419 | 5433.8968 | 7507.5451
6 | 49691.3682 | 12941.4419 | 4720.68 | 8220.7619
7 | 41470.6063 | 12941.4419 | 3939.7076 | 9001.7343
8 | 32468.872 | 12941.4419 | 3084.5428 | 9856.8991
9 | 22611.9729 | 12941.4419 | 2148.1374 | 10793.3045
10 | 11818.6684 | 12941.4419 | 1122.7735 | 11818.6684
[9 empty] | 7 Yr Debt |  |  | 100% Lease
[7 empty] | Total Price: |  | 116081 |  |  | 116081
[7 empty] | Debt | 65% | 75452.65 |  | 100% | 116081
[7 empty] | Equity |  | 40628.35 |  |  | 0
[7 empty] | LC | 0% | 0 |  | 20% | 23216.2
[7 empty] | Yr 5 Bal |  | 92412.8458 |  |  | 116081
[13 empty] | Diff | Diff $/kw-mo
[7 empty] | Annual Debt Pmt |  | 11634.9611 |  |  | 8706.075 | -2928.8861 | -1.0612
[7 empty] | Req'd Eq Ret | 15% | 5223.645 |  | 15% | 0 | -5223.645 | -1.8926
[7 empty] | LC Annual Cost | 3% | 0 |  | 3% | 696.486 | 696.486 | 0.25235
[7 empty] | Balance Amort Diff | 10% | 15136.9913 |  | 10% | 19013.7754 | 3876.784 | 1.4046
[7 empty] | Difference | [6 empty] | -1.2968

## Performance
UAE Lowell Power Expansion |  | Single LM6000 Unit
Equipment Performance |  | Ambient vs. Front End Simple Cycle Technology
5 - GE/S&S LM6000 Units
|  | 0 oF |  |  | 60 oF |  |  | 90 oF
|  | DLE | Spr. w/ WI | Spr. w/ SI | DLE | Spr. w/ WI | Spr. w/ SI | DLE | Spr. w/ WI | Spr. w/ SI
General Plant Performance Data
Generator Power, MW |  | S | 48.76 | 48.76 | 44.28 | 46.13 | 47.35 | 44.32 | 46.04 | 47.25
Gross Heat Rate, Btu/kWh (LHV) |  | & | 8338 | 8338 | 8261 | 8557 | 7934 | 8260 | 8555 | 7938
Gross Heat Rate, Btu/kWh (HHV) (3) |  | S | 9264.4352 | 9264.4352 | 9178.8797 | 9507.7683 | 8815.5467 | 9177.7686 | 9505.5461 | 8819.9912
Gross Heat Rate Adjusted for Steam Use, Btu/kWh (HHV) |  |  | na | 10132.1649 | na | na | 9665.9845 | na | na | 9664.0761
Fuel Flow, mmBtu/hr (LHV) |  |  | 406.5609 | 406.5609 | 365.7971 | 394.7344 | 375.6749 | 366.0832 | 393.8722 | 375.0705
Fuel Flow, mmBtu/hr (HHV) |  |  | 451.2826 | 451.2826 | 406.0348 | 438.1552 | 416.9991 | 406.3524 | 437.1981 | 416.3283
Chilling Requirements, tons |  | R | 0 | 0 | 210 | 208 | 212 | 1892 | 1590 | 1905
Water Injection Flow, pph |  | u | 20548 | 0 | 0 | 20835 | 0 | 0 | 20593 | 0
Steam Injection Flow, pph |  | n | 0 | 33500 | 0 | 0 | 31883 | 0 | 0 | 31578
Sprint Water Injection Flow, pph |  | s | 0 | 0 | 0 | 2445 | 2445 | 0 | 2445 | 2445
Aux Load (kW) (2) |  |  | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200
Chiller Aux. Load (kW) |  |  | 0 | 0 | 272 | 270.6 | 273.4 | 1449.4 | 1238 | 1458.5
Net Power Output, MW |  | @ | 47.56 | 47.56 | 42.808 | 44.6594 | 45.8766 | 41.6706 | 43.602 | 44.5915
NOx, ppm |  | 2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
NOx, pph |  | 0 | 41 | 41 | 37 | 40 | 38 | 37 | 40 | 38
CO, ppm |  | oF | 80 | 80 | 25 | 29 | 23 | 25 | 28 | 23
CO, pph |  |  | 80 | 80 | 22 | 28 | 22 | 22 | 27 | 21
Expected DEP NOx Emission Rate, ppm |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Reduction Required |  |  | 92% | 92% | 92% | 92% | 92% | 92% | 92% | 92%
Expected DEP NOx Emission Rate, lb/mmBtu |  |  | 0.0073729 | 0.0073729 | 0.0073729 | 0.0073729 | 0.0073729 | 0.0073729 | 0.0073729 | 0.0073729
Expected DEP NOx Emission Rate, lb/hr |  |  | 2.9937 | 2.996 | 3.3273 | 3.2305 | 3.2234 | 3.3273 | 3.0745 | 3.0696
Expected DEP CO Reduction Rate, % |  |  | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90%
Expected DEP CO Emission Rate, ppm |  |  | 8 | 8 | 2.5 | 2.9 | 2.3 | 2.5 | 2.8 | 2.3
Notes:
1 | Spray Intercooling (Sprint) is not currently available with DLE combustors.
2 | Auxiliary load includes fuel compression, misc. GT auxiliaries, and transformer losses
3 | Gross heat rate as a function of the HHV of the fuel plus degradation

## Perf.
UAE Lowell Power Expansion
Technology Comparison
5 - GE/S&S LM6000 Units | Yearly Revenue/Cost Variances per Unit
| DLE Combustor | Sprint w/ Water Injection | Sprint w/ Steam Injection (3)
| w/ Inlet Chilling | w/ Inlet Chilling | w/ Inlet Chilling
DLE Capital Recovery ($1.1m over 15 yr. @ 11%) (1) | 121000.0008 | 0 | 0
Chiller Cost (90 oF, electric @ $0.03/kw-hr, 2500 hrs) | 108705 | 92850 | 109387.5
Sprint Water Injection (@100 oF & $1.40/100 cu. ft.) | 0 | 1377.7575 | 1377.7575
Water Injection (@100 oF & $1.40/100 cu. ft.) | 0 | 11740.5225 | 0
Steam Injection (550 psig, 75 oF sprht, 1263 Btu/lb) | 0 | 0 | 358947.126
Major Maintenance | 264650 | 224871.0977 | 231000
Water Treatment Capital Recovery ($200,000 over 15 yr. @ 11%) | 0 | 22000.0002 | 22000.0002
Water Treatment Variable Cost ($0.0025/gal for chemical, 2500 hrs.) | 0 | 15432.4041 | 23664.5683
Fuel Cost ($3/mmBtu & 2500 hrs.) | 3047642.64 | 3278986.065 | 3122461.9125
Capacity Payment ($6/kw-mo w/ DLE Unit as datum) | 0 | -133300.8 | -220939.2
Total First Year Cost | 3541997.6408 | 3513957.0469 | 3647899.6645
Operating Hours | 2500
(1) Price differential between machines equipped with a DLE Combustor and those with the Sprint Technology is $1.1 m ($1.4 m for DLE, $0.3 for Sprint)
(2) General assumption of 2500 hrs. operating
(3) Steam injection rates of over 30,000 lbs/hr can not be handled by existing systems

## BS (hidden)
PROJECT NAME: UAE-Lowell
BALANCE SHEET
| 0 | 0.66667 | 1.6667 | 2.6667 | 3.6667 | 4.6667 | 5.6667 | 6.6667 | 7.6667 | 8.6667 | 9.6667 | 10.6667 | 11.6667 | 12.6667 | 13.6667 | 14.6667 | 15.6667 | 16.6667 | 17.6667 | 18.6667 | 19.6667 | 20.6667 | 21.6667 | 22.6667 | 23.6667 | 24.6667 | 25.6667 | 26.6667 | 27.6667 | 28.6667 | 29.6667 | 30.6667
('000 $) | Close | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
|  | 2001-12-30 12:00 | 2002-12-30 18:00 | 2003-12-31 | 2004-12-30 06:00 | 2005-12-30 12:00 | 2006-12-30 18:00 | 2007-12-31 | 2008-12-30 06:00 | 2009-12-30 12:00 | 2010-12-30 18:00 | 2011-12-31 | 2012-12-30 06:00 | 2013-12-30 12:00 | 2014-12-30 18:00 | 2015-12-31 | 2016-12-30 06:00 | 2017-12-30 12:00 | 2018-12-30 18:00 | 2019-12-31 | 2020-12-30 06:00 | 2021-12-30 12:00 | 2022-12-30 18:00 | 2023-12-31 | 2024-12-30 06:00 | 2025-12-30 12:00 | 2026-12-30 18:00 | 2027-12-31 | 2028-12-30 06:00 | 2029-12-30 12:00 | 2030-12-30 18:00 | 2031-12-31
Assets
Cash | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Accounts Receivable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inventories | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other Current Assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Debt Service Reserve | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current Assets |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gross PP&E | 116081 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831 | 115831
Accumulated Depreciation | 0 | 4714.8667 | 11787.1667 | 18859.4667 | 25931.7667 | 33004.0667 | 37254.9 | 40095 | 42935.1 | 45775.2 | 48615.3 | 51455.4 | 54295.5 | 57135.6 | 59975.7 | 62815.8 | 65655.9 | 68496 | 71336.1 | 74176.2 | 77016.3 | 79856.4 | 82696.5 | 85536.6 | 88376.7 | 91216.8 | 94056.9 | 96897 | 99737.1 | 102577.2 | 105417.3 | 106364
Net PP&E | 116081 | 111116.1333 | 104043.8333 | 96971.5333 | 89899.2333 | 82826.9333 | 78576.1 | 75736 | 72895.9 | 70055.8 | 67215.7 | 64375.6 | 61535.5 | 58695.4 | 55855.3 | 53015.2 | 50175.1 | 47335 | 44494.9 | 41654.8 | 38814.7 | 35974.6 | 33134.5 | 30294.4 | 27454.3 | 24614.2 | 21774.1 | 18934 | 16093.9 | 13253.8 | 10413.7 | 9467
Land | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
Other Assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Assets | 117081 | 112116.1333 | 105043.8333 | 97971.5333 | 90899.2333 | 83826.9333 | 79576.1 | 76736 | 73895.9 | 71055.8 | 68215.7 | 65375.6 | 62535.5 | 59695.4 | 56855.3 | 54015.2 | 51175.1 | 48335 | 45494.9 | 42654.8 | 39814.7 | 36974.6 | 34134.5 | 31294.4 | 28454.3 | 25614.2 | 22774.1 | 19934 | 17093.9 | 14253.8 | 11413.7 | 10467
Liabilities
Accounts Payable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Accrued Expenses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Deferred Tax Liability | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Working Capital Revolver | 0 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
Long Term Debt | 69202.7635 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Other Non-Current Liabilities | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Long-term Liabilities | 69202.7635 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Stockholders' Equity
Paid-In-Capital | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365 | 46878.2365
Retained earnings | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Total stockholders' equity | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Total Liabilities & Equity | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Proof | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## Debt
PROJECT NAME: UAE-Lowell
DEBT ISSUANCE | (This page is set up to solve for Debt Principal given DSCR, by using the Goal Seek Button)
('000 $) | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| 2001-12-31 | 2002-12-31 | 2003-12-31 | 2004-12-31 | 2005-12-31 | 2006-12-31 | 2007-12-31 | 2008-12-31 | 2009-12-31 | 2010-12-31 | 2011-12-31 | 2012-12-31 | 2013-12-31 | 2014-12-31 | 2015-12-31 | 2016-12-31 | 2017-12-31 | 2018-12-31 | 2019-12-31 | 2020-12-31 | 2021-12-31 | 2022-12-31 | 2023-12-31 | 2024-12-31 | 2025-12-31 | 2026-12-31 | 2027-12-31 | 2028-12-31 | 2029-12-31 | 2030-12-31 | 2031-12-31
EBITDA by Debt Fiscal Year | 4300.9303 | 10478.8692 | 10515.4969 | 10473.7498 | 10409.2759 | 10364.7649 | 10311.6913 | 10264.113 | 10194.077 | 10143.406 | 10084.1445 | 10030.0413 | 9953.7799 | 9896.2153 | 9830.0282 | 9768.6223 | 9685.392 | 9620.1114 | 9546.1717 | 9476.5912 | 4381.3118 | -1673.8616 | -3190.98 | -3278.1733 | -3361.0231 | -3453.0743 | -3545.4136 | -3642.8558 | -3735.4919 | -3838.375 | -4930.7614 |  | 1
DSCR | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 |  | 6
Target DS | 3308.4079 | 8060.6686 | 8088.8438 | 8056.7306 | 8007.1353 | 7972.8961 | 7932.0702 | 7895.4716 | 7841.5977 | 7802.62 | 7757.0342 | 7715.4164 | 7656.7538 | 7612.4733 | 7561.5601 | 7514.3248 | 7450.3016 | 7400.0857 | 7343.209 | 7289.6855 | 3370.2399 | -1287.5858 | -2454.6 | -2521.6718 | -2585.4024 | -2656.211 | -2727.2412 | -2802.1968 | -2873.4553 | -2952.5961 | -3792.8934
Debt Principal | 2001-12-31: 69202.7635
Ending Balance at Maturity | 2001-12-31: 1.1187e-10
| 2001-04-01 | 2002-04-01 | 2003-04-01 | 2004-04-01 | 2005-04-01 | 2006-04-01 | 2007-04-01 | 2008-04-01 | 2009-04-01 | 2010-04-01 | 2011-04-01 | 2012-04-01 | 2013-04-01 | 2014-04-01 | 2015-04-01 | 2016-04-01 | 2017-04-01 | 2018-04-01 | 2019-04-01 | 2020-04-01 | 2021-04-01 | 2022-04-01 | 2023-04-01 | 2024-04-01 | 2025-04-01 | 2026-04-01 | 2027-04-01 | 2028-04-01 | 2029-04-01 | 2030-04-01 | 2031-04-01 | 2031-05-01
Beginning Balance |  | 68285.9008 | 65807.3029 | 63092.2466 | 60185.5036 | 57076.9591 | 53745.1399 | 50174.4466 | 46343.8337 | 42239.5704 | 37832.2177 | 33100.2877 | 28014.7738 | 22556.9147 | 16686.3311 | 10373.4014 | 3578.1573 | 0 | 0 | 0 | 0 | 0 | 1314.215 | 3930.2388 | 6835.0822 | 10049.0791 | 13606.3726 | 17535.695 | 21873.2461 | 26646.61 | 31903.9561
Addition |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Principal Payment |  | 1222.2195 | 1337.3078 | 1422.2645 | 1531.0997 | 1638.474 | 1755.122 | 1875.2202 | 2016.9576 | 2163.7014 | 2322.2137 | 2490.4611 | 2677.5079 | 2878.3132 | 3094.3547 | 3328.6766 | 3578.1573 | 0 | 0 | 0 | 0 | -643.7929 | -1281.3628 | -1423.1791 | -1573.4917 | -1741.4943 | -1923.3458 | -2125.4313 | -2335.2978 | -2572.4593 | -3208.8793
Interest Payment |  | 1404.5381 | 1353.5571 | 1308.3884 | 1237.9251 | 1173.987 | 1105.4565 | 1040.5029 | 953.2228 | 868.8043 | 778.1517 | 686.424 | 576.2217 | 463.9617 | 343.2127 | 215.1205 | 73.5973 | 0 | 0 | 0 | 0 | 0 | 27.0314 | 81.5041 | 140.5873 | 206.6944 | 279.8626 | 363.6501 | 449.8997 | 548.0806 | 656.2163
Ending Balance |  | 67063.6813 | 64469.9952 | 61669.9821 | 58654.4039 | 55438.4852 | 51990.0179 | 48299.2264 | 44326.8761 | 40075.869 | 35510.0041 | 30609.8266 | 25337.2659 | 19678.6015 | 13591.9764 | 7044.7248 | 1.1187e-10 | 0 | 0 | 0 | 0 | 643.7929 | 2595.5779 | 5353.4179 | 8408.574 | 11790.5735 | 15529.7184 | 19661.1263 | 24208.544 | 29219.0693 | 35112.8354
Pro-rata EBITDA |  | 5188.7002 | 5249.327 | 5246.5689 | 5193.1298 | 5174.6821 | 5148.3994 | 5142.3926 | 5086.6335 | 5065.0632 | 5035.7166 | 5026.0754 | 4967.7185 | 4942.6539 | 4909.8783 | 4896.1705 | 4834.9043 | 4805.9289 | 4769.3147 | 4751.0559 | 3024.5368 | -105.3098 | -1580.7204 | -1629.5475 | -1663.7885 | -1710.504 | -1756.2282 | -1810.7586 | -1849.0898 | -1901.2946 | -3947.0803
DSCR |  | 1.2874 | 1.2979 | 1.3024 | 1.2971 | 1.2981 | 1.2981 | 1.3026 | 1.2973 | 1.2983 | 1.2984 | 1.3029 | 1.2976 | 1.2986 | 1.2986 | 1.3032 | [5 empty] | 0.16358 | 1.288 | 1.2924 | 1.2871 | 1.2879 | 1.2879 | 1.2924 | 1.287 | 1.2879 | 2.0813
(Debt Anniversary) | 2001-10-01 | 2002-10-01 | 2003-10-01 | 2004-10-01 | 2005-10-01 | 2006-10-01 | 2007-10-01 | 2008-10-01 | 2009-10-01 | 2010-10-01 | 2011-10-01 | 2012-10-01 | 2013-10-01 | 2014-10-01 | 2015-10-01 | 2016-10-01 | 2017-10-01 | 2018-10-01 | 2019-10-01 | 2020-10-01 | 2021-10-01 | 2022-10-01 | 2023-10-01 | 2024-10-01 | 2025-10-01 | 2026-10-01 | 2027-10-01 | 2028-10-01 | 2029-10-01 | 2030-10-01 | 2031-05-01
Beginning Balance | 69202.7635 | 67063.6813 | 64469.9952 | 61669.9821 | 58654.4039 | 55438.4852 | 51990.0179 | 48299.2264 | 44326.8761 | 40075.869 | 35510.0041 | 30609.8266 | 25337.2659 | 19678.6015 | 13591.9764 | 7044.7248 | 1.1187e-10 | 0 | 0 | 0 | 0 | 643.7929 | 2595.5779 | 5353.4179 | 8408.574 | 11790.5735 | 15529.7184 | 19661.1263 | 24208.544 | 29219.0693 | 35112.8354
Addition | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Principal Payment | 916.8627 | 1256.3783 | 1377.7486 | 1484.4785 | 1577.4448 | 1693.3452 | 1815.5713 | 1955.3927 | 2087.3057 | 2243.6513 | 2409.7163 | 2595.0528 | 2780.3512 | 2992.2704 | 3218.575 | 3466.5675 | 1.1187e-10 | 0 | 0 | 0 | 0 | -670.4221 | -1334.6609 | -1481.6644 | -1640.5051 | -1815.7992 | -2005.9766 | -2212.1199 | -2438.066 | -2684.8868 | -2134.5406
Interest Payment | 2391.5452 | 2773.956 | 2666.6733 | 2543.8868 | 2426.1229 | 2293.1028 | 2150.4638 | 1992.3431 | 1833.4932 | 1657.6587 | 1468.8008 | 1262.6553 | 1048.0257 | 813.9663 | 562.2051 | 290.5949 | 4.6272e-12 | 0 | 0 | 0 | 0 | 26.6292 | 107.3609 | 220.8285 | 347.804 | 487.6937 | 642.356 | 811.0215 | 1001.3383 | 1208.5888 | 238.0939
Ending Balance | 68285.9008 | 65807.3029 | 63092.2466 | 60185.5036 | 57076.9591 | 53745.1399 | 50174.4466 | 46343.8337 | 42239.5704 | 37832.2177 | 33100.2877 | 28014.7738 | 22556.9147 | 16686.3311 | 10373.4014 | 3578.1573 | 0 | 0 | 0 | 0 | 0 | 1314.215 | 3930.2388 | 6835.0822 | 10049.0791 | 13606.3726 | 17535.695 | 21873.2461 | 26646.61 | 31903.9561 | 37247.376
Pro-rata EBITDA | 4300.9303 | 5290.169 | 5266.1699 | 5227.1809 | 5216.1461 | 5190.0828 | 5163.2919 | 5121.7205 | 5107.4436 | 5078.3429 | 5048.4279 | 5003.9659 | 4986.0614 | 4953.5614 | 4920.1499 | 4872.4518 | 4850.4877 | 4814.1825 | 4776.857 | 4725.5353 | 1356.775 | -1568.5518 | -1610.2596 | -1648.6258 | -1697.2346 | -1742.5703 | -1789.1854 | -1832.0973 | -1886.4021 | -1937.0804 | -983.6811
DSCR | 1.3 | 1.3126 | 1.3021 | 1.2976 | 1.3029 | 1.3019 | 1.3019 | 1.2974 | 1.3027 | 1.3017 | 1.3016 | 1.2971 | 1.3024 | 1.3014 | 1.3014 | 1.2968 | [5 empty] | 2.4364 | 1.312 | 1.3076 | 1.3129 | 1.3121 | 1.3121 | 1.3076 | 1.313 | 1.3121 | 0.5187
| 2001-12-31 | 2002-12-31 | 2003-12-31 | 2004-12-31 | 2005-12-31 | 2006-12-31 | 2007-12-31 | 2008-12-31 | 2009-12-31 | 2010-12-31 | 2011-12-31 | 2012-12-31 | 2013-12-31 | 2014-12-31 | 2015-12-31 | 2016-12-31 | 2017-12-31 | 2018-12-31 | 2019-12-31 | 2020-12-31 | 2021-12-31 | 2022-12-31 | 2023-12-31 | 2024-12-31 | 2025-12-31 | 2026-12-31 | 2027-12-31 | 2028-12-31 | 2029-12-31 | 2030-12-31 | 2031-12-31
Beginning Balance | 68285.9008 | 65807.3029 | 63092.2466 | 60185.5036 | 57076.9591 | 53745.1399 | 50174.4466 | 46343.8337 | 42239.5704 | 37832.2177 | 33100.2877 | 28014.7738 | 22556.9147 | 16686.3311 | 10373.4014 | 3578.1573 | 0 | 0 | 0 | 0 | 0 | 1314.215 | 3930.2388 | 6835.0822 | 10049.0791 | 13606.3726 | 17535.695 | 21873.2461 | 26646.61 | 31903.9561 | 37247.376
Addition | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Interest Payment | 1403.5767 | 1353.5571 | 1297.7124 | 1234.5428 | 1173.987 | 1105.4565 | 1032.0128 | 950.6184 | 868.8043 | 778.1517 | 680.823 | 574.6473 | 463.9617 | 343.2127 | 213.3652 | 73.3962 | 0 | 0 | 0 | 0 | 0 | 27.0314 | 80.8391 | 140.2032 | 206.6944 | 279.8626 | 360.6828 | 448.6705 | 548.0806 | 656.2163 | 2054.2183
Ending Balance | 68285.9008 | 65807.3029 | 63092.2466 | 60185.5036 | 57076.9591 | 53745.1399 | 50174.4466 | 46343.8337 | 42239.5704 | 37832.2177 | 33100.2877 | 28014.7738 | 22556.9147 | 16686.3311 | 10373.4014 | 3578.1573 | 0 | 0 | 0 | 0 | 0 | 1314.215 | 3930.2388 | 6835.0822 | 10049.0791 | 13606.3726 | 17535.695 | 21873.2461 | 26646.61 | 31903.9561 | 37247.376
Debt Service
Principal Payments | 916.8627 | 2478.5978 | 2715.0563 | 2906.743 | 3108.5445 | 3331.8192 | 3570.6933 | 3830.6129 | 4104.2633 | 4407.3527 | 4731.93 | 5085.514 | 5457.8591 | 5870.5836 | 6312.9297 | 6795.2442 | 3578.1573 | 0 | 0 | 0 | 0 | -1314.215 | -2616.0237 | -2904.8435 | -3213.9969 | -3557.2935 | -3929.3224 | -4337.5512 | -4773.3638 | -5257.3461 | -5343.4199
Interest Expense | 2391.5452 | 5582.0708 | 5373.7874 | 5149.9876 | 4898.5908 | 4641.0769 | 4361.3769 | 4064.8587 | 3737.3344 | 3395.2674 | 3025.1042 | 2629.9024 | 2198.8947 | 1741.8898 | 1248.6305 | 719.0807 | 146.9935 | 0 | 0 | 0 | 0 | 26.6292 | 161.4238 | 383.1717 | 628.5945 | 901.0825 | 1202.0811 | 1535.3543 | 1899.9085 | 2304.75 | 1550.5265
Net Debt Service | 3308.4079 | 8060.6686 | 8088.8438 | 8056.7306 | 8007.1353 | 7972.8961 | 7932.0702 | 7895.4716 | 7841.5977 | 7802.62 | 7757.0342 | 7715.4164 | 7656.7538 | 7612.4733 | 7561.5601 | 7514.3248 | 3725.1508 | 0 | 0 | 0 | 0 | -1287.5858 | -2454.6 | -2521.6718 | -2585.4024 | -2656.211 | -2727.2412 | -2802.1968 | -2873.4553 | -2952.5961 | -3792.8934
ACTUAL DSCR | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | [5 empty] | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
Accrued Debt Service
Principal Payments | 916.8627 | 2478.5978 | 2715.0563 | 2906.743 | 3108.5445 | 3331.8192 | 3570.6933 | 3830.6129 | 4104.2633 | 4407.3527 | 4731.93 | 5085.514 | 5457.8591 | 5870.5836 | 6312.9297 | 6795.2442 | 3578.1573 | 0 | 0 | 0 | 0 | -1314.215 | -2616.0237 | -2904.8435 | -3213.9969 | -3557.2935 | -3929.3224 | -4337.5512 | -4773.3638 | -5257.3461 | -5343.4199
Interest Expense | 3795.1219 | 5532.0511 | 5317.9428 | 5086.818 | 4838.0351 | 4572.5464 | 4287.9331 | 3983.4644 | 3655.5203 | 3304.6147 | 2927.7755 | 2523.7267 | 2088.2091 | 1621.1407 | 1118.783 | 579.1117 | 73.5973 | 0 | 0 | 0 | 0 | 53.6606 | 215.2314 | 442.5358 | 695.0857 | 974.2506 | 1282.9014 | 1623.342 | 1999.3187 | 2412.8857 | 2948.5285
Net Debt Service | 4711.9847 | 8010.6489 | 8032.9991 | 7993.561 | 7946.5796 | 7904.3656 | 7858.6265 | 7814.0772 | 7759.7836 | 7711.9674 | 7659.7055 | 7609.2406 | 7546.0682 | 7491.7243 | 7431.7127 | 7374.3558 | 3651.7546 | 0 | 0 | 0 | 0 | -1260.5544 | -2400.7923 | -2462.3076 | -2518.9112 | -2583.0428 | -2646.421 | -2714.2091 | -2774.0452 | -2844.4605 | -2394.8914
Debt Summary
| Treasury (%) |  |  | 6.5%
| Spread (%) |  |  | 1.75%
| All In Coupon Rate (%) |  |  | 8.25%
| Term (years) |  |  | 20
| Average Life (years) |  |  | -4.5166
| Total amount ($ '000) |  |  | 69202.7635
| DSCR |  | Average | 1.3
|  |  | Minimum | 1.3
Time Factor | 0 | 0.99932 | 1.9986 | 3.0007 | 4 | 4.9993 | 5.9986 | 7.0007 | 8 | 8.9993 | 9.9986 | 11.0007 | 12 | 12.9993 | 13.9986 | 15.0007 | 16 | 16.9993 | 17.9986 | 19.0007 | 20 | 20.9993 | 21.9986 | 23.0007 | 24 | 24.9993 | 25.9986 | 27.0007 | 28 | 28.9993 | 29.5797
| 0.49829 | 1.4976 | 2.4997 | 3.499 | 4.4983 | 5.4976 | 6.4997 | 7.499 | 8.4983 | 9.4976 | 10.4997 | 11.499 | 12.4983 | 13.4976 | 14.4997 | 15.499 | 16.4983 | 17.4976 | 18.4997 | 19.499 | 20.4983 | 21.4976 | 22.4997 | 23.499 | 24.4983 | 25.4976 | 26.4997 | 27.499 | 28.4983 | 29.4976 | 29.5797
Average Life | 2001-12-31: -4.5166
Goal Seek Debt

## Depreciation
PROJECT NAME: UAE-Lowell
DEPRECIATION SCHEDULE
|  |  | 0.66667 | 1.6667 | 2.6667 | 3.6667 | 4.6667 | 5.6667 | 6.6667 | 7.6667 | 8.6667 | 9.6667 | 10.6667 | 11.6667 | 12.6667 | 13.6667 | 14.6667 | 15.6667 | 16.6667 | 17.6667 | 18.6667 | 19.6667 | 20.6667 | 21.6667 | 22.6667 | 23.6667 | 24.6667 | 25.6667 | 26.6667 | 27.6667 | 28.6667 | 29.6667 | 30.6667
('000 $) |  |  | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
|  |  | 2001-12-31 | 2002-12-31 | 2003-12-31 | 2004-12-31 | 2005-12-31 | 2006-12-31 | 2007-12-31 | 2008-12-31 | 2009-12-31 | 2010-12-31 | 2011-12-31 | 2012-12-31 | 2013-12-31 | 2014-12-31 | 2015-12-31 | 2016-12-31 | 2017-12-31 | 2018-12-31 | 2019-12-31 | 2020-12-31 | 2021-12-31 | 2022-12-31 | 2023-12-31 | 2024-12-31 | 2025-12-31 | 2026-12-31 | 2027-12-31 | 2028-12-31 | 2029-12-31 | 2030-12-31 | 2031-12-31
US FEDERAL TAX DEPRECIATION & AMORTIZATION
Years
Plant & Equipment - MACRS | 15 |  | 5% | 9.5% | 8.55% | 7.7% | 6.93% | 6.23% | 5.9% | 5.91% | 5.9% | 5.91% | 5.9% | 5.91% | 5.9% | 5.91% | 5.9% | 2.95% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Start-Up Costs - SL | 5 |  | 13.33% | 20% | 20% | 20% | 20% | 6.667% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Transaction Costs - SL | 20 |  | 3.333% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 1.667% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Plant & Equipment - MACRS | 94670 |  | 4733.5 | 8993.65 | 8094.285 | 7289.59 | 6560.631 | 5897.941 | 5585.53 | 5594.997 | 5585.53 | 5594.997 | 5585.53 | 5594.997 | 5585.53 | 5594.997 | 5585.53 | 2792.765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Start-Up Costs - SL | 21161 |  | 2821.4667 | 4232.2 | 4232.2 | 4232.2 | 4232.2 | 1410.7333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Transaction Costs - SL | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Beginning Book Value | 115831 |  | 7554.9667 | 13225.85 | 12326.485 | 11521.79 | 10792.831 | 7308.6743 | 5585.53 | 5594.997 | 5585.53 | 5594.997 | 5585.53 | 5594.997 | 5585.53 | 5594.997 | 5585.53 | 2792.765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ending Value of Assets | 115831 |  | 108276.0333 | 95050.1833 | 82723.6983 | 71201.9083 | 60409.0773 | 53100.403 | 47514.873 | 41919.876 | 36334.346 | 30739.349 | 25153.819 | 19558.822 | 13973.292 | 8378.295 | 2792.765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STATE TAX DEPRECIATION & AMORTIZATION
Years
Plant & Equipment - MACRS | 15 |  | 5% | 9.5% | 8.55% | 7.7% | 6.93% | 6.23% | 5.9% | 5.91% | 5.9% | 5.91% | 5.9% | 5.91% | 5.9% | 5.91% | 5.9% | 2.95% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Start-Up Costs - SL | 5 |  | 13.33% | 20% | 20% | 20% | 20% | 6.667% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Transaction Costs - SL | 20 |  | 3.333% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 1.667% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Plant & Equipment - MACRS | 94670 |  | 4733.5 | 8993.65 | 8094.285 | 7289.59 | 6560.631 | 5897.941 | 5585.53 | 5594.997 | 5585.53 | 5594.997 | 5585.53 | 5594.997 | 5585.53 | 5594.997 | 5585.53 | 2792.765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Start-Up Costs - SL | 21161 |  | 2821.4667 | 4232.2 | 4232.2 | 4232.2 | 4232.2 | 1410.7333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Transaction Costs - SL | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Beginning Book Value | 115831 |  | 7554.9667 | 13225.85 | 12326.485 | 11521.79 | 10792.831 | 7308.6743 | 5585.53 | 5594.997 | 5585.53 | 5594.997 | 5585.53 | 5594.997 | 5585.53 | 5594.997 | 5585.53 | 2792.765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ending Value of Assets | 115831 |  | 108276.0333 | 95050.1833 | 82723.6983 | 71201.9083 | 60409.0773 | 53100.403 | 47514.873 | 41919.876 | 36334.346 | 30739.349 | 25153.819 | 19558.822 | 13973.292 | 8378.295 | 2792.765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BOOK DEPRECIATION & AMORTIZATION
| Years | Residual
Plant & Equipment - SL | 30 | 10% | 2% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 1%
Start-Up Costs - SL | 5 |  | 13.33% | 20% | 20% | 20% | 20% | 6.667% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Transaction Costs - SL | 20 |  | 3.333% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 1.667% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Plant & Equipment - MACRS | 94670 |  | 1893.4 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 946.7
Start-Up Costs - SL | 21161 |  | 2821.4667 | 4232.2 | 4232.2 | 4232.2 | 4232.2 | 1410.7333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Transaction Costs - SL | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Beginning Book Value | 115831 |  | 4714.8667 | 7072.3 | 7072.3 | 7072.3 | 7072.3 | 4250.8333 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 946.7
Ending Book Value of Assets | 115831 |  | 111116.1333 | 104043.8333 | 96971.5333 | 89899.2333 | 82826.9333 | 78576.1 | 75736 | 72895.9 | 70055.8 | 67215.7 | 64375.6 | 61535.5 | 58695.4 | 55855.3 | 53015.2 | 50175.1 | 47335 | 44494.9 | 41654.8 | 38814.7 | 35974.6 | 33134.5 | 30294.4 | 27454.3 | 24614.2 | 21774.1 | 18934 | 16093.9 | 13253.8 | 10413.7 | 9467

## Taxes
PROJECT NAME: UAE-Lowell
TAXES
| 0.66667 | 1.6667 | 2.6667 | 3.6667 | 4.6667 | 5.6667 | 6.6667 | 7.6667 | 8.6667 | 9.6667 | 10.6667 | 11.6667 | 12.6667 | 13.6667 | 14.6667 | 15.6667 | 16.6667 | 17.6667 | 18.6667 | 19.6667 | 20.6667 | 21.6667 | 22.6667 | 23.6667 | 24.6667 | 25.6667 | 26.6667 | 27.6667 | 28.6667 | 29.6667 | 30.6667
('000 $) | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| 2001-12-31 | 2002-12-31 | 2003-12-31 | 2004-12-31 | 2005-12-31 | 2006-12-31 | 2007-12-31 | 2008-12-31 | 2009-12-31 | 2010-12-31 | 2011-12-31 | 2012-12-31 | 2013-12-31 | 2014-12-31 | 2015-12-31 | 2016-12-31 | 2017-12-31 | 2018-12-31 | 2019-12-31 | 2020-12-31 | 2021-12-31 | 2022-12-31 | 2023-12-31 | 2024-12-31 | 2025-12-31 | 2026-12-31 | 2027-12-31 | 2028-12-31 | 2029-12-31 | 2030-12-31 | 2031-12-31
STATE TAXES
Adjusted Pretax Book Income | -1650.9886 | -2052.9211 | -1886.6799 | -1704.7562 | -1506.5464 | 1528.4248 | 3170.3359 | 3419.8766 | 3691.3573 | 3984.2205 | 4301.3932 | 4644.1051 | 5016.5675 | 5418.8134 | 5854.5307 | 6325.6919 | 6760.7727 | 6761.958 | 6687.511 | 6610.9705 | -133.9641 | -6022.2929 | -6267.0513 | -6579.8874 | -6920.3804 | -7289.9689 | -7691.5952 | -8127.6365 | -8601.9146 | -9116.5614 | -7862.7422
Plus Book Depreciation & Amortization | 4714.8667 | 7072.3 | 7072.3 | 7072.3 | 7072.3 | 4250.8333 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 2840.1 | 946.7
Less State Tax Depreciation | -7554.9667 | -13225.85 | -12326.485 | -11521.79 | -10792.831 | -7308.6743 | -5585.53 | -5594.997 | -5585.53 | -5594.997 | -5585.53 | -5594.997 | -5585.53 | -5594.997 | -5585.53 | -2792.765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
State Taxable Income | -4491.0886 | -8206.4711 | -7140.8649 | -6154.2462 | -5227.0774 | -1529.4162 | 424.9059 | 664.9796 | 945.9273 | 1229.3235 | 1555.9632 | 1889.2081 | 2271.1375 | 2663.9164 | 3109.1007 | 6373.0269 | 9600.8727 | 9602.058 | 9527.611 | 9451.0705 | 2706.1359 | -3182.1929 | -3426.9513 | -3739.7874 | -4080.2804 | -4449.8689 | -4851.4952 | -5287.5365 | -5761.8146 | -6276.4614 | -6916.0422
State Income Tax Rate | bar: 2001-12-31 to 2031-12-31
Current State Income Tax Expense (Benefit) | -314.3762 | -574.453 | -499.8605 | -430.7972 | -365.8954 | -107.0591 | 29.7434 | 46.5486 | 66.2149 | 86.0526 | 108.9174 | 132.2446 | 158.9796 | 186.4741 | 217.6371 | 446.1119 | 672.0611 | 672.1441 | 666.9328 | 661.5749 | 189.4295 | -222.7535 | -239.8866 | -261.7851 | -285.6196 | -311.4908 | -339.6047 | -370.1276 | -403.327 | -439.3523 | -484.123
Beginning NOL's | 0 | 314.3762 | 888.8292 | 1388.6897 | 1819.487 | 2185.3824 | 2292.4415 | 2262.6981 | 2216.1495 | 1911.8504 | 1631.9359 | 1523.0185 | 1390.7739 | 1231.7943 | 1045.3201 | 827.6831 | 381.5712 | 0 | 0 | 0 | 0 | 0 | 222.7535 | 462.6401 | 724.4252 | 1010.0448 | 1321.5357 | 1661.1403 | 2031.2679 | 2434.5949 | 2651.1937
New NOL's | 314.3762 | 574.453 | 499.8605 | 430.7972 | 365.8954 | 107.0591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222.7535 | 239.8866 | 261.7851 | 285.6196 | 311.4908 | 339.6047 | 370.1276 | 403.327 | 439.3523 | 484.123
Expired NOLs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -238.0842 | -193.8619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -222.7535 | -17.1331
NOL Utilization (8 years) | 0 | 0 | 0 | 0 | 0 | 0 | -29.7434 | -46.5486 | -66.2149 | -86.0526 | -108.9174 | -132.2446 | -158.9796 | -186.4741 | -217.6371 | -446.1119 | -381.5712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ending NOL's | 314.3762 | 888.8292 | 1388.6897 | 1819.487 | 2185.3824 | 2292.4415 | 2262.6981 | 2216.1495 | 1911.8504 | 1631.9359 | 1523.0185 | 1390.7739 | 1231.7943 | 1045.3201 | 827.6831 | 381.5712 | 0 | 0 | 0 | 0 | 0 | 222.7535 | 462.6401 | 724.4252 | 1010.0448 | 1321.5357 | 1661.1403 | 2031.2679 | 2434.5949 | 2651.1937 | 3118.1836
TOTAL STATE TAXES UTILIZING NOLs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290.4899 | 672.1441 | 666.9328 | 661.5749 | 189.4295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FEDERAL TAXES
State Taxable Income | -4491.0886 | -8206.4711 | -7140.8649 | -6154.2462 | -5227.0774 | -1529.4162 | 424.9059 | 664.9796 | 945.9273 | 1229.3235 | 1555.9632 | 1889.2081 | 2271.1375 | 2663.9164 | 3109.1007 | 6373.0269 | 9600.8727 | 9602.058 | 9527.611 | 9451.0705 | 2706.1359 | -3182.1929 | -3426.9513 | -3739.7874 | -4080.2804 | -4449.8689 | -4851.4952 | -5287.5365 | -5761.8146 | -6276.4614 | -6916.0422
Less: State Taxes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -290.4899 | -672.1441 | -666.9328 | -661.5749 | -189.4295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Federal Taxable Income | -4491.0886 | -8206.4711 | -7140.8649 | -6154.2462 | -5227.0774 | -1529.4162 | 424.9059 | 664.9796 | 945.9273 | 1229.3235 | 1555.9632 | 1889.2081 | 2271.1375 | 2663.9164 | 3109.1007 | 6373.0269 | 9310.3828 | 8929.914 | 8860.6782 | 8789.4956 | 2516.7064 | -3182.1929 | -3426.9513 | -3739.7874 | -4080.2804 | -4449.8689 | -4851.4952 | -5287.5365 | -5761.8146 | -6276.4614 | -6916.0422
Federal Tax Rate | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35%
Federal Tax Expense/ (Benefit) | -1571.881 | -2872.2649 | -2499.3027 | -2153.9862 | -1829.4771 | -535.2957 | 148.7171 | 232.7429 | 331.0745 | 430.2632 | 544.5871 | 661.2228 | 794.8981 | 932.3707 | 1088.1853 | 2230.5594 | 3258.634 | 3125.4699 | 3101.2374 | 3076.3235 | 880.8472 | -1113.7675 | -1199.433 | -1308.9256 | -1428.0981 | -1557.4541 | -1698.0233 | -1850.6378 | -2016.6351 | -2196.7615 | -2420.6148
Beginning NOL's | 0 | 1571.881 | 4444.1459 | 6943.4486 | 9097.4348 | 10926.9119 | 11462.2075 | 11313.4905 | 11080.7476 | 10749.6731 | 10319.4099 | 9774.8228 | 9113.5999 | 8318.7018 | 7386.3311 | 6298.1458 | 4067.5864 | 808.9524 | 0 | 0 | 0 | 0 | 1113.7675 | 2313.2005 | 3622.1261 | 5050.2242 | 6607.6783 | 8305.7016 | 10156.3394 | 12172.9745 | 14369.736
New NOL's | 1571.881 | 2872.2649 | 2499.3027 | 2153.9862 | 1829.4771 | 535.2957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1113.7675 | 1199.433 | 1308.9256 | 1428.0981 | 1557.4541 | 1698.0233 | 1850.6378 | 2016.6351 | 2196.7615 | 2420.6148
Expired NOLs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NOL Utilization (15 years) | 0 | 0 | 0 | 0 | 0 | 0 | -148.7171 | -232.7429 | -331.0745 | -430.2632 | -544.5871 | -661.2228 | -794.8981 | -932.3707 | -1088.1853 | -2230.5594 | -3258.634 | -808.9524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ending NOL's | 1571.881 | 4444.1459 | 6943.4486 | 9097.4348 | 10926.9119 | 11462.2075 | 11313.4905 | 11080.7476 | 10749.6731 | 10319.4099 | 9774.8228 | 9113.5999 | 8318.7018 | 7386.3311 | 6298.1458 | 4067.5864 | 808.9524 | 0 | 0 | 0 | 0 | 1113.7675 | 2313.2005 | 3622.1261 | 5050.2242 | 6607.6783 | 8305.7016 | 10156.3394 | 12172.9745 | 14369.736 | 16790.3508
TOTAL STATE TAXES UTILIZING NOLs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2316.5175 | 3101.2374 | 3076.3235 | 880.8472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## IDC
PROJECT NAME: UAE-Lowell
IDC CALCULATIONS
Total Construction & Other Costs (000$): |  | 10220
No. of Construction Months: |  | 7
Interest During Construction: |  | 8.25% | 0.02292%
|  | Annual | Daily (360-Day)
|  |  | Turbine Cost | Construction &
IDC Calculations |  |  | including Carry | Other Cost | Principal | Balance | Interest | Cum. Interest
Month | Date | % Drawn | (000$) | (000$) | (000$) | (000$) | (000$) | (000$)
1 | 2000-04-01 | 17% | 71302.248 | 1737.4 | 73039.648 | 73039.648 | 0 | 0
2 | 2000-05-01 | 12% | 0 | 1226.4 | 1226.4 | 74768.1956 | 502.1476 | 502.1476
3 | 2000-06-01 | 12% | 0 | 1226.4 | 1226.4 | 76525.7613 | 531.1657 | 1033.3133
4 | 2000-07-01 | 14% | 0 | 1430.8 | 1430.8 | 78482.6759 | 526.1146 | 1559.4279
5 | 2000-08-01 | 13% | 0 | 1328.6 | 1328.6 | 80368.83 | 557.554 | 2116.9819
6 | 2000-09-01 | 12% | 0 | 1226.4 | 1226.4 | 82166.1835 | 570.9536 | 2687.9355
7 | 2000-10-01 | 10% | 0 | 1022 | 1022 | 83753.076 | 564.8925 | 3252.828
8 | 2000-11-01 | 10% | 0 | 1022 | 1022 | 85370.0718 | 594.9958 | 3847.8238
9 | 2000-12-01 | 0% | 0 | 0 | 0 | 85370.0718 | 0 | 3847.8238
10 | 2001-01-01 | 0% | 0 | 0 | 0 | 85370.0718 | 0 | 3847.8238
11 | 2001-02-01 | 0% | 0 | 0 | 0 | 85370.0718 | 0 | 3847.8238
12 | 2001-03-01 | 0% | 0 | 0 | 0 | 85370.0718 | 0 | 3847.8238
13 | 2001-04-01 | 0% | 0 | 0 | 0 | 85370.0718 | 0 | 3847.8238
14 | 2001-05-01 | 0% | 0 | 0 | 0 | 85370.0718 | 0 | 3847.8238
15 | 2001-06-01 | 0% | 0 | 0 | 0 | 85370.0718 | 0 | 3847.8238
16 | 2001-07-01 | 0% | 0 | 0 | 0 | 85370.0718 | 0 | 3847.8238
17 | 2001-08-01 | 0% | 0 | 0 | 0 | 85370.0718 | 0 | 3847.8238
18 | 2001-09-01 | 0% | 0 | 0 | 0 | 85370.0718 | 0 | 3847.8238
19 | 2001-10-01 | 0% | 0 | 0 | 0 | 85370.0718 | 0 | 3847.8238
|  | 100% | 71302.248 | 10220 | 81522.248 |  | 3847.8238
TURBINE DELIVERY SCHEDULE
*Rough Estimate by Bruce Golden. Please double-check for deal specific
[6 empty] | Turbine No. | 1 | 2 | 3 | 4 | 5 | 6
Unit | Turbines | Delivery | LD'S |  | Month | No. of Months | 5.5 | 6 | 6.5 | 7 | 7.5 | 8
Number | Delivered | Schedule | Enforced On |  | 1 |  | 17% | 17% | 17% | 17% | 17% | 17%
1-3 | 3 | 2000-07-30 | 2000-10-30 |  | 2 |  | 16% | 16% | 16% | 12% | 12% | 12%
4-6 | 3 | 2000-08-30 | 2000-10-30 |  | 3 |  | 16% | 16% | 13% | 12% | 12% | 12%
7-8 | 2 | 2000-09-30 | 2000-10-30 |  | 4 |  | 16% | 16% | 16% | 14% | 14% | 14%
9-11 | 3 | 2000-10-30 | 2000-10-30 |  | 5 |  | 17% | 17% | 16% | 18% | 13% | 13%
12-13 | 2 | 2000-11-30 | 2000-11-30 |  | 6 |  | 18% | 18% | 12% | 12% | 12% | 12%
14-15 | 2 | 2000-12-30 | 2000-12-30 |  | 7 |  | 0% | 0% | 10% | 15% | 10% | 10%
16-18 | 3 | 2000-01-30 | 2000-01-30 |  | 8 |  | 0% | 0% | 0% | 0% | 10% | 10%
19-20 | 2 | 2001-02-28 | 2001-02-28 |  | 9 | bar: 1 to 6
21-22 | 2 | 2001-03-30 | 2001-03-30 |  | 10 | bar: 1 to 6
23-24 | 2 | 2001-04-30 | 2001-04-30 |  | 11 | bar: 1 to 6
12 | bar: 1 to 6
13 | bar: 1 to 6
Summary (000$): |  |  |  |  | 14 | bar: 1 to 6
Basis Per Turbine |  |  | 13950 |  | 15 | bar: 1 to 6
Carry Cost Per Turbine |  |  | 289.6163 |  | Sum |  | 100% | 100% | 100% | 100% | 100% | 100%
WestLB Structuring, Restructuring & Legal Fees |  |  | 20.8333
Total Price |  |  | 14260.4496