## Page 1
DATA SHEET
LOST CREEK GATHERING COMPANY, L.L.C. | [36 empty] | Number
[37 empty] | Sheet |  |  | 1 |  |  |  | of |  | 2
LOST CREEK COMPRESSOR STATION | [28 empty] | Date |  | By | [5 empty] | Rev. |  |  |  |  | Date |  | 1995-07-25
[25 empty] | Approved | [11 empty] | P.O. Number
| VARIABLE FREQUENCY DRIVE | [23 empty] | Approved | [11 empty] | P.O. Item No.
Spec. No.
GENERAL INFORMATION
|  | Applicable To: |  |  |  |  | X | Proposal | [5 empty] | Purchase |  |  |  | As Built |  |  |  | X | contractdor shall complete Data Sheet with information not otherwise provided by Company.
LOST CREEK COMPRESSOR STATION
For
SWEETWATER COUNTY, WYOMING
Site
MOTOR DRIVEN RECIPROCATING COMPRESSOR
Service
Vendor
INSTALLATION CONDITIONS
SWEETWATER COUNTY, WYOMING
|  | Geographical Location | [23 empty] | Snow Load (PSF):
7,000'
|  | Elevation (FT MSL) | [23 empty] | Unusual Conditions:
[15 empty] | 100 | [5 empty] | -50
|  | Ambient Temperature, °F: | [9 empty] | Max. | [5 empty] | Min. | [8 empty] | Seismic Zone per Uniform Building Code:
[15 empty] | 80 |  |  |  |  | 25
|  | Relative Humidity (%): | [9 empty] | Max. | [5 empty] | Min. | [8 empty] | Other:
Rainfall Intensity (Inch/Hr):
|  | Drive Location: | [6 empty] | Outdoor |  |  |  | X |  | Indoor
|  | Electrical Area Classification: | [11 empty] | X | Unclassified | [5 empty] | Classified
|  |  | Class | [7 empty] | Division | [7 empty] | Group
DESIGN DATA
|  | Isolation Transformer Primary Voltage: | [23 empty] | Redundant Feature: | [8 empty] | N+1 |  |  |  | Other:
4160 VAC
|  |  | Nominal: |  |  |  | X | [25 empty] | X | Contractor's Standard
Dual Primaries of
[26 empty] | Enclosure: |  |  |  | Purchaser's | [7 empty] | X | Contractor's Standard
[8 empty] | 3 | [5 empty] | Other:
|  | No. of Phases: |  |  |  |  | X | [18 empty] | Incoming Line:
[8 empty] | 60 Hz | [5 empty] | 50 Hz
|  | Frequency: |  |  |  |  | X | [19 empty] | Location:
[8 empty] | 3-Wire | [5 empty] | 4-Wire | [5 empty] | Wye | [10 empty] | Bottom of cabinet
|  | System Type: |  |  |  |  | X | [19 empty] | From:
[8 empty] | Grounded | [5 empty] | Ungrounded | [5 empty] | Delta
|  | Nameplate Horsepower: | [23 empty] | Surge/Lightning Arrestors: | [9 empty] | X | Required on Incoming Terminations
See attached data sheet
|  | Torque: | [23 empty] | Isolation Transformer:
|  | Service Factor: | [8 empty] | 1.0 |  |  | X |  | 1.15 | [12 empty] | CT's Required |  |  |  | Number | [7 empty] | Ratio
|  | Motor Type: | [6 empty] | Induction | [6 empty] | X | Synchronous | [11 empty] | VT's Required |  |  |  | Number | [7 empty] | Ratio
1200 (600 to 1400 rpm on VFD)
|  | RPM: | [24 empty] | X |  | Configured for fans. [Future]
.95 lagging at 1800 rpm
|  | Drive Service Conditions: | [9 empty] | X |  | Indoor |  |  |  | Outdoor | [7 empty] | Power Factor Required:
UTILITY COMPANY INFORMATION
UTILITY COMPANY:
Pacific Power and Light (PacifiCorp)
CONTACT PERSON:
Bob Dahl
TELEPHONE:
(307) 352-5201
START-UP ASSISTANCE AND OPERATOR TRAINING
[12 empty] | Include in Proposal | [7 empty] | 40 | [5 empty] | Operator Training: | [16 empty] | 40
|  | Start-up Assistance: | [8 empty] | X | [12 empty] | MH* | [7 empty] | X | Include in Proposal | [11 empty] | MH**
Unit rate for additional Manhours:
[32 empty] | X | On Site | [6 empty] | At Vendor's Facility
Daily Per diem rate for additional days:
Daily Rate for Additional Training:
|  |  |  | * - Based on a 10 hour day | [28 empty] | ** Based on an 8 hour day
COMMENTS/ ADDITIONAL INFORMATION
1. System required to be a 12 pulse converter, 6 pulse inverter as minimum.
2. Buss work should be rated at 250MVA withstand.
3. Buss cable cabinet shall be of sufficient sizing to install two[2]] 750 MCM 8kv cables per phase.

## Page 2
DATA SHEET
LOST CREEK GATHERING COMPANY, L.L.C. | [7 empty] | Number
[8 empty] | Sheet | 2 |  | of | 2
LSOT CREEK COMPRESSOR STATION | [5 empty] | Date | By | Rev. |  | Date
|  |  |  | Approved |  |  |  | P.O. Number
| VARIABLE FREQUENCY DRIVE |  |  | Approved |  |  |  | P.O. Item No.
Spec. No.
VENDOR SUPPLIED DATA
|  | Variable Frequency Drive Manufacturer: |  |  | DRIVE PARAMETERS:
|  | Model Number: |  |  | Horsepower/KVA:
|  | Guaranteed Package Overall Efficiency: |  |  | Nominal Voltage
|  | @ 100% Rated Freq. & Torque |  |  | Minimum Starting Voltage
|  | @ 90% Rated Freq. & Torque |  |  | Frequency Range (hz)
|  | @ 75 % Rated Freq. & Torque |  |  | Service Factor
|  | @ 50 % Rated Freq. & Torque |  |  | Maximum Speed
|  | Thyristors: |  |  | Speed Range
|  | Manufacturer: |  |  | Temperature Rise
|  | Model Number: |  |  | Minimum Starting Current
|  | Rated Current: |  |  | Full Load Current
|  | D C Link Reactors: |  |  | Maximum KVAR
|  | Manufacturer |  |  | Guaranteed Efficiency (Isolation Transformer):
|  | Model No. or Type |  |  | 100% Freq. and Torque
|  | Rated Current |  |  | 90% Freq. and Torque
|  | Rated Voltage |  |  | 75% Freq. and Torque
|  | Reactance Value |  |  | 50% Freq. and Torque
|  | Weight |  |  | 25% Freq. and Torque
|  | Dimensions |  |  | Guaranteed Efficiency (Variable Frequency Drive):
|  | Watt Loss @ Rated Load |  |  | 100% Freq. and Torque
|  | D C Resistance |  |  | 90% Freq. and Torque
|  | Reactance (ohms) |  |  | 75% Freq. and Torque
|  | Inductance (mh) |  |  | 50% Freq. and Torque
|  | Rated Continuous DC Amps |  |  | 25% Freq. and Torque
|  | Rated Voltage to Ground |  |  | GuaranteedPower Factor without correction (Package):
|  | Rated Short Circuit Current |  |  | 100% Freq. and Torque
|  | Insulation BIL |  |  | 90% Freq. and Torque
|  | X/R Ratio |  |  | 75% Freq. and Torque
|  | Isolation Transformer: |  |  | 50% Freq. and Torque
|  | Manufacturer |  |  | 25% Freq. and Torque
|  | Model No. and Type |  |  | GuaranteedPower Factor with correction (Package):
|  | KVA Rating |  |  | 100% Freq. and Torque
|  | Estimated Weight |  |  | 90% Freq. and Torque
|  | Total Estimated Drive Weight: |  |  | 75% Freq. and Torque
|  | Power Factor Correction Capacitors: |  |  | 50% Freq. and Torque
|  | KVAR |  |  | 25% Freq. and Torque
Harmonic Filter/Power Factor Correction Capacitors Enclosure:
NEMA 3R
Other
Harmonic Filter/Power Factor Correction:
Estimated Price
$/KVAR for Harmonic Filter/Power Factor Correction Changes: