## Master Data Base
AES Wolf Hollow Project Model Input
Long TERM -Assumes all degradation Instantaneous/Non-recoverable
1 | Plant Performance Data: |  |  | New & Clean Conditions |  |  |  |  | Degradated Performance
|  |  |  | Qtr 1 | Qtr 2 | Qtr 3 | Qtr 3 | Qtr 4 |  | Qtr 1 | Qtr 2 | Qtr 3 | Qtr 3 | Qtr 4
|  |  |  | 50F | 66F | 96F | 96F | 50F |  | 50F | 66F | 96F | 96F | 50F
1.1 | Plant Performance - New & Clean |  |  |  |  | w/ DF | w/o DF |  |  |  |  | w/ DF | w/o DF
| Net Plant Output | MW |  | 725.367 | 714.362 | 720.547 | 667.945 | 725.367 |  | 703.606 | 692.9311 | 698.9306 | 647.9067 | 703.606
| Net Plant Heat Rate ( LHV ) | Btu/KWh |  | 6097 | 6090 | 6281 | 6133 | 6097 |  | 6188.455 | 6181.35 | 6375.215 | 6224.995 | 6188.455
| Net Plant Heat Rate ( HHV ) | Btu/KWh |  | 6763 | 6756 | 6967 | 6803 | 6763 |  | 6864.445 | 6857.34 | 7071.505 | 6905.045 | 6864.445
| Auxiliary Load | MW |  | 18.536 | 18.28 | 18.901 | 17.178 | 18.536
| Gas Compressor Load | MW |  | 2.108 | 2.108 | 2.108 | 2.108 | 2.108
| Gross Plant Output | MW |  | 743.903 | 732.642 | 739.448 | 685.123 | 743.903
| Parasitic Load Ratio W/O Gas Compressor | % |  | 2.492% | 2.495% | 2.556% | 2.507% | 2.492%
| Parasitic Load Ratio W / Gas Compressor | % |  | 2.775% | 2.783% | 2.841% | 2.815% | 2.775%
| Gross Plant Heat Rate ( LHV ) | Btu/KWh |  | 5945.0797 | 5938.0497 | 6120.4516 | 5979.2281 | 5945.0797
| Gross Plant Heat Rate ( HHV ) | Btu/KWh |  | 6594.4848 | 6587.4324 | 6788.9168 | 6632.4293 | 6594.4848
1.2 | Plant Performance W/ Test Tolerance |  | Suggest to use this set of data for one of the sensitivity cases.
| Test Tolerance for Output |  | 0.75%
| Test Tolerance for Heat Rate |  | 1%
| Net Plant Output | MW |  | 719.9267 | 709.0043 | 715.1429 | 662.9354 | 719.9267
| Net Plant Heat Rate ( LHV ) | Btu/KWh |  | 6157.97 | 6150.9 | 6343.81 | 6194.33 | 6157.97
| Net Plant Heat Rate ( HHV ) | Btu/KWh |  | 6830.63 | 6823.56 | 7036.67 | 6871.03 | 6830.63
1.3 | Plant Performance W/ Degradation |  | Annual Base | Yr1 | Yr2 | Yr3 | Yr4 | Yr5 | Yr6 | Yr7 | Yr8 | Yr9 | Yr10 | Yr11 | Yr12 | Yr13 | Yr14 | Yr15 | Yr16 | Yr17 | Yr18 | Yr19 | Yr20 | Yr21 | Yr22 | Yr23 | Yr24 | Yr25 | Yr26 | Yr27 | Yr28 | Yr29 | Yr30
| Degradation Assumption: |  | Assuming: (1) Long term degradation 3% on output & 1.5% on heat rate. (2) Each Major Overhaul will bring back 99% of full new and clean condition (3) Short term degradation as per MHI supplied curves.
| Long term average output degradation |  | 3%
| LongTerm average heat rate degradation |  | 1.5%
| Degradation Rate For Output |  |  | 2% | 2.6% | 2.8% | 3% | 1.8% | 2% | 2.3% | 2.5% | 2.8% | 3% | 1.8% | 2% | 2.3% | 2.5% | 2.8% | 3% | 1.8% | 2% | 2.3% | 2.5% | 2.8% | 3% | 1.8% | 2% | 2.3% | 2.5% | 2.8% | 3% | 1.8% | 2%
| Degradation Rate For Heat Rate |  |  | 1% | 1.3% | 1.4% | 1.5% | 1.4% | 1% | 1.15% | 1.25% | 1.4% | 1.5% | 1.4% | 1% | 1.15% | 1.25% | 1.4% | 1.5% | 1.4% | 1% | 1.15% | 1.25% | 1.4% | 1.5% | 1.4% | 1% | 1.15% | 1.25% | 1.4% | 1.5% | 1.4% | 1%
| Non Recovable Output |  | 1%
| Non Recovable Heat Rate |  | 1%
| Output Base W/O Test Tolerance | MW | 714.362 | 700.0748 | 695.7886 | 694.3599 | 692.9311 | 694.4884 | 693.074 | 690.9524 | 689.5379 | 687.4163 | 686.0018 | 694.4884 | 693.074 | 690.9524 | 689.5379 | 687.4163 | 686.0018 | 694.4884 | 693.074 | 690.9524 | 689.5379 | 687.4163 | 686.0018 | 694.4884 | 693.074 | 690.9524 | 689.5379 | 687.4163 | 686.0018 | 694.4884 | 693.074
| Heat Rate Base W/O Test Tolerance ( LHV ) | Btu/KWh | 6090 | 6150.9 | 6169.17 | 6175.26 | 6181.35 | 6237.0126 | 6212.409 | 6221.6353 | 6227.7863 | 6237.0126 | 6243.1635 | 6237.0126 | 6212.409 | 6221.6353 | 6227.7863 | 6237.0126 | 6243.1635 | 6237.0126 | 6212.409 | 6221.6353 | 6227.7863 | 6237.0126 | 6243.1635 | 6237.0126 | 6212.409 | 6221.6353 | 6227.7863 | 6237.0126 | 6243.1635 | 6237.0126 | 6212.409
| Heat Rate Base W/O Test Tolerance ( HHV) | Btu/KWh | 6756 | 6823.56 | 6843.828 | 6850.584 | 6857.34 | 6919.0898 | 6891.7956 | 6902.0309 | 6908.8545 | 6919.0898 | 6925.9134 | 6919.0898 | 6891.7956 | 6902.0309 | 6908.8545 | 6919.0898 | 6925.9134 | 6919.0898 | 6891.7956 | 6902.0309 | 6908.8545 | 6919.0898 | 6925.9134 | 6919.0898 | 6891.7956 | 6902.0309 | 6908.8545 | 6919.0898 | 6925.9134 | 6919.0898 | 6891.7956
| Output Base W/ Test Tolerance | MW | 709.0043 | 694.8242 | 690.5702 | 689.1522 | 687.7342 | 689.2798 | 687.876 | 685.7702 | 684.3664 | 682.2606 | 680.8568 | 689.2798 | 687.876 | 685.7702 | 684.3664 | 682.2606 | 680.8568 | 689.2798 | 687.876 | 685.7702 | 684.3664 | 682.2606 | 680.8568 | 689.2798 | 687.876 | 685.7702 | 684.3664 | 682.2606 | 680.8568 | 689.2798 | 687.876
| Heat Rate W/ test Tolerance ( LHV ) | Btu/KWh | 6150.9 | 6212.409 | 6230.8617 | 6237.0126 | 6243.1635 | 6299.3827 | 6274.5331 | 6283.8517 | 6290.0641 | 6299.3827 | 6305.5951 | 6299.3827 | 6274.5331 | 6283.8517 | 6290.0641 | 6299.3827 | 6305.5951 | 6299.3827 | 6274.5331 | 6283.8517 | 6290.0641 | 6299.3827 | 6305.5951 | 6299.3827 | 6274.5331 | 6283.8517 | 6290.0641 | 6299.3827 | 6305.5951 | 6299.3827 | 6274.5331
| Heat Rate W/ test Tolerance ( HHV ) | Btu/KWh | 6823.56 | 6891.7956 | 6912.2663 | 6919.0898 | 6925.9134 | 6988.2807 | 6960.7136 | 6971.0512 | 6977.943 | 6988.2807 | 6995.1725 | 6988.2807 | 6960.7136 | 6971.0512 | 6977.943 | 6988.2807 | 6995.1725 | 6988.2807 | 6960.7136 | 6971.0512 | 6977.943 | 6988.2807 | 6995.1725 | 6988.2807 | 6960.7136 | 6971.0512 | 6977.943 | 6988.2807 | 6995.1725 | 6988.2807 | 6960.7136
2 | Availability Calculation:
|  |  | PAD | Yr1 | Yr2 | Yr3 | Yr4 | Yr5 | Yr6 | Yr7 | Yr8 | Yr9 | Yr10 | Yr11 | Yr12 | Yr13 | Yr14 | Yr15 | Yr16 | Yr17 | Yr18 | Yr19 | Yr20 | Yr21 | Yr22 | Yr23 | Yr24 | Yr25 | Yr26 | Yr27 | Yr28 | Yr29 | Yr30
| Total Annual Calender Hours | Hr | June 1,2000 | 5136 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
2.1 | Forced Outage |  | Annual Base | Yr1 | Yr2 | Yr3 | Yr4 | Yr5 | Yr6 | Yr7 | Yr8 | Yr9 | Yr10 | Yr11 | Yr12 | Yr13 | Yr14 | Yr15 | Yr16 | Yr17 | Yr18 | Yr19 | Yr20 | Yr21 | Yr22 | Yr23 | Yr24 | Yr25 | Yr26 | Yr27 | Yr28 | Yr29 | Yr30
| Forced Outage Rate Assumption: | % |  | 5% | 4% | 3% | 3% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2%
| Forced Outage Rate | % |  | 5% | 4% | 3% | 3% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2%
| Annual Hours of Forced Outage | Hr |  | 256.8 | 350.4 | 262.8 | 262.8 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2
2.2 | Scheduled Outage |  | Annual Base | Yr1 | Yr2 | Yr3 | Yr4 | Yr5 | Yr6 | Yr7 | Yr8 | Yr9 | Yr10 | Yr11 | Yr12 | Yr13 | Yr14 | Yr15 | Yr16 | Yr17 | Yr18 | Yr19 | Yr20 | Yr21 | Yr22 | Yr23 | Yr24 | Yr25 | Yr26 | Yr27 | Yr28 | Yr29 | Yr30
| Days Needed for Combuster Inspection | days | 10
| Days Needed for Turbine Inspection | days | 16
| Days Needed for Major Overhaul | days | 35
| MHI Mainenance Program |  |  | T | T | C | M | C | T | C | T | C | M | C | T | C | T | C | M | C | T | C | T | C | M | C | T | C | T | C | M | C | T
| Days Needed for Inspection | days |  | 16 | 16 | 10 | 35 | 10 | 16 | 10 | 16 | 10 | 35 | 10 | 16 | 10 | 16 | 10 | 35 | 10 | 16 | 10 | 16 | 10 | 35 | 10 | 16 | 10 | 16 | 10 | 35 | 10 | 16
| Annual Hours Needed for Inspection | Hr |  | 384 | 384 | 240 | 840 | 240 | 384 | 240 | 384 | 240 | 840 | 240 | 384 | 240 | 384 | 240 | 840 | 240 | 384 | 240 | 384 | 240 | 840 | 240 | 384 | 240 | 384 | 240 | 840 | 240 | 384
| Annual Scheduled Outage Rate | % |  | 4.384% | 4.384% | 2.74% | 9.589% | 2.74% | 4.384% | 2.74% | 4.384% | 2.74% | 9.589% | 2.74% | 4.384% | 2.74% | 4.384% | 2.74% | 9.589% | 2.74% | 4.384% | 2.74% | 4.384% | 2.74% | 9.589% | 2.74% | 4.384% | 2.74% | 4.384% | 2.74% | 9.589% | 2.74% | 4.384%
2.3 | Annual Plant Availability |  |  | Yr1 | Yr2 | Yr3 | Yr4 | Yr5 | Yr6 | Yr7 | Yr8 | Yr9 | Yr10 | Yr11 | Yr12 | Yr13 | Yr14 | Yr15 | Yr16 | Yr17 | Yr18 | Yr19 | Yr20 | Yr21 | Yr22 | Yr23 | Yr24 | Yr25 | Yr26 | Yr27 | Yr28 | Yr29 | Yr30
| Total Annual Calender Hours | Hr |  | 5136 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
| Total Scheduled Outage Hours | Hr |  | 384 | 384 | 240 | 840 | 240 | 384 | 240 | 384 | 240 | 840 | 240 | 384 | 240 | 384 | 240 | 840 | 240 | 384 | 240 | 384 | 240 | 840 | 240 | 384 | 240 | 384 | 240 | 840 | 240 | 384
| Total Forced Outage Hours | Hr |  | 256.8 | 350.4 | 262.8 | 262.8 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2 | 175.2
| Total Available Operation Hours | Hr |  | 4495.2 | 8025.6 | 8257.2 | 7657.2 | 8344.8 | 8200.8 | 8344.8 | 8200.8 | 8344.8 | 7744.8 | 8344.8 | 8200.8 | 8344.8 | 8200.8 | 8344.8 | 7744.8 | 8344.8 | 8200.8 | 8344.8 | 8200.8 | 8344.8 | 7744.8 | 8344.8 | 8200.8 | 8344.8 | 8200.8 | 8344.8 | 7744.8 | 8344.8 | 8200.8
| Plant Annual Availability | % |  | 87.52% | 91.62% | 94.26% | 87.41% | 95.26% | 93.62% | 95.26% | 93.62% | 95.26% | 88.41% | 95.26% | 93.62% | 95.26% | 93.62% | 95.26% | 88.41% | 95.26% | 93.62% | 95.26% | 93.62% | 95.26% | 88.41% | 95.26% | 93.62% | 95.26% | 93.62% | 95.26% | 88.41% | 95.26% | 93.62%
| 10 Year Plant Average Availability | % | 92.22%
| 20 Year Plant Average Availability | % | 93.07%
| 30 Year Plant Average Availability | % | 93.18%
3 | EOH Calculation |  | Annual Base | Yr1 | Yr2 | Yr3 | Yr4 | Yr5 | Yr6 | Yr7 | Yr8 | Yr9 | Yr10 | Yr11 | Yr12 | Yr13 | Yr14 | Yr15 | Yr16 | Yr17 | Yr18 | Yr19 | Yr20 | Yr21 | Yr22 | Yr23 | Yr24 | Yr25 | Yr26 | Yr27 | Yr28 | Yr29 | Yr30
| Assumed Number of Starts Per Year |  | 60 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
| EOH Per Start |  | 20
| EOH for Starts |  |  | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
Number of Trips | bar: Yr1 to Yr30
| EOH for Trips |  |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
| Dispatch Rate Assumption (out of total available hours) |  | 78%
| Actual Fired Hours |  |  | 3506.256 | 6259.968 | 6440.616 | 5972.616 | 6508.944 | 6396.624 | 6508.944 | 6396.624 | 6508.944 | 6040.944 | 6508.944 | 6396.624 | 6508.944 | 6396.624 | 6508.944 | 6040.944 | 6508.944 | 6396.624 | 6508.944 | 6396.624 | 6508.944 | 6040.944 | 6508.944 | 6396.624 | 6508.944 | 6396.624 | 6508.944 | 6040.944 | 6508.944 | 6396.624
| Annual Total EOH |  | 7380.0988 | 4506.256 | 7259.968 | 7440.616 | 6972.616 | 7508.944 | 7396.624 | 7508.944 | 7396.624 | 7508.944 | 7040.944 | 7508.944 | 7396.624 | 7508.944 | 7396.624 | 7508.944 | 7040.944 | 7508.944 | 7396.624 | 7508.944 | 7396.624 | 7508.944 | 7040.944 | 7508.944 | 7396.624 | 7508.944 | 7396.624 | 7508.944 | 7040.944 | 7508.944 | 7396.624
| Capacity Factor | % | 72.83% | 68.27% | 71.46% | 73.52% | 68.18% | 74.3% | 73.02% | 74.3% | 73.02% | 74.3% | 68.96% | 74.3% | 73.02% | 74.3% | 73.02% | 74.3% | 68.96% | 74.3% | 73.02% | 74.3% | 73.02% | 74.3% | 68.96% | 74.3% | 73.02% | 74.3% | 73.02% | 74.3% | 68.96% | 74.3% | 73.02%
4 | EPC Payment Schedule
| EPC Pricing |  | See Separate file
| EPC Payment Schedule - June 1 |  | See Separate file
| EPC Payment Schedule - July 1 |  | See Separate file
5 | MHI Maintenance Program
|  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  | PAD | Yr1 | Yr2 | Yr3 | Yr4 | Yr5 | Yr6 | Yr7 | Yr8 | Yr9 | Yr10 | Yr11 | Yr12 | Yr13 | Yr14 | Yr15 | Yr16 | Yr17 | Yr18 | Yr19 | Yr20 | Yr21 | Yr22 | Yr23 | Yr24 | Yr25 | Yr26 | Yr27 | Yr28 | Yr29 | Yr30
| MHI Mainenance Program |  |  | T | T | C | M | C | T | C | T | C | M | C | T | C | T | C | M | C | T | C | T | C | M | C | T | C | T | C | M | C | T
| MHI Proposed 30 Price per Turbine ( w/o inflation ) | k$ | 4846.6 | 2775.6 | 2775.6 | 2775.6 | 2775.6 | 2775.6 | 2775.6 | 4791.1 | 4791.1 | 4791.1 | 4791.1 | 4791.1 | 4791.1 | 2911.7 | 1819.6 | 10642.1 | 4308.7 | 904.2 | 3643.6 | 3858.4 | 2548.5 | 2548.5 | 1850.9 | 1850.9 | 15457.7 | 2993.6 | 10167.4 | 986.1 | 5126.6 | 1722.1 | 986.1
| Adjusted MHI Price Per Gas Turbine | k$ | 4846.6 | 2775.6 | 2775.6 | 2775.6 | 2775.6 | 2775.6 | 2775.6 | 4791.1 | 4791.1 | 4791.1 | 4791.1 | 4791.1 | 4791.1 | 2911.7 | 1819.6 | 10642.1 | 4308.7 | 904.2 | 3643.6 | 3858.4 | 2548.5 | 2548.5 | 1850.9 | 1850.9 | 15457.7 | 2993.6 | 10167.4 | 986.1 | 5126.6 | 1722.1 | 986.1
| Adjusted MHI Price for Both Turbines | k$ | 9693.2 | 5551.2 | 5551.2 | 5551.2 | 5551.2 | 5551.2 | 5551.2 | 9582.2 | 9582.2 | 9582.2 | 9582.2 | 9582.2 | 9582.2 | 5823.4 | 3639.2 | 21284.2 | 8617.4 | 1808.4 | 7287.2 | 7716.8 | 5097 | 5097 | 3701.8 | 3701.8 | 30915.4 | 5987.2 | 20334.8 | 1972.2 | 10253.2 | 3444.2 | 1972.2
| MHI Yr1 through Yr 6 Fixed Price | K$ | 43000
| MHI Yr1 through Yr 6 Fixed Price Initial Spare | k$ | 9600
| MHI Yr 7 through Yr 12 base price | k$ | 58000
| MHI Technical Assistance per EOH | $ | 45
| Per EOH Payment Per Turbine - Yr 1 through Yr 6 | $ | 392.9167 | 1 Yr1: 785.8333; 2 Yr2: 785.8333; 3 Yr3: 785.8333; 4 Yr4: 785.8333; 5 Yr5: 785.8333; 6 Yr6: 785.8333
| Per EOH Payment Per Turbine - Yr 7 through Yr 12 | $ | 649.1667 | 7 Yr7: 1298.3333; 8 Yr8: 1298.3333; 9 Yr9: 1298.3333; 10 Yr10: 1298.3333; 11 Yr11: 1298.3333; 12 Yr12: 1298.3333
| Total Available Operation Hours | Hr |  | 4495.2 | 8025.6 | 8257.2 | 7657.2 | 8344.8 | 8200.8 | 8344.8 | 8200.8 | 8344.8 | 7744.8 | 8344.8 | 8200.8 | 8344.8 | 8200.8 | 8344.8 | 7744.8 | 8344.8 | 8200.8 | 8344.8 | 8200.8 | 8344.8 | 7744.8 | 8344.8 | 8200.8 | 8344.8 | 8200.8 | 8344.8 | 7744.8 | 8344.8 | 8200.8
| Annual EOH |  |  | 4506.256 | 7259.968 | 7440.616 | 6972.616 | 7508.944 | 7396.624 | 7508.944 | 7396.624 | 7508.944 | 7040.944 | 7508.944 | 7396.624 | 7508.944 | 7396.624 | 7508.944 | 7040.944 | 7508.944 | 7396.624 | 7508.944 | 7396.624 | 7508.944 | 7040.944 | 7508.944 | 7396.624 | 7508.944 | 7396.624 | 7508.944 | 7040.944 | 7508.944 | 7396.624
| Gas Turbine Maintenance Payment -MHI Service | k$ |  | 3541.1662 | 5705.1249 | 5847.0841 | 5479.3141 | 5900.7785 | 5812.5137 | 9749.1123 | 9603.2835 | 9749.1123 | 9141.4923 | 9749.1123 | 9603.2835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Gas Turbine Maintenance Payment - AES Self Service |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5823.4 | 3639.2 | 21284.2 | 8617.4 | 1808.4 | 7287.2 | 7716.8 | 5097 | 5097 | 3701.8 | 3701.8 | 30915.4 | 5987.2 | 20334.8 | 1972.2 | 10253.2 | 3444.2 | 1972.2
| Gas Turbine Maintenance Payment | k$ |  | 3541.1662 | 5705.1249 | 5847.0841 | 5479.3141 | 5900.7785 | 5812.5137 | 9749.1123 | 9603.2835 | 9749.1123 | 9141.4923 | 9749.1123 | 9603.2835 | 5823.4 | 3639.2 | 21284.2 | 8617.4 | 1808.4 | 7287.2 | 7716.8 | 5097 | 5097 | 3701.8 | 3701.8 | 30915.4 | 5987.2 | 20334.8 | 1972.2 | 10253.2 | 3444.2 | 1972.2
| Smoothed Gas Turbine Maint. Payment by EOH | K$ |  | 3658.664 | 6335.8033 | 6495.9624 | 6081.0424 | 6556.5407 | 6456.9599 | 11121.2112 | 10952.3021 | 11121.2112 | 10417.4234 | 11121.2112 | 10952.3021 | 8423.347 | 8295.4132 | 8423.347 | 7890.2892 | 8423.347 | 8295.4132 | 9773.9388 | 9625.4921 | 9773.9388 | 9155.411 | 9773.9388 | 9625.4921 | 7641.8463 | 7525.7819 | 7641.8463 | 7158.2445 | 7641.8463 | 7525.7819
| Inflation Rate: | % | 0% | 3541.1662 | 5705.1249 | 5847.0841 | 5479.3141 | 5900.7785 | 5812.5137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SCR Catalyst Replacement Schedule |  | 6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
| SCR Catalyst Cost | k$ | 1332 | 0 | 0 | 0 | 0 | 0 | 1332 | 0 | 0 | 0 | 0 | 0 | 1332 | 0 | 0 | 0 | 0 | 0 | 1332 | 0 | 0 | 0 | 0 | 0 | 1332 | 0 | 0 | 0 | 0 | 0 | 0
Note on D33: Qing Fang: This is a Long Term degradation for the output
Note on D34: Qing Fang: This is a Long Term degradation for the Heat Rate
Note on D38: Qing Fang: Assuming 1% Non Recovable degradation for the output from new and clean conditions
Note on D39: Qing Fang: Assuming 1% Non Recovable degradation for the Heat Rate from new and clean conditions
Note on D41: Qing Fang: This is the EPC Contractor guaranteed Net Plant Output at annual average temperature 66F
Note on D42: Qing Fang: This is the EPC Contractor guaranteed Net Plant Heat Rate (LHV) at annual average temperature 66F
Note on D43: Qing Fang: This is the EPC Contractor guaranteed Net Plant Heat Rate (HHV) at annual average temperature 66F
Note on D94: Qing Fang: 1. This is a assumed number! 2. This number varies depending on the number of starts per year assumed. 3. The idea is to get an average annual EOH of 8000 - 8600EOH 4. Watch closely how this should affect the capacity factors
Note on D97: Qing Fang: This is effectively assuming that out of all the available hours, when it is dispatched, it will run the plant full load
Note on D133: Qing Fang: Assumptions: 1. SCR Catalyst should be replaced every 6 years; 2. SCR Catalyst could be changed during a Turbine Inspection 3. 0 means no need to change, 1 means need to change
Note on D134: Qing Fang: Assumption: 1. This is base year price for year 2000; 2. Inflation rate of 3%
Note on E7: Qing Fang: Assumptions: 1. Average Tepmerature during Jan - Mar is 50F 2. Evap On 3. Duct Firing OFF
Note on F7: Qing Fang: Assumptions: 1. Average Tepmerature during Apr - June is 66F 2. Evap On 3. Duct Firing OFF
Note on G7: Qing Fang: Assumptions: 1. Average Tepmerature during July - Sept. is 96F 2. Evap On 3. Duct Firing ON
Note on H7: Qing Fang: Assumptions: 1. Average Tepmerature during July - Sept. is 96F 2. Evap On 3. Duct Firing OFF
Note on I7: Qing Fang: Assumptions: 1. Average Tepmerature during Oct - Dec is 50F 2. Evap On 3. Duct Firing OFF
Note on K7: Qing Fang: Assumptions: 1. Average Tepmerature during Jan - Mar is 50F 2. Evap On 3. Duct Firing OFF
Note on K122: Qing Fang: Assuming: (1) 3% inflation over 3 years ( first 6 year numbers are average for Yr1 thru Y6 ) (2) No Forex rate adjustment
Note on L7: Qing Fang: Assumptions: 1. Average Tepmerature during Apr - June is 66F 2. Evap On 3. Duct Firing OFF
Note on M7: Qing Fang: Assumptions: 1. Average Tepmerature during July - Sept. is 96F 2. Evap On 3. Duct Firing ON
Note on N7: Qing Fang: Assumptions: 1. Average Tepmerature during July - Sept. is 96F 2. Evap On 3. Duct Firing OFF
Note on O7: Qing Fang: Assumptions: 1. Average Tepmerature during Oct - Dec is 50F 2. Evap On 3. Duct Firing OFF

## Quarterly Data
Operating Year |  |  | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 13 | 13 | 13 | 13 | 14 | 14 | 14 | 14 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 23 | 23 | 23 | 23 | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 27 | 27 | 27 | 27 | 28 | 28 | 28 | 28 | 29 | 29 | 29 | 29 | 30 | 30 | 30 | 30 | 31
Calender Year |  |  | 2002 | 2002 | 2002 | 2003 | 2003 | 2003 | 2003 | 2004 | 2004 | 2004 | 2004 | 2005 | 2005 | 2005 | 2005 | 2006 | 2006 | 2006 | 2006 | 2007 | 2007 | 2007 | 2007 | 2008 | 2008 | 2008 | 2008 | 2009 | 2009 | 2009 | 2009 | 2010 | 2010 | 2010 | 2010 | 2011 | 2011 | 2011 | 2011 | 2012 | 2012 | 2012 | 2012 | 2013 | 2013 | 2013 | 2013 | 2014 | 2014 | 2014 | 2014 | 2015 | 2015 | 2015 | 2015 | 2016 | 2016 | 2016 | 2016 | 2017 | 2017 | 2017 | 2017 | 2018 | 2018 | 2018 | 2018 | 2019 | 2019 | 2019 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2026 | 2026 | 2026 | 2026 | 2027 | 2027 | 2027 | 2027 | 2028 | 2028 | 2028 | 2028 | 2029 | 2029 | 2029 | 2029 | 2030 | 2030 | 2030 | 2030 | 2031 | 2031 | 2031 | 2031 | 2032
Quarter |  |  | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1
Plant Performance w/o Degradation:
| Plant Gross Output | MW | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9 | 732.5 | 739.3 | 743.9 | 743.9
| Parasitic Load | MW | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975 | 18.3125 | 18.4825 | 18.5975 | 18.5975
| Plant Net Output | MW | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 725.3025
| Plant Gross Heat Rate HHV | Btu/kWh | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594 | 6587 | 6793 | 6594 | 6594
| Plant Net Heat Rate HHV | Btu/kWh | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769 | 6755.8974 | 6967.1795 | 6763.0769 | 6763.0769
| Plant Net Heat Rate LHV | Btu/kWh | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644 | 6099.5824 | 6290.339 | 6106.0644 | 6106.0644
Plant Performance w/ Degradation
| Accumulated Output Degradation Factor | % | -0.6667% | -1.333% | -2% | -2.6% | -2.6% | -2.6% | -2.6% | -2.8% | -2.8% | -2.8% | -2.8% | -3% | -3% | -3% | -3% | -1.8% | -1.8% | -1.8% | -1.8% | -2% | -2% | -2% | -2% | -2.3% | -2.3% | -2.3% | -2.3% | -2.5% | -2.5% | -2.5% | -2.5% | -2.8% | -2.8% | -2.8% | -2.8% | -3% | -3% | -3% | -3% | -1.8% | -1.8% | -1.8% | -1.8% | -2% | -2% | -2% | -2% | -2.3% | -2.3% | -2.3% | -2.3% | -2.5% | -2.5% | -2.5% | -2.5% | -2.8% | -2.8% | -2.8% | -2.8% | -3% | -3% | -3% | -3% | -1.8% | -1.8% | -1.8% | -1.8% | -2% | -2% | -2% | -2% | -2.3% | -2.3% | -2.3% | -2.3% | -2.5% | -2.5% | -2.5% | -2.5% | -2.8% | -2.8% | -2.8% | -2.8% | -3% | -3% | -3% | -3% | -1.8% | -1.8% | -1.8% | -1.8% | -2% | -2% | -2% | -2% | -2.3% | -2.3% | -2.3% | -2.3% | -2.5% | -2.5% | -2.5% | -2.5% | -2.8% | -2.8% | -2.8% | -2.8% | -3% | -3% | -3% | -3% | -1.8% | -1.8% | -1.8% | -1.8% | -2% | -2% | -2% | -2% | -2.3%
| Plant Gross Output w/ Degradation | MW | 727.6167 | 729.4427 | 729.022 | 724.5586 | 713.455 | 720.0782 | 724.5586 | 723.0708 | 711.99 | 718.5996 | 723.0708 | 721.583 | 710.525 | 717.121 | 721.583 | 730.5098 | 719.315 | 725.9926 | 730.5098 | 729.022 | 717.85 | 724.514 | 729.022 | 726.7903 | 715.6525 | 722.2961 | 726.7903 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 723.0708 | 711.99 | 718.5996 | 723.0708 | 721.583 | 710.525 | 717.121 | 721.583 | 730.5098 | 719.315 | 725.9926 | 730.5098 | 729.022 | 717.85 | 724.514 | 729.022 | 726.7903 | 715.6525 | 722.2961 | 726.7903 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 723.0708 | 711.99 | 718.5996 | 723.0708 | 721.583 | 710.525 | 717.121 | 721.583 | 730.5098 | 719.315 | 725.9926 | 730.5098 | 729.022 | 717.85 | 724.514 | 729.022 | 726.7903 | 715.6525 | 722.2961 | 726.7903 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 723.0708 | 711.99 | 718.5996 | 723.0708 | 721.583 | 710.525 | 717.121 | 721.583 | 730.5098 | 719.315 | 725.9926 | 730.5098 | 729.022 | 717.85 | 724.514 | 729.022 | 726.7903 | 715.6525 | 722.2961 | 726.7903 | 725.3025 | 714.1875 | 720.8175 | 725.3025 | 723.0708 | 711.99 | 718.5996 | 723.0708 | 721.583 | 710.525 | 717.121 | 721.583 | 730.5098 | 719.315 | 725.9926 | 730.5098 | 729.022 | 717.85 | 724.514 | 729.022 | 726.7903
| Plant Net Output w/ Degradation | MW | 709.3042 | 710.9602 | 710.4245 | 705.9611 | 695.1425 | 701.5957 | 705.9611 | 704.4733 | 693.6775 | 700.1171 | 704.4733 | 702.9855 | 692.2125 | 698.6385 | 702.9855 | 711.9123 | 701.0025 | 707.5101 | 711.9123 | 710.4245 | 699.5375 | 706.0315 | 710.4245 | 708.1928 | 697.34 | 703.8136 | 708.1928 | 706.705 | 695.875 | 702.335 | 706.705 | 704.4733 | 693.6775 | 700.1171 | 704.4733 | 702.9855 | 692.2125 | 698.6385 | 702.9855 | 711.9123 | 701.0025 | 707.5101 | 711.9123 | 710.4245 | 699.5375 | 706.0315 | 710.4245 | 708.1928 | 697.34 | 703.8136 | 708.1928 | 706.705 | 695.875 | 702.335 | 706.705 | 704.4733 | 693.6775 | 700.1171 | 704.4733 | 702.9855 | 692.2125 | 698.6385 | 702.9855 | 711.9123 | 701.0025 | 707.5101 | 711.9123 | 710.4245 | 699.5375 | 706.0315 | 710.4245 | 708.1928 | 697.34 | 703.8136 | 708.1928 | 706.705 | 695.875 | 702.335 | 706.705 | 704.4733 | 693.6775 | 700.1171 | 704.4733 | 702.9855 | 692.2125 | 698.6385 | 702.9855 | 711.9123 | 701.0025 | 707.5101 | 711.9123 | 710.4245 | 699.5375 | 706.0315 | 710.4245 | 708.1928 | 697.34 | 703.8136 | 708.1928 | 706.705 | 695.875 | 702.335 | 706.705 | 704.4733 | 693.6775 | 700.1171 | 704.4733 | 702.9855 | 692.2125 | 698.6385 | 702.9855 | 711.9123 | 701.0025 | 707.5101 | 711.9123 | 710.4245 | 699.5375 | 706.0315 | 710.4245 | 708.1928
| Accumulated Heat Rate Degradation Factor | % | 0.3333% | 0.6667% | 1% | 1.3% | 1.3% | 1.3% | 1.3% | 1.4% | 1.4% | 1.4% | 1.4% | 1.5% | 1.5% | 1.5% | 1.5% | 1.4% | 1.4% | 1.4% | 1.4% | 1% | 1% | 1% | 1% | 1.15% | 1.15% | 1.15% | 1.15% | 1.25% | 1.25% | 1.25% | 1.25% | 1.4% | 1.4% | 1.4% | 1.4% | 1.5% | 1.5% | 1.5% | 1.5% | 1.4% | 1.4% | 1.4% | 1.4% | 1% | 1% | 1% | 1% | 1.15% | 1.15% | 1.15% | 1.15% | 1.25% | 1.25% | 1.25% | 1.25% | 1.4% | 1.4% | 1.4% | 1.4% | 1.5% | 1.5% | 1.5% | 1.5% | 1.4% | 1.4% | 1.4% | 1.4% | 1% | 1% | 1% | 1% | 1.15% | 1.15% | 1.15% | 1.15% | 1.25% | 1.25% | 1.25% | 1.25% | 1.4% | 1.4% | 1.4% | 1.4% | 1.5% | 1.5% | 1.5% | 1.5% | 1.4% | 1.4% | 1.4% | 1.4% | 1% | 1% | 1% | 1% | 1.15% | 1.15% | 1.15% | 1.15% | 1.25% | 1.25% | 1.25% | 1.25% | 1.4% | 1.4% | 1.4% | 1.4% | 1.5% | 1.5% | 1.5% | 1.5% | 1.4% | 1.4% | 1.4% | 1.4% | 1% | 1% | 1% | 1% | 1.15%
| Plant Gross Heat Rate HHV w/ Degradation | Btu/kWh | 6608.9567 | 6838.2867 | 6659.94 | 6679.722 | 6672.631 | 6881.309 | 6679.722 | 6686.316 | 6679.218 | 6888.102 | 6686.316 | 6692.91 | 6685.805 | 6894.895 | 6692.91 | 6686.316 | 6679.218 | 6888.102 | 6686.316 | 6659.94 | 6652.87 | 6860.93 | 6659.94 | 6669.831 | 6662.7505 | 6871.1195 | 6669.831 | 6676.425 | 6669.3375 | 6877.9125 | 6676.425 | 6686.316 | 6679.218 | 6888.102 | 6686.316 | 6692.91 | 6685.805 | 6894.895 | 6692.91 | 6686.316 | 6679.218 | 6888.102 | 6686.316 | 6659.94 | 6652.87 | 6860.93 | 6659.94 | 6669.831 | 6662.7505 | 6871.1195 | 6669.831 | 6676.425 | 6669.3375 | 6877.9125 | 6676.425 | 6686.316 | 6679.218 | 6888.102 | 6686.316 | 6692.91 | 6685.805 | 6894.895 | 6692.91 | 6686.316 | 6679.218 | 6888.102 | 6686.316 | 6659.94 | 6652.87 | 6860.93 | 6659.94 | 6669.831 | 6662.7505 | 6871.1195 | 6669.831 | 6676.425 | 6669.3375 | 6877.9125 | 6676.425 | 6686.316 | 6679.218 | 6888.102 | 6686.316 | 6692.91 | 6685.805 | 6894.895 | 6692.91 | 6686.316 | 6679.218 | 6888.102 | 6686.316 | 6659.94 | 6652.87 | 6860.93 | 6659.94 | 6669.831 | 6662.7505 | 6871.1195 | 6669.831 | 6676.425 | 6669.3375 | 6877.9125 | 6676.425 | 6686.316 | 6679.218 | 6888.102 | 6686.316 | 6692.91 | 6685.805 | 6894.895 | 6692.91 | 6686.316 | 6679.218 | 6888.102 | 6686.316 | 6659.94 | 6652.87 | 6860.93 | 6659.94 | 6669.831
| Plant Net Heat Rate HHV w/ Degradation | Btu/kWh | 6778.4171 | 7013.6274 | 6830.7077 | 6850.9969 | 6843.7241 | 7057.7528 | 6850.9969 | 6857.76 | 6850.48 | 7064.72 | 6857.76 | 6864.5231 | 6857.2359 | 7071.6872 | 6864.5231 | 6857.76 | 6850.48 | 7064.72 | 6857.76 | 6830.7077 | 6823.4564 | 7036.8513 | 6830.7077 | 6840.8523 | 6833.5903 | 7047.3021 | 6840.8523 | 6847.6154 | 6840.3462 | 7054.2692 | 6847.6154 | 6857.76 | 6850.48 | 7064.72 | 6857.76 | 6864.5231 | 6857.2359 | 7071.6872 | 6864.5231 | 6857.76 | 6850.48 | 7064.72 | 6857.76 | 6830.7077 | 6823.4564 | 7036.8513 | 6830.7077 | 6840.8523 | 6833.5903 | 7047.3021 | 6840.8523 | 6847.6154 | 6840.3462 | 7054.2692 | 6847.6154 | 6857.76 | 6850.48 | 7064.72 | 6857.76 | 6864.5231 | 6857.2359 | 7071.6872 | 6864.5231 | 6857.76 | 6850.48 | 7064.72 | 6857.76 | 6830.7077 | 6823.4564 | 7036.8513 | 6830.7077 | 6840.8523 | 6833.5903 | 7047.3021 | 6840.8523 | 6847.6154 | 6840.3462 | 7054.2692 | 6847.6154 | 6857.76 | 6850.48 | 7064.72 | 6857.76 | 6864.5231 | 6857.2359 | 7071.6872 | 6864.5231 | 6857.76 | 6850.48 | 7064.72 | 6857.76 | 6830.7077 | 6823.4564 | 7036.8513 | 6830.7077 | 6840.8523 | 6833.5903 | 7047.3021 | 6840.8523 | 6847.6154 | 6840.3462 | 7054.2692 | 6847.6154 | 6857.76 | 6850.48 | 7064.72 | 6857.76 | 6864.5231 | 6857.2359 | 7071.6872 | 6864.5231 | 6857.76 | 6850.48 | 7064.72 | 6857.76 | 6830.7077 | 6823.4564 | 7036.8513 | 6830.7077 | 6840.8523
| Plant Net Heat Rate LHV / Degradation | Btu/kWh | 6119.9143 | 6332.2746 | 6167.125 | 6185.4432 | 6178.8769 | 6372.1134 | 6185.4432 | 6191.5493 | 6184.9765 | 6378.4038 | 6191.5493 | 6197.6554 | 6191.0761 | 6384.6941 | 6197.6554 | 6191.5493 | 6184.9765 | 6378.4038 | 6191.5493 | 6167.125 | 6160.5782 | 6353.2424 | 6167.125 | 6176.2841 | 6169.7276 | 6362.6779 | 6176.2841 | 6182.3902 | 6175.8272 | 6368.9682 | 6182.3902 | 6191.5493 | 6184.9765 | 6378.4038 | 6191.5493 | 6197.6554 | 6191.0761 | 6384.6941 | 6197.6554 | 6191.5493 | 6184.9765 | 6378.4038 | 6191.5493 | 6167.125 | 6160.5782 | 6353.2424 | 6167.125 | 6176.2841 | 6169.7276 | 6362.6779 | 6176.2841 | 6182.3902 | 6175.8272 | 6368.9682 | 6182.3902 | 6191.5493 | 6184.9765 | 6378.4038 | 6191.5493 | 6197.6554 | 6191.0761 | 6384.6941 | 6197.6554 | 6191.5493 | 6184.9765 | 6378.4038 | 6191.5493 | 6167.125 | 6160.5782 | 6353.2424 | 6167.125 | 6176.2841 | 6169.7276 | 6362.6779 | 6176.2841 | 6182.3902 | 6175.8272 | 6368.9682 | 6182.3902 | 6191.5493 | 6184.9765 | 6378.4038 | 6191.5493 | 6197.6554 | 6191.0761 | 6384.6941 | 6197.6554 | 6191.5493 | 6184.9765 | 6378.4038 | 6191.5493 | 6167.125 | 6160.5782 | 6353.2424 | 6167.125 | 6176.2841 | 6169.7276 | 6362.6779 | 6176.2841 | 6182.3902 | 6175.8272 | 6368.9682 | 6182.3902 | 6191.5493 | 6184.9765 | 6378.4038 | 6191.5493 | 6197.6554 | 6191.0761 | 6384.6941 | 6197.6554 | 6191.5493 | 6184.9765 | 6378.4038 | 6191.5493 | 6167.125 | 6160.5782 | 6353.2424 | 6167.125 | 6176.2841